## ASORC
PV SCADA Signal List
Signal
No | Equipment | Source IED Name | Signal Type | Address | Description
1 | Weather Station | WS / MR |  | 0000 | Ambient temperature
2 | Weather Station | WS / MR |  | 0001 | Temperature 1 (Bracket)
3 | Weather Station | WS / MR |  | 0015 | Instantaneous wind direction
4 | Weather Station | WS / MR |  | 0016 | Instantaneous wind speed
5 | Weather Station | WS / MR |  | 0006 | Dew-point Temperature
6 | Weather Station | WS / MR |  | 0007 | Ambient Humidity
7 | Weather Station | WS / MR |  | 0017 | Wind speed in 2 minutes
8 | Weather Station | WS / MR |  | 000E | Instantaneous value of total radiation 1
9 | Weather Station | WS / MR |  | 001A | Cumulative value of sunshine duration
10 | Weather Station | WS / MR |  | 001B | Cumulative value of total radiation 1
11 | Weather Station | WS / MR |  | 001C | Cumulative value of scattered radiation
12 | Weather Station | WS / MR |  | 001D | Cumulative value of direct radiation
13 | Weather Station | WS / MR |  | 0020 | Cumulative value of photosynthetic
14 | Weather Station | WS / MR |  | 0023 | Daily sunshine duration
15 | Weather Station | WS / MR |  | 0024 | Daily cumulative value of total radiation 1
16 | Weather Station | WS / MR |  | 0025 | Daily cumulative value of scattered radiation
17 | Weather Station | WS / MR |  | 0026 | Daily cumulative value of direct radiation
18 | Weather Station | WS / MR |  | 0028 | Daily cumulative value of net radiation
19 | Weather Station | WS / MR |  | 0029 | Daily cumulative value of photosynthetic radiation
20 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL1 | Active Power (per inverter and total) | DL : Data Logger / Inv : Inverter / MR : Measurements / S : Status / W : Alarms Warnings / F : Faults / WS: Weather Station
21 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL2 | Reactive Power
22 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL3 | Apparent Power | Logger Summary Event & Alarm Log Visualization
23 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL4 | Power Factor | Fault Code (numeric)
24 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL5 | AC Voltage (L-L or L-N) | Fault Description (text)
25 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL6 | AC Current (per phase) | Time of Last Fault
26 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL7 | Frequency | Time of Last Status Change
27 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL8 | DC Voltage ( String Level) | Operating Hours Counter
28 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL9 | DC Current
29 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL10 | DC Power
30 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL11 | Inverter Efficiency
31 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL12 | Daily Energy Yield
32 | DL 01/Inv 01 | DL 01/Inv 01/MR | Data Link | DL13 | Total Energy Yield
33 | DL 01/Inv 01 | DL 01/Inv 01/S | Data Link | DL14 | Inverter Running / Stopped
34 | DL 01/Inv 01 | DL 01/Inv 01/S | Data Link | DL15 | Inverter Grid Connection Status (Connected / Disconnected)
35 | DL 01/Inv 01 | DL 01/Inv 01/S | Data Link | DL16 | Communication Status (Healthy / Lost)
36 | DL 01/Inv 01 | DL 01/Inv 01/S | Data Link | DL17 | Remote ON/OFF Status
37 | DL 01/Inv 01 | DL 01/Inv 01/S | Data Link | DL18 | Active Power Control Mode
38 | DL 01/Inv 01 | DL 01/Inv 01/S | Data Link | DL19 | Reactive Power Control Mode
39 | DL 01/Inv 01 | DL 01/Inv 01/S | Data Link | DL20 | Islanding Detection Status
40 | DL 01/Inv 01 | DL 01/Inv 01/S | Data Link | DL21 | Power Curtailment Status
41 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL22 | General Fault Trip
42 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL23 | Warning Active (Derating, Overtemperature)
43 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL24 | DC Insulation Fault
44 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL25 | Ground Fault
45 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL26 | AC Overvoltage
46 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL27 | AC Undervoltage
47 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL28 | Grid Overfrequency
48 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL29 | Grid Underfrequency
49 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL30 | DC Overvoltage
50 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL31 | Inverter Over temperature
51 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL32 | String Reverse Polarity
52 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL33 | Fan Failure
53 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL34 | Communication Failure
54 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL35 | Power Limitation Active due to Grid Command
55 | DL 01/Inv 01 | DL 01/Inv 01/F | Data Link | DL36 | Inverter Trip History Available
56 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL37 | Active Power (per inverter and total)
57 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL38 | Reactive Power
58 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL39 | Apparent Power
59 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL40 | Power Factor
60 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL41 | AC Voltage (L-L or L-N)
61 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL42 | AC Current (per phase)
62 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL43 | Frequency
63 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL44 | DC Voltage ( String Level)
64 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL45 | DC Current
65 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL46 | DC Power
66 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL47 | Inverter Efficiency
67 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL48 | Daily Energy Yield
68 | DL 01/Inv 02 | DL 01/Inv 02/MR | Data Link | DL49 | Total Energy Yield
69 | DL 01/Inv 02 | DL 01/Inv 02/S | Data Link | DL50 | Inverter Running / Stopped
70 | DL 01/Inv 02 | DL 01/Inv 02/S | Data Link | DL51 | Inverter Grid Connection Status (Connected / Disconnected)
71 | DL 01/Inv 02 | DL 01/Inv 02/S | Data Link | DL52 | Communication Status (Healthy / Lost)
72 | DL 01/Inv 02 | DL 01/Inv 02/S | Data Link | DL53 | Remote ON/OFF Status
73 | DL 01/Inv 02 | DL 01/Inv 02/S | Data Link | DL54 | Active Power Control Mode
74 | DL 01/Inv 02 | DL 01/Inv 02/S | Data Link | DL55 | Reactive Power Control Mode
75 | DL 01/Inv 02 | DL 01/Inv 02/S | Data Link | DL56 | Islanding Detection Status
76 | DL 01/Inv 02 | DL 01/Inv 02/S | Data Link | DL57 | Power Curtailment Status
77 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL58 | General Fault Trip
78 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL59 | Warning Active (Derating, Overtemperature)
79 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL60 | DC Insulation Fault
80 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL61 | Ground Fault
81 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL62 | AC Overvoltage
82 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL63 | AC Undervoltage
83 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL64 | Grid Overfrequency
84 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL65 | Grid Underfrequency
85 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL66 | DC Overvoltage
86 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL67 | Inverter Over temperature
87 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL68 | String Reverse Polarity
88 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL69 | Fan Failure
89 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL70 | Communication Failure
90 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL71 | Power Limitation Active due to Grid Command
91 | DL 01/Inv 02 | DL 01/Inv 02/F | Data Link | DL72 | Inverter Trip History Available
92 | I | I | I | I | I
93 | I | I | I | I | I
94 | I | I | I | I | I
95 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2593 | Active Power (per inverter and total)
96 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2594 | Reactive Power
97 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2595 | Apparent Power
98 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2596 | Power Factor
99 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2597 | AC Voltage (L-L or L-N)
100 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2598 | AC Current (per phase)
101 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2599 | Frequency
102 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2600 | DC Voltage ( String Level)
103 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2601 | DC Current
104 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2602 | DC Power
105 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2603 | Inverter Efficiency
106 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2604 | Daily Energy Yield
107 | DL 01/Inv 75 | DL 01/Inv 75/MR | Data Link | DL2605 | Total Energy Yield
108 | DL 01/Inv 75 | DL 01/Inv 75/S | Data Link | DL2606 | Inverter Running / Stopped
109 | DL 01/Inv 75 | DL 01/Inv 75/S | Data Link | DL2607 | Inverter Grid Connection Status (Connected / Disconnected)
110 | DL 01/Inv 75 | DL 01/Inv 75/S | Data Link | DL2608 | Communication Status (Healthy / Lost)
111 | DL 01/Inv 75 | DL 01/Inv 75/S | Data Link | DL2609 | Remote ON/OFF Status
112 | DL 01/Inv 75 | DL 01/Inv 75/S | Data Link | DL2610 | Active Power Control Mode
113 | DL 01/Inv 75 | DL 01/Inv 75/S | Data Link | DL2611 | Reactive Power Control Mode
114 | DL 01/Inv 75 | DL 01/Inv 75/S | Data Link | DL2612 | Islanding Detection Status
115 | DL 01/Inv 75 | DL 01/Inv 75/S | Data Link | DL2613 | Power Curtailment Status
116 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2614 | General Fault Trip
117 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2615 | Warning Active (Derating, Overtemperature)
118 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2616 | DC Insulation Fault
119 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2617 | Ground Fault
120 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2618 | AC Overvoltage
121 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2619 | AC Undervoltage
122 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2620 | Grid Overfrequency
123 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2621 | Grid Underfrequency
124 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2622 | DC Overvoltage
125 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2623 | Inverter Over temperature
126 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2624 | String Reverse Polarity
127 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2625 | Fan Failure
128 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2626 | Communication Failure
129 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2627 | Power Limitation Active due to Grid Command
130 | DL 01/Inv 75 | DL 01/Inv 75/F | Data Link | DL2628 | Inverter Trip History Available
131 | PVMV - K01 - ASORC - O - A | CB - PVMV - K01 | Data Link | PVMV01 | Circuit breaker open/close position | Colomn B : (cell No./Feeder type (PV or Grid or Asorc Use)/O:Outgoing,I: Incomer,BC:Bus Coupler,BR:Bus Riser/Bus No.)
132 | PVMV - K01 - ASORC - O - A | CB - PVMV - K01 | Data Link | PVMV02 | Circuit breaker trip | Colomn C : (ID Type: PR Protection Relay, MR:Meter - PVMV: Refer to PV Plant MV SWGR - Cell No.)
133 | PVMV - K01 - ASORC - O - A | CB - PVMV - K01 | Data Link | PVMV03 | Spring charged/discharged | Clomn D : ( CB - Circuit Breaker , L - Lockout , FR - Flag Relay , PR : Protection Relay , MR - Meter , ES - Earth Switch , SS : Selector Switch
134 | PVMV - K01 - ASORC - O - A | CB - PVMV - K01 | Data Link | PVMV04 | Test/service position status
135 | PVMV - K01 - ASORC - O - A | SS - PVMV - K01 | Data Link | PVMV05 | Remote/local control status | PV MV Dynamic SLD Visualization
136 | PVMV - K01 - ASORC - O - A | ES - PVMV - K01 | Data Link | PVMV06 | Earth switch open/close position | Status Displayed beside each MV feeder on the SLD
137 | PVMV - K01 - ASORC - O - A | FR - PVMV - K01 | Data Link | PVMV07 | Relay trip Flag | Measurements Displayed on SLD nodes
138 | PVMV - K01 - ASORC - O - A | FR - PVMV - K01 | Data Link | PVMV08 | AC Trip Flag | Protection Functions ( Color Coded Icons )
139 | PVMV - K01 - ASORC - O - A | FR - PVMV - K01 | Data Link | PVMV09 | DC Trip Flag | Power Flow Directions ( Import / Export ) Arrows
140 | PVMV - K01 - ASORC - O - A | FR - PVMV - K01 | Data Link | PVMV10 | MCB Trip Flag | Line color: live (energized) / dead (de-energized)
141 | PVMV - K01 - ASORC - O - A | PR - PVMV - K01 | Data Link | PVMV11 | Protection Relay Status ( Alarm / Trip / Reset ) | Busbar highlight: energized if voltage > threshold
142 | PVMV - K01 - ASORC - O - A | PR - PVMV - K01 | Data Link | PVMV12 | - (67) Directional overcurrent | Blinking: for active fault or trip conditions
143 | PVMV - K01 - ASORC - O - A | PR - PVMV - K01 | Data Link | PVMV13 | - (46) Negative-sequence overcurrent protection
144 | PVMV - K01 - ASORC - O - A | PR - PVMV - K01 | Data Link | PVMV14 | - (47 -) Negative-sequence overvoltage protection
145 | PVMV - K01 - ASORC - O - A | PR - PVMV - K01 | Data Link | PVMV15 | - (50) instantaneous overcurrent
146 | PVMV - K01 - ASORC - O - A | PR - PVMV - K01 | Data Link | PVMV16 | - (51) Time Overcurrent
147 | PVMV - K01 - ASORC - O - A | PR - PVMV - K01 | Data Link | PVMV17 | - (86) Lockout Relay
148 | PVMV - K01 - ASORC - O - A | PR - PVMV - K01 | Data Link | PVMV18 | - (67N) Directional Earth Fault
149 | PVMV - K01 - ASORC - O - A | PR - PVMV - K01 | Data Link | PVMV19 | - (51BF) Circuit breaker failure
150 | PVMV - K01 - ASORC - O - A | MR - PVMV - K01 | Data Link | PVMV20 | Feeder current per phase
151 | PVMV - K01 - ASORC - O - A | MR - PVMV - K01 | Data Link | PVMV21 | Active power (kW) per feeder
152 | PVMV - K01 - ASORC - O - A | MR - PVMV - K01 | Data Link | PVMV22 | Reactive power (kVAr) per feeder
153 | PVMV - K01 - ASORC - O - A | MR - PVMV - K01 | Data Link | PVMV23 | Apparent power (kVA)
154 | PVMV - K01 - ASORC - O - A | MR - PVMV - K01 | Data Link | PVMV24 | Power factor
155 | PVMV - K01 - ASORC - O - A | MR - PVMV - K01 | Data Link | PVMV25 | Frequency
156 | PVMV - K01 - ASORC - O - A | MR - PVMV - K01 | Data Link | PVMV26 | Energy (kWh, kVArh) totalizers
157 | PVMV - K02 - ASORC - O - A | CB - PVMV - K02 | Data Link | PVMV27 | Circuit breaker open/close position
158 | PVMV - K02 - ASORC - O - A | CB - PVMV - K02 | Data Link | PVMV28 | Circuit breaker trip
159 | PVMV - K02 - ASORC - O - A | CB - PVMV - K02 | Data Link | PVMV29 | Spring charged/discharged
160 | PVMV - K02 - ASORC - O - A | CB - PVMV - K02 | Data Link | PVMV30 | Test/service position status
161 | PVMV - K02 - ASORC - O - A | SS - PVMV - K02 | Data Link | PVMV31 | Remote/local control status
162 | PVMV - K02 - ASORC - O - A | ES - PVMV - K02 | Data Link | PVMV32 | Earth switch open/close position
163 | PVMV - K02 - ASORC - O - A | FR - PVMV - K02 | Data Link | PVMV33 | Relay trip Flag
164 | PVMV - K02 - ASORC - O - A | FR - PVMV - K02 | Data Link | PVMV34 | AC Trip Flag
165 | PVMV - K02 - ASORC - O - A | FR - PVMV - K02 | Data Link | PVMV35 | DC Trip Flag
166 | PVMV - K02 - ASORC - O - A | FR - PVMV - K02 | Data Link | PVMV36 | MCB Trip Flag
167 | PVMV - K02 - ASORC - O - A | PR - PVMV - K02 | Data Link | PVMV37 | Protection Relay Status ( Alarm / Trip / Reset )
168 | PVMV - K02 - ASORC - O - A | PR - PVMV - K02 | Data Link | PVMV38 | - (67) Directional overcurrent
169 | PVMV - K02 - ASORC - O - A | PR - PVMV - K02 | Data Link | PVMV39 | - (46) Negative-sequence overcurrent protection
170 | PVMV - K02 - ASORC - O - A | PR - PVMV - K02 | Data Link | PVMV40 | - (47 -) Negative-sequence overvoltage protection
171 | PVMV - K02 - ASORC - O - A | PR - PVMV - K02 | Data Link | PVMV41 | - (50) instantaneous overcurrent
172 | PVMV - K02 - ASORC - O - A | PR - PVMV - K02 | Data Link | PVMV42 | - (51) Time Overcurrent
173 | PVMV - K02 - ASORC - O - A | PR - PVMV - K02 | Data Link | PVMV43 | - (86) Lockout Relay
174 | PVMV - K02 - ASORC - O - A | PR - PVMV - K02 | Data Link | PVMV44 | - (67N) Directional Earth Fault
175 | PVMV - K02 - ASORC - O - A | PR - PVMV - K02 | Data Link | PVMV45 | - (51BF) Circuit breaker failure
176 | PVMV - K02 - ASORC - O - A | MR - PVMV - K02 | Data Link | PVMV46 | Feeder current per phase
177 | PVMV - K02 - ASORC - O - A | MR - PVMV - K02 | Data Link | PVMV47 | Active power (kW) per feeder
178 | PVMV - K02 - ASORC - O - A | MR - PVMV - K02 | Data Link | PVMV48 | Reactive power (kVAr) per feeder
179 | PVMV - K02 - ASORC - O - A | MR - PVMV - K02 | Data Link | PVMV49 | Apparent power (kVA)
180 | PVMV - K02 - ASORC - O - A | MR - PVMV - K02 | Data Link | PVMV50 | Power factor
181 | PVMV - K02 - ASORC - O - A | MR - PVMV - K02 | Data Link | PVMV51 | Frequency
182 | PVMV - K02 - ASORC - O - A | MR - PVMV - K02 | Data Link | PVMV52 | Energy (kWh, kVArh) totalizers
183 | PVMV - K03 - PVS - O - A | CB - PVMV - K03 | Data Link | PVMV53 | Circuit breaker open/close position
184 | PVMV - K03 - PVS - O - A | CB - PVMV - K03 | Data Link | PVMV54 | Circuit breaker trip
185 | PVMV - K03 - PVS - O - A | CB - PVMV - K03 | Data Link | PVMV55 | Spring charged/discharged
186 | PVMV - K03 - PVS - O - A | CB - PVMV - K03 | Data Link | PVMV56 | Test/service position status
187 | PVMV - K03 - PVS - O - A | SS - PVMV - K03 | Data Link | PVMV57 | Remote/local control status
188 | PVMV - K03 - PVS - O - A | ES - PVMV - K03 | Data Link | PVMV58 | Earth switch open/close position
189 | PVMV - K03 - PVS - O - A | FR - PVMV - K03 | Data Link | PVMV59 | Relay trip Flag
190 | PVMV - K03 - PVS - O - A | FR - PVMV - K03 | Data Link | PVMV60 | AC Trip Flag
191 | PVMV - K03 - PVS - O - A | FR - PVMV - K03 | Data Link | PVMV61 | DC Trip Flag
192 | PVMV - K03 - PVS - O - A | FR - PVMV - K03 | Data Link | PVMV62 | MCB Trip Flag
193 | PVMV - K03 - PVS - O - A | PR - PVMV - K03 | Data Link | PVMV63 | Protection Relay Status ( Alarm / Trip / Reset )
194 | PVMV - K03 - PVS - O - A | PR - PVMV - K03 | Data Link | PVMV64 | - (67) Directional overcurrent
195 | PVMV - K03 - PVS - O - A | PR - PVMV - K03 | Data Link | PVMV65 | - (46) Negative-sequence overcurrent protection
196 | PVMV - K03 - PVS - O - A | PR - PVMV - K03 | Data Link | PVMV66 | - (47 -) Negative-sequence overvoltage protection
197 | PVMV - K03 - PVS - O - A | PR - PVMV - K03 | Data Link | PVMV67 | - (50) instantaneous overcurrent
198 | PVMV - K03 - PVS - O - A | PR - PVMV - K03 | Data Link | PVMV68 | - (51) Time Overcurrent
199 | PVMV - K03 - PVS - O - A | PR - PVMV - K03 | Data Link | PVMV69 | - (86) Lockout Relay
200 | PVMV - K03 - PVS - O - A | PR - PVMV - K03 | Data Link | PVMV70 | - (67N) Directional Earth Fault
201 | PVMV - K03 - PVS - O - A | PR - PVMV - K03 | Data Link | PVMV71 | - (51BF) Circuit breaker failure
202 | PVMV - K03 - PVS - O - A | MR - PVMV - K03 | Data Link | PVMV72 | Feeder current per phase
203 | PVMV - K03 - PVS - O - A | MR - PVMV - K03 | Data Link | PVMV73 | Active power (kW) per feeder
204 | PVMV - K03 - PVS - O - A | MR - PVMV - K03 | Data Link | PVMV74 | Reactive power (kVAr) per feeder
205 | PVMV - K03 - PVS - O - A | MR - PVMV - K03 | Data Link | PVMV75 | Apparent power (kVA)
206 | PVMV - K03 - PVS - O - A | MR - PVMV - K03 | Data Link | PVMV76 | Power factor
207 | PVMV - K03 - PVS - O - A | MR - PVMV - K03 | Data Link | PVMV77 | Frequency
208 | PVMV - K03 - PVS - O - A | MR - PVMV - K03 | Data Link | PVMV78 | Energy (kWh, kVArh) totalizers
209 | PVMV - K04 - PVA - O - A | CB - PVMV - K04 | Data Link | PVMV79 | Circuit breaker open/close position
210 | PVMV - K04 - PVA - O - A | CB - PVMV - K04 | Data Link | PVMV80 | Circuit breaker trip
211 | PVMV - K04 - PVA - O - A | CB - PVMV - K04 | Data Link | PVMV81 | Spring charged/discharged
212 | PVMV - K04 - PVA - O - A | CB - PVMV - K04 | Data Link | PVMV82 | Test/service position status
213 | PVMV - K04 - PVA - O - A | SS - PVMV - K04 | Data Link | PVMV83 | Remote/local control status
214 | PVMV - K04 - PVA - O - A | ES - PVMV - K04 | Data Link | PVMV84 | Earth switch open/close position
215 | PVMV - K04 - PVA - O - A | FR - PVMV - K04 | Data Link | PVMV85 | Relay trip Flag
216 | PVMV - K04 - PVA - O - A | FR - PVMV - K04 | Data Link | PVMV86 | AC Trip Flag
217 | PVMV - K04 - PVA - O - A | FR - PVMV - K04 | Data Link | PVMV87 | DC Trip Flag
218 | PVMV - K04 - PVA - O - A | FR - PVMV - K04 | Data Link | PVMV88 | MCB Trip Flag
219 | PVMV - K04 - PVA - O - A | PR - PVMV - K04 | Data Link | PVMV89 | Protection Relay Status ( Alarm / Trip / Reset )
220 | PVMV - K04 - PVA - O - A | PR - PVMV - K04 | Data Link | PVMV90 | - (67) Directional overcurrent
221 | PVMV - K04 - PVA - O - A | PR - PVMV - K04 | Data Link | PVMV91 | - (46) Negative-sequence overcurrent protection
222 | PVMV - K04 - PVA - O - A | PR - PVMV - K04 | Data Link | PVMV92 | - (47 -) Negative-sequence overvoltage protection
223 | PVMV - K04 - PVA - O - A | PR - PVMV - K04 | Data Link | PVMV93 | - (50) instantaneous overcurrent
224 | PVMV - K04 - PVA - O - A | PR - PVMV - K04 | Data Link | PVMV94 | - (51) Time Overcurrent
225 | PVMV - K04 - PVA - O - A | PR - PVMV - K04 | Data Link | PVMV95 | - (86) Lockout Relay
226 | PVMV - K04 - PVA - O - A | PR - PVMV - K04 | Data Link | PVMV96 | - (67N) Directional Earth Fault
227 | PVMV - K04 - PVA - O - A | PR - PVMV - K04 | Data Link | PVMV97 | - (51BF) Circuit breaker failure
228 | PVMV - K04 - PVA - O - A | MR - PVMV - K04 | Data Link | PVMV98 | Feeder current per phase
229 | PVMV - K04 - PVA - O - A | MR - PVMV - K04 | Data Link | PVMV99 | Active power (kW) per feeder
230 | PVMV - K04 - PVA - O - A | MR - PVMV - K04 | Data Link | PVMV100 | Reactive power (kVAr) per feeder
231 | PVMV - K04 - PVA - O - A | MR - PVMV - K04 | Data Link | PVMV101 | Apparent power (kVA)
232 | PVMV - K04 - PVA - O - A | MR - PVMV - K04 | Data Link | PVMV102 | Power factor
233 | PVMV - K04 - PVA - O - A | MR - PVMV - K04 | Data Link | PVMV103 | Frequency
234 | PVMV - K04 - PVA - O - A | MR - PVMV - K04 | Data Link | PVMV104 | Energy (kWh, kVArh) totalizers
235 | PVMV - K05 - PVB - O - A | CB - PVMV - K05 | Data Link | PVMV105 | Circuit breaker open/close position
236 | PVMV - K05 - PVB - O - A | CB - PVMV - K05 | Data Link | PVMV106 | Circuit breaker trip
237 | PVMV - K05 - PVB - O - A | CB - PVMV - K05 | Data Link | PVMV107 | Spring charged/discharged
238 | PVMV - K05 - PVB - O - A | CB - PVMV - K05 | Data Link | PVMV108 | Test/service position status
239 | PVMV - K05 - PVB - O - A | SS - PVMV - K05 | Data Link | PVMV109 | Remote/local control status
240 | PVMV - K05 - PVB - O - A | ES - PVMV - K05 | Data Link | PVMV110 | Earth switch open/close position
241 | PVMV - K05 - PVB - O - A | FR - PVMV - K05 | Data Link | PVMV111 | Relay trip Flag
242 | PVMV - K05 - PVB - O - A | FR - PVMV - K05 | Data Link | PVMV112 | AC Trip Flag
243 | PVMV - K05 - PVB - O - A | FR - PVMV - K05 | Data Link | PVMV113 | DC Trip Flag
244 | PVMV - K05 - PVB - O - A | FR - PVMV - K05 | Data Link | PVMV114 | MCB Trip Flag
245 | PVMV - K05 - PVB - O - A | PR - PVMV - K05 | Data Link | PVMV115 | Protection Relay Status ( Alarm / Trip / Reset )
246 | PVMV - K05 - PVB - O - A | PR - PVMV - K05 | Data Link | PVMV116 | - (67) Directional overcurrent
247 | PVMV - K05 - PVB - O - A | PR - PVMV - K05 | Data Link | PVMV117 | - (46) Negative-sequence overcurrent protection
248 | PVMV - K05 - PVB - O - A | PR - PVMV - K05 | Data Link | PVMV118 | - (47 -) Negative-sequence overvoltage protection
249 | PVMV - K05 - PVB - O - A | PR - PVMV - K05 | Data Link | PVMV119 | - (50) instantaneous overcurrent
250 | PVMV - K05 - PVB - O - A | PR - PVMV - K05 | Data Link | PVMV120 | - (51) Time Overcurrent
251 | PVMV - K05 - PVB - O - A | PR - PVMV - K05 | Data Link | PVMV121 | - (86) Lockout Relay
252 | PVMV - K05 - PVB - O - A | PR - PVMV - K05 | Data Link | PVMV122 | - (67N) Directional Earth Fault
253 | PVMV - K05 - PVB - O - A | PR - PVMV - K05 | Data Link | PVMV123 | - (51BF) Circuit breaker failure
254 | PVMV - K05 - PVB - O - A | MR - PVMV - K05 | Data Link | PVMV124 | Feeder current per phase
255 | PVMV - K05 - PVB - O - A | MR - PVMV - K05 | Data Link | PVMV125 | Active power (kW) per feeder
256 | PVMV - K05 - PVB - O - A | MR - PVMV - K05 | Data Link | PVMV126 | Reactive power (kVAr) per feeder
257 | PVMV - K05 - PVB - O - A | MR - PVMV - K05 | Data Link | PVMV127 | Apparent power (kVA)
258 | PVMV - K05 - PVB - O - A | MR - PVMV - K05 | Data Link | PVMV128 | Power factor
259 | PVMV - K05 - PVB - O - A | MR - PVMV - K05 | Data Link | PVMV129 | Frequency
260 | PVMV - K05 - PVB - O - A | MR - PVMV - K05 | Data Link | PVMV130 | Energy (kWh, kVArh) totalizers
261 | PVMV - K06 - Grid - I - A | CB - PVMV - K06 | Data Link | PVMV131 | Circuit breaker open/close position
262 | PVMV - K06 - Grid - I - A | CB - PVMV - K06 | Data Link | PVMV132 | Circuit breaker trip
263 | PVMV - K06 - Grid - I - A | CB - PVMV - K06 | Data Link | PVMV133 | Spring charged/discharged
264 | PVMV - K06 - Grid - I - A | CB - PVMV - K06 | Data Link | PVMV134 | Test/service position status
265 | PVMV - K06 - Grid - I - A | SS - PVMV - K06 | Data Link | PVMV135 | Remote/local control status
266 | PVMV - K06 - Grid - I - A | ES - PVMV - K06 | Data Link | PVMV136 | Earth switch open/close position
267 | PVMV - K06 - Grid - I - A | FR - PVMV - K06 | Data Link | PVMV137 | Relay trip Flag
268 | PVMV - K06 - Grid - I - A | FR - PVMV - K06 | Data Link | PVMV138 | AC Trip Flag
269 | PVMV - K06 - Grid - I - A | FR - PVMV - K06 | Data Link | PVMV139 | DC Trip Flag
270 | PVMV - K06 - Grid - I - A | FR - PVMV - K06 | Data Link | PVMV140 | MCB Trip Flag
271 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV141 | Protection Relay Status ( Alarm / Trip / Reset )
272 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV142 | - (67) Directional overcurrent
273 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV143 | - (46) Negative-sequence overcurrent protection
274 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV144 | - (47 -) Negative-sequence overvoltage protection
275 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV145 | - (50) instantaneous overcurrent
276 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV146 | - (51) Time Overcurrent
277 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV147 | - (86) Lockout Relay
278 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV148 | - (67N) Directional Earth Fault
279 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV149 | - (27) Under voltage
280 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV150 | - (59) Over voltage
281 | PVMV - K06 - Grid - I - A | PR - PVMV - K06 | Data Link | PVMV151 | - (51BF) Circuit breaker failure
282 | PVMV - K06 - Grid - I - A | MR - PVMV - K06 | Data Link | PVMV152 | Bus voltage (phase-to-phase)
283 | PVMV - K06 - Grid - I - A | MR - PVMV - K06 | Data Link | PVMV153 | Feeder current per phase
284 | PVMV - K06 - Grid - I - A | MR - PVMV - K06 | Data Link | PVMV154 | Active power (kW) per feeder
285 | PVMV - K06 - Grid - I - A | MR - PVMV - K06 | Data Link | PVMV155 | Reactive power (kVAr) per feeder
286 | PVMV - K06 - Grid - I - A | MR - PVMV - K06 | Data Link | PVMV156 | Apparent power (kVA)
287 | PVMV - K06 - Grid - I - A | MR - PVMV - K06 | Data Link | PVMV157 | Power factor
288 | PVMV - K06 - Grid - I - A | MR - PVMV - K06 | Data Link | PVMV158 | Frequency
289 | PVMV - K06 - Grid - I - A | MR - PVMV - K06 | Data Link | PVMV159 | Energy (kWh, kVArh) totalizers
290 | PVMV - K07 - Coupler - BC - A/B | CB - PVMV - K07 | Data Link | PVMV160 | Circuit breaker open/close position
291 | PVMV - K07 - Coupler - BC - A/B | CB - PVMV - K07 | Data Link | PVMV161 | Circuit breaker trip
292 | PVMV - K07 - Coupler - BC - A/B | CB - PVMV - K07 | Data Link | PVMV162 | Spring charged/discharged
293 | PVMV - K07 - Coupler - BC - A/B | CB - PVMV - K07 | Data Link | PVMV163 | Test/service position status
294 | PVMV - K07 - Coupler - BC - A/B | SS - PVMV - K07 | Data Link | PVMV164 | Remote/local control status
295 | PVMV - K07 - Coupler - BC - A/B | ES - PVMV - K07 | Data Link | PVMV165 | Earth switch open/close position
296 | PVMV - K07 - Coupler - BC - A/B | FR - PVMV - K07 | Data Link | PVMV166 | Relay trip Flag
297 | PVMV - K07 - Coupler - BC - A/B | FR - PVMV - K07 | Data Link | PVMV167 | AC Trip Flag
298 | PVMV - K07 - Coupler - BC - A/B | FR - PVMV - K07 | Data Link | PVMV168 | DC Trip Flag
299 | PVMV - K07 - Coupler - BC - A/B | FR - PVMV - K07 | Data Link | PVMV169 | MCB Trip Flag
300 | PVMV - K07 - Coupler - BC - A/B | PR - PVMV - K07 | Data Link | PVMV170 | Protection Relay Status ( Alarm / Trip / Reset )
301 | PVMV - K07 - Coupler - BC - A/B | PR - PVMV - K07 | Data Link | PVMV171 | - (67) Directional overcurrent
302 | PVMV - K07 - Coupler - BC - A/B | PR - PVMV - K07 | Data Link | PVMV172 | - (46) Negative-sequence overcurrent protection
303 | PVMV - K07 - Coupler - BC - A/B | PR - PVMV - K07 | Data Link | PVMV173 | - (47 -) Negative-sequence overvoltage protection
304 | PVMV - K07 - Coupler - BC - A/B | PR - PVMV - K07 | Data Link | PVMV174 | - (50) instantaneous overcurrent
305 | PVMV - K07 - Coupler - BC - A/B | PR - PVMV - K07 | Data Link | PVMV175 | - (51) Time Overcurrent
306 | PVMV - K07 - Coupler - BC - A/B | PR - PVMV - K07 | Data Link | PVMV176 | - (86) Lockout Relay
307 | PVMV - K07 - Coupler - BC - A/B | PR - PVMV - K07 | Data Link | PVMV177 | - (67N) Directional Earth Fault
308 | PVMV - K07 - Coupler - BC - A/B | PR - PVMV - K07 | Data Link | PVMV178 | - (51BF) Circuit breaker failure
309 | PVMV - K07 - Coupler - BC - A/B | MR - PVMV - K07 | Data Link | PVMV179 | Feeder current per phase
310 | PVMV - K07 - Coupler - BC - A/B | MR - PVMV - K07 | Data Link | PVMV180 | Active power (kW) per feeder
311 | PVMV - K07 - Coupler - BC - A/B | MR - PVMV - K07 | Data Link | PVMV181 | Reactive power (kVAr) per feeder
312 | PVMV - K07 - Coupler - BC - A/B | MR - PVMV - K07 | Data Link | PVMV182 | Apparent power (kVA)
313 | PVMV - K07 - Coupler - BC - A/B | MR - PVMV - K07 | Data Link | PVMV183 | Power factor
314 | PVMV - K07 - Coupler - BC - A/B | MR - PVMV - K07 | Data Link | PVMV184 | Frequency
315 | PVMV - K07 - Coupler - BC - A/B | MR - PVMV - K07 | Data Link | PVMV185 | Energy (kWh, kVArh) totalizers
316 | PVMV - K08 - Riser - BR - A/B | CB - PVMV - K08 | Data Link | PVMV186 | Circuit breaker open/close position
317 | PVMV - K08 - Riser - BR - A/B | CB - PVMV - K08 | Data Link | PVMV187 | Circuit breaker trip
318 | PVMV - K08 - Riser - BR - A/B | CB - PVMV - K08 | Data Link | PVMV188 | Spring charged/discharged
319 | PVMV - K08 - Riser - BR - A/B | CB - PVMV - K08 | Data Link | PVMV189 | Test/service position status
320 | PVMV - K08 - Riser - BR - A/B | SS - PVMV - K08 | Data Link | PVMV190 | Remote/local control status
321 | PVMV - K08 - Riser - BR - A/B | SS - PVMV - K08 | Data Link | PVMV191 | Electrical Interlock ( 2 out of 3 ) control status
322 | PVMV - K08 - Riser - BR - A/B | ES - PVMV - K08 | Data Link | PVMV192 | Earth switch open/close position
323 | PVMV - K08 - Riser - BR - A/B | FR - PVMV - K08 | Data Link | PVMV193 | Relay trip Flag
324 | PVMV - K08 - Riser - BR - A/B | FR - PVMV - K08 | Data Link | PVMV194 | AC Trip Flag
325 | PVMV - K08 - Riser - BR - A/B | FR - PVMV - K08 | Data Link | PVMV195 | DC Trip Flag
326 | PVMV - K08 - Riser - BR - A/B | FR - PVMV - K08 | Data Link | PVMV196 | MCB Trip Flag
327 | PVMV - K08 - Riser - BR - A/B | PR - PVMV - K08 | Data Link | PVMV197 | Protection Relay Status ( Alarm / Trip / Reset )
328 | PVMV - K08 - Riser - BR - A/B | PR - PVMV - K08 | Data Link | PVMV198 | - (25) synchro- check for BC
329 | PVMV - K08 - Riser - BR - A/B | PR - PVMV - K08 | Data Link | PVMV199 | - (47 +) Positive-sequence undervoltage protection for BC
330 | PVMV - K08 - Riser - BR - A/B | PR - PVMV - K08 | Data Link | PVMV200 | - (47 -) Negative-sequence overvoltage protection for BC
331 | PVMV - K08 - Riser - BR - A/B | PR - PVMV - K08 | Data Link | PVMV201 | - (81) Frequency protection for BC
332 | PVMV - K08 - Riser - BR - A/B | MR - PVMV - K08 | Data Link | PVMV202 | Bus voltage (phase-to-phase)
333 | PVMV - K08 - Riser - BR - A/B | MR - PVMV - K08 | Data Link | PVMV203 | Feeder current per phase
334 | PVMV - K08 - Riser - BR - A/B | MR - PVMV - K08 | Data Link | PVMV204 | Active power (kW) per feeder
335 | PVMV - K08 - Riser - BR - A/B | MR - PVMV - K08 | Data Link | PVMV205 | Reactive power (kVAr) per feeder
336 | PVMV - K08 - Riser - BR - A/B | MR - PVMV - K08 | Data Link | PVMV206 | Apparent power (kVA)
337 | PVMV - K08 - Riser - BR - A/B | MR - PVMV - K08 | Data Link | PVMV207 | Power factor
338 | PVMV - K08 - Riser - BR - A/B | MR - PVMV - K08 | Data Link | PVMV208 | Frequency
339 | PVMV - K08 - Riser - BR - A/B | MR - PVMV - K08 | Data Link | PVMV209 | Energy (kWh, kVArh) totalizers
340 | PVMV - K09 - Grid - I - B | CB - PVMV - K09 | Data Link | PVMV210 | Circuit breaker open/close position
341 | PVMV - K09 - Grid - I - B | CB - PVMV - K09 | Data Link | PVMV211 | Circuit breaker trip
342 | PVMV - K09 - Grid - I - B | CB - PVMV - K09 | Data Link | PVMV212 | Spring charged/discharged
343 | PVMV - K09 - Grid - I - B | CB - PVMV - K09 | Data Link | PVMV213 | Test/service position status
344 | PVMV - K09 - Grid - I - B | SS - PVMV - K09 | Data Link | PVMV214 | Remote/local control status
345 | PVMV - K09 - Grid - I - B | ES - PVMV - K09 | Data Link | PVMV215 | Earth switch open/close position
346 | PVMV - K09 - Grid - I - B | FR - PVMV - K09 | Data Link | PVMV216 | Relay trip Flag
347 | PVMV - K09 - Grid - I - B | FR - PVMV - K09 | Data Link | PVMV217 | AC Trip Flag
348 | PVMV - K09 - Grid - I - B | FR - PVMV - K09 | Data Link | PVMV218 | DC Trip Flag
349 | PVMV - K09 - Grid - I - B | FR - PVMV - K09 | Data Link | PVMV219 | MCB Trip Flag
350 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV220 | Protection Relay Status ( Alarm / Trip / Reset )
351 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV221 | - (67) Directional overcurrent
352 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV222 | - (46) Negative-sequence overcurrent protection
353 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV223 | - (47 -) Negative-sequence overvoltage protection
354 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV224 | - (50) instantaneous overcurrent
355 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV225 | - (51) Time Overcurrent
356 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV226 | - (86) Lockout Relay
357 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV227 | - (67N) Directional Earth Fault
358 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV228 | - (27) Under voltage
359 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV229 | - (59) Over voltage
360 | PVMV - K09 - Grid - I - B | PR - PVMV - K09 | Data Link | PVMV230 | - (51BF) Circuit breaker failure
361 | PVMV - K09 - Grid - I - B | MR - PVMV - K09 | Data Link | PVMV231 | Bus voltage (phase-to-phase)
362 | PVMV - K09 - Grid - I - B | MR - PVMV - K09 | Data Link | PVMV232 | Feeder current per phase
363 | PVMV - K09 - Grid - I - B | MR - PVMV - K09 | Data Link | PVMV233 | Active power (kW) per feeder
364 | PVMV - K09 - Grid - I - B | MR - PVMV - K09 | Data Link | PVMV234 | Reactive power (kVAr) per feeder
365 | PVMV - K09 - Grid - I - B | MR - PVMV - K09 | Data Link | PVMV235 | Apparent power (kVA)
366 | PVMV - K09 - Grid - I - B | MR - PVMV - K09 | Data Link | PVMV236 | Power factor
367 | PVMV - K09 - Grid - I - B | MR - PVMV - K09 | Data Link | PVMV237 | Frequency
368 | PVMV - K09 - Grid - I - B | MR - PVMV - K09 | Data Link | PVMV238 | Energy (kWh, kVArh) totalizers
369 | PVMV - K010 - PVB - O - B | CB - PVMV - K10 | Data Link | PVMV239 | Circuit breaker open/close position
370 | PVMV - K010 - PVB - O - B | CB - PVMV - K10 | Data Link | PVMV240 | Circuit breaker trip
371 | PVMV - K010 - PVB - O - B | CB - PVMV - K10 | Data Link | PVMV241 | Spring charged/discharged
372 | PVMV - K010 - PVB - O - B | CB - PVMV - K10 | Data Link | PVMV242 | Test/service position status
373 | PVMV - K010 - PVB - O - B | SS - PVMV - K10 | Data Link | PVMV243 | Remote/local control status
374 | PVMV - K010 - PVB - O - B | ES - PVMV - K10 | Data Link | PVMV244 | Earth switch open/close position
375 | PVMV - K010 - PVB - O - B | FR - PVMV - K10 | Data Link | PVMV245 | Relay trip Flag
376 | PVMV - K010 - PVB - O - B | FR - PVMV - K10 | Data Link | PVMV246 | AC Trip Flag
377 | PVMV - K010 - PVB - O - B | FR - PVMV - K10 | Data Link | PVMV247 | DC Trip Flag
378 | PVMV - K010 - PVB - O - B | FR - PVMV - K10 | Data Link | PVMV248 | MCB Trip Flag
379 | PVMV - K010 - PVB - O - B | PR - PVMV - K10 | Data Link | PVMV249 | Protection Relay Status ( Alarm / Trip / Reset )
380 | PVMV - K010 - PVB - O - B | PR - PVMV - K10 | Data Link | PVMV250 | - (67) Directional overcurrent
381 | PVMV - K010 - PVB - O - B | PR - PVMV - K10 | Data Link | PVMV251 | - (46) Negative-sequence overcurrent protection
382 | PVMV - K010 - PVB - O - B | PR - PVMV - K10 | Data Link | PVMV252 | - (47 -) Negative-sequence overvoltage protection
383 | PVMV - K010 - PVB - O - B | PR - PVMV - K10 | Data Link | PVMV253 | - (50) instantaneous overcurrent
384 | PVMV - K010 - PVB - O - B | PR - PVMV - K10 | Data Link | PVMV254 | - (51) Time Overcurrent
385 | PVMV - K010 - PVB - O - B | PR - PVMV - K10 | Data Link | PVMV255 | - (86) Lockout Relay
386 | PVMV - K010 - PVB - O - B | PR - PVMV - K10 | Data Link | PVMV256 | - (67N) Directional Earth Fault
387 | PVMV - K010 - PVB - O - B | PR - PVMV - K10 | Data Link | PVMV257 | - (51BF) Circuit breaker failure
388 | PVMV - K010 - PVB - O - B | MR - PVMV - K10 | Data Link | PVMV258 | Feeder current per phase
389 | PVMV - K010 - PVB - O - B | MR - PVMV - K10 | Data Link | PVMV259 | Active power (kW) per feeder
390 | PVMV - K010 - PVB - O - B | MR - PVMV - K10 | Data Link | PVMV260 | Reactive power (kVAr) per feeder
391 | PVMV - K010 - PVB - O - B | MR - PVMV - K10 | Data Link | PVMV261 | Apparent power (kVA)
392 | PVMV - K010 - PVB - O - B | MR - PVMV - K10 | Data Link | PVMV262 | Power factor
393 | PVMV - K010 - PVB - O - B | MR - PVMV - K10 | Data Link | PVMV263 | Frequency
394 | PVMV - K010 - PVB - O - B | MR - PVMV - K10 | Data Link | PVMV264 | Energy (kWh, kVArh) totalizers
395 | PVMV - K011 - PVA - O - B | CB - PVMV - K11 | Data Link | PVMV265 | Circuit breaker open/close position
396 | PVMV - K011 - PVA - O - B | CB - PVMV - K11 | Data Link | PVMV266 | Circuit breaker trip
397 | PVMV - K011 - PVA - O - B | CB - PVMV - K11 | Data Link | PVMV267 | Spring charged/discharged
398 | PVMV - K011 - PVA - O - B | CB - PVMV - K11 | Data Link | PVMV268 | Test/service position status
399 | PVMV - K011 - PVA - O - B | SS - PVMV - K11 | Data Link | PVMV269 | Remote/local control status
400 | PVMV - K011 - PVA - O - B | ES - PVMV - K11 | Data Link | PVMV270 | Earth switch open/close position
401 | PVMV - K011 - PVA - O - B | FR - PVMV - K11 | Data Link | PVMV271 | Relay trip Flag
402 | PVMV - K011 - PVA - O - B | FR - PVMV - K11 | Data Link | PVMV272 | AC Trip Flag
403 | PVMV - K011 - PVA - O - B | FR - PVMV - K11 | Data Link | PVMV273 | DC Trip Flag
404 | PVMV - K011 - PVA - O - B | FR - PVMV - K11 | Data Link | PVMV274 | MCB Trip Flag
405 | PVMV - K011 - PVA - O - B | PR - PVMV - K11 | Data Link | PVMV275 | Protection Relay Status ( Alarm / Trip / Reset )
406 | PVMV - K011 - PVA - O - B | PR - PVMV - K11 | Data Link | PVMV276 | - (67) Directional overcurrent
407 | PVMV - K011 - PVA - O - B | PR - PVMV - K11 | Data Link | PVMV277 | - (46) Negative-sequence overcurrent protection
408 | PVMV - K011 - PVA - O - B | PR - PVMV - K11 | Data Link | PVMV278 | - (47 -) Negative-sequence overvoltage protection
409 | PVMV - K011 - PVA - O - B | PR - PVMV - K11 | Data Link | PVMV279 | - (50) instantaneous overcurrent
410 | PVMV - K011 - PVA - O - B | PR - PVMV - K11 | Data Link | PVMV280 | - (51) Time Overcurrent
411 | PVMV - K011 - PVA - O - B | PR - PVMV - K11 | Data Link | PVMV281 | - (86) Lockout Relay
412 | PVMV - K011 - PVA - O - B | PR - PVMV - K11 | Data Link | PVMV282 | - (67N) Directional Earth Fault
413 | PVMV - K011 - PVA - O - B | PR - PVMV - K11 | Data Link | PVMV283 | - (51BF) Circuit breaker failure
414 | PVMV - K011 - PVA - O - B | MR - PVMV - K11 | Data Link | PVMV284 | Feeder current per phase
415 | PVMV - K011 - PVA - O - B | MR - PVMV - K11 | Data Link | PVMV285 | Active power (kW) per feeder
416 | PVMV - K011 - PVA - O - B | MR - PVMV - K11 | Data Link | PVMV286 | Reactive power (kVAr) per feeder
417 | PVMV - K011 - PVA - O - B | MR - PVMV - K11 | Data Link | PVMV287 | Apparent power (kVA)
418 | PVMV - K011 - PVA - O - B | MR - PVMV - K11 | Data Link | PVMV288 | Power factor
419 | PVMV - K011 - PVA - O - B | MR - PVMV - K11 | Data Link | PVMV289 | Frequency
420 | PVMV - K011 - PVA - O - B | MR - PVMV - K11 | Data Link | PVMV290 | Energy (kWh, kVArh) totalizers
421 | PVMV - K012 - PVS - O - B | CB - PVMV - K12 | Data Link | PVMV291 | Circuit breaker open/close position
422 | PVMV - K012 - PVS - O - B | CB - PVMV - K12 | Data Link | PVMV292 | Circuit breaker trip
423 | PVMV - K012 - PVS - O - B | CB - PVMV - K12 | Data Link | PVMV293 | Spring charged/discharged
424 | PVMV - K012 - PVS - O - B | CB - PVMV - K12 | Data Link | PVMV294 | Test/service position status
425 | PVMV - K012 - PVS - O - B | SS - PVMV - K12 | Data Link | PVMV295 | Remote/local control status
426 | PVMV - K012 - PVS - O - B | ES - PVMV - K12 | Data Link | PVMV296 | Earth switch open/close position
427 | PVMV - K012 - PVS - O - B | FR - PVMV - K12 | Data Link | PVMV297 | Relay trip Flag
428 | PVMV - K012 - PVS - O - B | FR - PVMV - K12 | Data Link | PVMV298 | AC Trip Flag
429 | PVMV - K012 - PVS - O - B | FR - PVMV - K12 | Data Link | PVMV299 | DC Trip Flag
430 | PVMV - K012 - PVS - O - B | FR - PVMV - K12 | Data Link | PVMV300 | MCB Trip Flag
431 | PVMV - K012 - PVS - O - B | PR - PVMV - K12 | Data Link | PVMV301 | Protection Relay Status ( Alarm / Trip / Reset )
432 | PVMV - K012 - PVS - O - B | PR - PVMV - K12 | Data Link | PVMV302 | - (67) Directional overcurrent
433 | PVMV - K012 - PVS - O - B | PR - PVMV - K12 | Data Link | PVMV303 | - (46) Negative-sequence overcurrent protection
434 | PVMV - K012 - PVS - O - B | PR - PVMV - K12 | Data Link | PVMV304 | - (47 -) Negative-sequence overvoltage protection
435 | PVMV - K012 - PVS - O - B | PR - PVMV - K12 | Data Link | PVMV305 | - (50) instantaneous overcurrent
436 | PVMV - K012 - PVS - O - B | PR - PVMV - K12 | Data Link | PVMV306 | - (51) Time Overcurrent
437 | PVMV - K012 - PVS - O - B | PR - PVMV - K12 | Data Link | PVMV307 | - (86) Lockout Relay
438 | PVMV - K012 - PVS - O - B | PR - PVMV - K12 | Data Link | PVMV308 | - (67N) Directional Earth Fault
439 | PVMV - K012 - PVS - O - B | PR - PVMV - K12 | Data Link | PVMV309 | - (51BF) Circuit breaker failure
440 | PVMV - K012 - PVS - O - B | MR - PVMV - K12 | Data Link | PVMV310 | Feeder current per phase
441 | PVMV - K012 - PVS - O - B | MR - PVMV - K12 | Data Link | PVMV311 | Active power (kW) per feeder
442 | PVMV - K012 - PVS - O - B | MR - PVMV - K12 | Data Link | PVMV312 | Reactive power (kVAr) per feeder
443 | PVMV - K012 - PVS - O - B | MR - PVMV - K12 | Data Link | PVMV313 | Apparent power (kVA)
444 | PVMV - K012 - PVS - O - B | MR - PVMV - K12 | Data Link | PVMV314 | Power factor
445 | PVMV - K012 - PVS - O - B | MR - PVMV - K12 | Data Link | PVMV315 | Frequency
446 | PVMV - K012 - PVS - O - B | MR - PVMV - K12 | Data Link | PVMV316 | Energy (kWh, kVArh) totalizers
447 | PVMV - K013 - ASORC - O - B | CB - PVMV - K13 | Data Link | PVMV317 | Circuit breaker open/close position
448 | PVMV - K013 - ASORC - O - B | CB - PVMV - K13 | Data Link | PVMV318 | Circuit breaker trip
449 | PVMV - K013 - ASORC - O - B | CB - PVMV - K13 | Data Link | PVMV319 | Spring charged/discharged
450 | PVMV - K013 - ASORC - O - B | CB - PVMV - K13 | Data Link | PVMV320 | Test/service position status
451 | PVMV - K013 - ASORC - O - B | SS - PVMV - K13 | Data Link | PVMV321 | Remote/local control status
452 | PVMV - K013 - ASORC - O - B | ES - PVMV - K13 | Data Link | PVMV322 | Earth switch open/close position
453 | PVMV - K013 - ASORC - O - B | FR - PVMV - K13 | Data Link | PVMV323 | Relay trip Flag
454 | PVMV - K013 - ASORC - O - B | FR - PVMV - K13 | Data Link | PVMV324 | AC Trip Flag
455 | PVMV - K013 - ASORC - O - B | FR - PVMV - K13 | Data Link | PVMV325 | DC Trip Flag
456 | PVMV - K013 - ASORC - O - B | FR - PVMV - K13 | Data Link | PVMV326 | MCB Trip Flag
457 | PVMV - K013 - ASORC - O - B | PR - PVMV - K13 | Data Link | PVMV327 | Protection Relay Status ( Alarm / Trip / Reset )
458 | PVMV - K013 - ASORC - O - B | PR - PVMV - K13 | Data Link | PVMV328 | - (67) Directional overcurrent
459 | PVMV - K013 - ASORC - O - B | PR - PVMV - K13 | Data Link | PVMV329 | - (46) Negative-sequence overcurrent protection
460 | PVMV - K013 - ASORC - O - B | PR - PVMV - K13 | Data Link | PVMV330 | - (47 -) Negative-sequence overvoltage protection
461 | PVMV - K013 - ASORC - O - B | PR - PVMV - K13 | Data Link | PVMV331 | - (50) instantaneous overcurrent
462 | PVMV - K013 - ASORC - O - B | PR - PVMV - K13 | Data Link | PVMV332 | - (51) Time Overcurrent
463 | PVMV - K013 - ASORC - O - B | PR - PVMV - K13 | Data Link | PVMV333 | - (86) Lockout Relay
464 | PVMV - K013 - ASORC - O - B | PR - PVMV - K13 | Data Link | PVMV334 | - (67N) Directional Earth Fault
465 | PVMV - K013 - ASORC - O - B | PR - PVMV - K13 | Data Link | PVMV335 | - (51BF) Circuit breaker failure
466 | PVMV - K013 - ASORC - O - B | MR - PVMV - K13 | Data Link | PVMV336 | Feeder current per phase
467 | PVMV - K013 - ASORC - O - B | MR - PVMV - K13 | Data Link | PVMV337 | Active power (kW) per feeder
468 | PVMV - K013 - ASORC - O - B | MR - PVMV - K13 | Data Link | PVMV338 | Reactive power (kVAr) per feeder
469 | PVMV - K013 - ASORC - O - B | MR - PVMV - K13 | Data Link | PVMV339 | Apparent power (kVA)
470 | PVMV - K013 - ASORC - O - B | MR - PVMV - K13 | Data Link | PVMV340 | Power factor
471 | PVMV - K013 - ASORC - O - B | MR - PVMV - K13 | Data Link | PVMV341 | Frequency
472 | PVMV - K013 - ASORC - O - B | MR - PVMV - K13 | Data Link | PVMV342 | Energy (kWh, kVArh) totalizers
473 | PVMV - K014 - ASORC - O - B | CB - PVMV - K14 | Data Link | PVMV343 | Circuit breaker open/close position
474 | PVMV - K014 - ASORC - O - B | CB - PVMV - K14 | Data Link | PVMV344 | Circuit breaker trip
475 | PVMV - K014 - ASORC - O - B | CB - PVMV - K14 | Data Link | PVMV345 | Spring charged/discharged
476 | PVMV - K014 - ASORC - O - B | CB - PVMV - K14 | Data Link | PVMV346 | Test/service position status
477 | PVMV - K014 - ASORC - O - B | SS - PVMV - K14 | Data Link | PVMV347 | Remote/local control status
478 | PVMV - K014 - ASORC - O - B | ES - PVMV - K14 | Data Link | PVMV348 | Earth switch open/close position
479 | PVMV - K014 - ASORC - O - B | FR - PVMV - K14 | Data Link | PVMV349 | Relay trip Flag
480 | PVMV - K014 - ASORC - O - B | FR - PVMV - K14 | Data Link | PVMV350 | AC Trip Flag
481 | PVMV - K014 - ASORC - O - B | FR - PVMV - K14 | Data Link | PVMV351 | DC Trip Flag
482 | PVMV - K014 - ASORC - O - B | FR - PVMV - K14 | Data Link | PVMV352 | MCB Trip Flag
483 | PVMV - K014 - ASORC - O - B | PR - PVMV - K14 | Data Link | PVMV353 | Protection Relay Status ( Alarm / Trip / Reset )
484 | PVMV - K014 - ASORC - O - B | PR - PVMV - K14 | Data Link | PVMV354 | - (67) Directional overcurrent
485 | PVMV - K014 - ASORC - O - B | PR - PVMV - K14 | Data Link | PVMV355 | - (46) Negative-sequence overcurrent protection
486 | PVMV - K014 - ASORC - O - B | PR - PVMV - K14 | Data Link | PVMV356 | - (47 -) Negative-sequence overvoltage protection
487 | PVMV - K014 - ASORC - O - B | PR - PVMV - K14 | Data Link | PVMV357 | - (50) instantaneous overcurrent
488 | PVMV - K014 - ASORC - O - B | PR - PVMV - K14 | Data Link | PVMV358 | - (51) Time Overcurrent
489 | PVMV - K014 - ASORC - O - B | PR - PVMV - K14 | Data Link | PVMV359 | - (86) Lockout Relay
490 | PVMV - K014 - ASORC - O - B | PR - PVMV - K14 | Data Link | PVMV360 | - (67N) Directional Earth Fault
491 | PVMV - K014 - ASORC - O - B | PR - PVMV - K14 | Data Link | PVMV361 | - (51BF) Circuit breaker failure
492 | PVMV - K014 - ASORC - O - B | MR - PVMV - K14 | Data Link | PVMV362 | Feeder current per phase
493 | PVMV - K014 - ASORC - O - B | MR - PVMV - K14 | Data Link | PVMV363 | Active power (kW) per feeder
494 | PVMV - K014 - ASORC - O - B | MR - PVMV - K14 | Data Link | PVMV364 | Reactive power (kVAr) per feeder
495 | PVMV - K014 - ASORC - O - B | MR - PVMV - K14 | Data Link | PVMV365 | Apparent power (kVA)
496 | PVMV - K014 - ASORC - O - B | MR - PVMV - K14 | Data Link | PVMV366 | Power factor
497 | PVMV - K014 - ASORC - O - B | MR - PVMV - K14 | Data Link | PVMV367 | Frequency
498 | PVMV - K014 - ASORC - O - B | MR - PVMV - K14 | Data Link | PVMV368 | Energy (kWh, kVArh) totalizers

## REFF.
PV SCADA Signal List
Signal
No | Equipment | Source IED Name | Description
1 | J02/PV O/G-1 | PR-PVDS-J02 | AC MCBs trip
2 | J02/PV O/G-1 | PR-PVDS-J02 | DC MCBs trip
3 | J02/PV O/G-1 | PR-PVDS-J02 | Main AC MCB Trip
4 | J02/PV O/G-1 | PR-PVDS-J02 | Main DC MCB Trip
5 | J02/PV O/G-1 | PR-PVDS-J02 | Protection relay faulty
6 | J02/PV O/G-1 | PR-PVDS-J02 | Local / Remote SS on Local
7 | J02/PV O/G-1 | PR-PVDS-J02 | Local / Remote SS on Remote
8 | J02/PV O/G-1 | PR-PVDS-J02 | Disconnector ON
9 | J02/PV O/G-1 | PR-PVDS-J02 | Disconnector OFF
10 | J02/PV O/G-1 | PR-PVDS-J02 | Earth Switch ON
11 | J02/PV O/G-1 | PR-PVDS-J02 | Earth Switch OFF
12 | J02/PV O/G-1 | PR-PVDS-J02 | TCS Faulty
13 | J02/PV O/G-1 | PR-PVDS-J02 | Lockout Trip
14 | J02/PV O/G-1 | PR-PVDS-J02 | CB Spring Charged
15 | J02/PV O/G-1 | PR-PVDS-J02 | CB Gas Pressure Loss
16 | J02/PV O/G-1 | PR-PVDS-J02 | CB Gas Pressure Min
17 | J02/PV O/G-1 | PR-PVDS-J02 | VT MCB Tripped Core 01 > BC
18 | J02/PV O/G-1 | PR-PVDS-J02 | VT MCB Tripped Core 02 > BC
19 | J02/PV O/G-1 | PR-PVDS-J02 | O/C Protection Operated
20 | J02/PV O/G-1 | PR-PVDS-J02 | Earth Fault Protection Operated
21 | J02/PV O/G-1 | PR-PVDS-J02 | Over Voltage Protection Operated
22 | J02/PV O/G-1 | PR-PVDS-J02 | Under Voltage Protection Operated
23 | J02/PV O/G-1 | PR-PVDS-J02 | Line Diff. Protection Operated
24 | J06/PV O/G-2 | PR-PVDS-J06 | AC MCBs trip
25 | J06/PV O/G-2 | PR-PVDS-J06 | DC MCBs trip
26 | J06/PV O/G-2 | PR-PVDS-J06 | Main AC MCB Trip
27 | J06/PV O/G-2 | PR-PVDS-J06 | Main DC MCB Trip
28 | J06/PV O/G-2 | PR-PVDS-J06 | Protection relay faulty
29 | J06/PV O/G-2 | PR-PVDS-J06 | Local / Remote SS on Local
30 | J06/PV O/G-2 | PR-PVDS-J06 | Local / Remote SS on Remote
31 | J06/PV O/G-2 | PR-PVDS-J06 | Disconnector ON
32 | J06/PV O/G-2 | PR-PVDS-J06 | Disconnector OFF
33 | J06/PV O/G-2 | PR-PVDS-J06 | Earth Switch ON
34 | J06/PV O/G-2 | PR-PVDS-J06 | Earth Switch OFF
35 | J06/PV O/G-2 | PR-PVDS-J06 | TCS Faulty
36 | J06/PV O/G-2 | PR-PVDS-J06 | Lockout Trip
37 | J06/PV O/G-2 | PR-PVDS-J06 | CB Spring Charged
38 | J06/PV O/G-2 | PR-PVDS-J06 | CB Gas Pressure Loss
39 | J06/PV O/G-2 | PR-PVDS-J06 | CB Gas Pressure Min
40 | J06/PV O/G-2 | PR-PVDS-J06 | VT MCB Tripped Core 01 > BC
41 | J06/PV O/G-2 | PR-PVDS-J06 | VT MCB Tripped Core 02 > BC
42 | J06/PV O/G-2 | PR-PVDS-J06 | O/C Protection Operated
43 | J06/PV O/G-2 | PR-PVDS-J06 | Earth Fault Protection Operated
44 | J06/PV O/G-2 | PR-PVDS-J06 | Over Voltage Protection Operated
45 | J06/PV O/G-2 | PR-PVDS-J06 | Under Voltage Protection Operated
46 | J06/PV O/G-2 | PR-PVDS-J06 | Line Diff. Protection Operated
47 | J08/PV O/G-3 | PR-PVDS-J08 | AC MCBs trip
48 | J08/PV O/G-3 | PR-PVDS-J08 | DC MCBs trip
49 | J08/PV O/G-3 | PR-PVDS-J08 | Main AC MCB Trip
50 | J08/PV O/G-3 | PR-PVDS-J08 | Main DC MCB Trip
51 | J08/PV O/G-3 | PR-PVDS-J08 | Protection relay faulty
52 | J08/PV O/G-3 | PR-PVDS-J08 | Local / Remote SS on Local
53 | J08/PV O/G-3 | PR-PVDS-J08 | Local / Remote SS on Remote
54 | J08/PV O/G-3 | PR-PVDS-J08 | Disconnector ON
55 | J08/PV O/G-3 | PR-PVDS-J08 | Disconnector OFF
56 | J08/PV O/G-3 | PR-PVDS-J08 | Earth Switch ON
57 | J08/PV O/G-3 | PR-PVDS-J08 | Earth Switch OFF
58 | J08/PV O/G-3 | PR-PVDS-J08 | TCS Faulty
59 | J08/PV O/G-3 | PR-PVDS-J08 | Lockout Trip
60 | J08/PV O/G-3 | PR-PVDS-J08 | CB Spring Charged
61 | J08/PV O/G-3 | PR-PVDS-J08 | CB Gas Pressure Loss
62 | J08/PV O/G-3 | PR-PVDS-J08 | CB Gas Pressure Min
63 | J08/PV O/G-3 | PR-PVDS-J08 | VT MCB Tripped Core 01 > BC
64 | J08/PV O/G-3 | PR-PVDS-J08 | VT MCB Tripped Core 02 > BC
65 | J08/PV O/G-3 | PR-PVDS-J08 | O/C Protection Operated
66 | J08/PV O/G-3 | PR-PVDS-J08 | Earth Fault Protection Operated
67 | J08/PV O/G-3 | PR-PVDS-J08 | Over Voltage Protection Operated
68 | J08/PV O/G-3 | PR-PVDS-J08 | Under Voltage Protection Operated
69 | J08/PV O/G-3 | PR-PVDS-J08 | Line Diff. Protection Operated
70 | J11/PV O/G-4 | PR-PVDS-J11 | AC MCBs trip
71 | J11/PV O/G-4 | PR-PVDS-J11 | DC MCBs trip
72 | J11/PV O/G-4 | PR-PVDS-J11 | Main AC MCB Trip
73 | J11/PV O/G-4 | PR-PVDS-J11 | Main DC MCB Trip
74 | J11/PV O/G-4 | PR-PVDS-J11 | Protection relay faulty
75 | J11/PV O/G-4 | PR-PVDS-J11 | Local / Remote SS on Local
76 | J11/PV O/G-4 | PR-PVDS-J11 | Local / Remote SS on Remote
77 | J11/PV O/G-4 | PR-PVDS-J11 | Disconnector ON
78 | J11/PV O/G-4 | PR-PVDS-J11 | Disconnector OFF
79 | J11/PV O/G-4 | PR-PVDS-J11 | Earth Switch ON
80 | J11/PV O/G-4 | PR-PVDS-J11 | Earth Switch OFF
81 | J11/PV O/G-4 | PR-PVDS-J11 | TCS Faulty
82 | J11/PV O/G-4 | PR-PVDS-J11 | Lockout Trip
83 | J11/PV O/G-4 | PR-PVDS-J11 | CB Spring Charged
84 | J11/PV O/G-4 | PR-PVDS-J11 | CB Gas Pressure Loss
85 | J11/PV O/G-4 | PR-PVDS-J11 | CB Gas Pressure Min
86 | J11/PV O/G-4 | PR-PVDS-J11 | VT MCB Tripped Core 01 > BC
87 | J11/PV O/G-4 | PR-PVDS-J11 | VT MCB Tripped Core 02 > BC
88 | J11/PV O/G-4 | PR-PVDS-J11 | O/C Protection Operated
89 | J11/PV O/G-4 | PR-PVDS-J11 | Earth Fault Protection Operated
90 | J11/PV O/G-4 | PR-PVDS-J11 | Over Voltage Protection Operated
91 | J11/PV O/G-4 | PR-PVDS-J11 | Under Voltage Protection Operated
92 | J11/PV O/G-4 | PR-PVDS-J11 | Line Diff. Protection Operated