## IEC104 All Data
Telemetry <13>: = Measurement value, short floating point number |  |  | Teleindication <1>: = Single point information | Signal Name | Status | Telecontrol <45>: = Single point command <46>: = Double point command | Signal Name | Command | Teleadjust
No. | Signal Name |  | No. | Signal Name |  | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | (16385– 1) + (Start telemetry signal address – 1) + Telemetry No. | 1 | Communication failure |  | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | 16393 | 2 | Locking status |  | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage |  | 3 | Inverter startup/shutdown status |  | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage |  | 4 | High string input voltage
5 | PV5 voltage |  | 5 | DC Arc Fault
6 | PV6 voltage |  | 6 | String Reverse Connection
7 | PV7 voltage |  | 7 | String current backfeed
8 | PV8 voltage |  | 8 | Abnormal String Power
9 | PV1 current |  | 9 | AFCI Self-Check Failure
10 | PV2 current |  | 10 | Phase Wire Short-Circuited to PE
11 | PV3 current |  | 11 | Grid Loss
12 | PV4 current |  | 12 | Grid Undervoltage |  |  | Teleindication: (0x0001 – 1) + (Start teleindication signal address – 1) + Teleindication No. Telemetry: (0x4001 – 1) + (Start telemetry signal address – 1) + Telemetry No. Telecontrol: (0x6001 – 1) + (Start telecontrol signal address – 1) + Telecontrol No. Teleadjust: (0x6201 – 1) + (Start teleadjust signal address – 1) + Teleadjust No.
13 | PV5 current |  | 13 | Grid Overvoltage
14 | PV6 current |  | 14 | Grid Voltage Imbalance
15 | PV7 current |  | 15 | Grid Overfrequency
16 | PV8 current |  | 16 | Grid Underfrequency
17 | AB Line voltage |  | 17 | Unstable Grid Frequency
18 | BC Line voltage |  | 18 | Output Overcurrent
19 | CA Line voltage |  | 19 | Output DC Component Overhigh
20 | Phase A voltage |  | 20 | Abnormal Residual Current
21 | Phase B voltage |  | 21 | Abnormal Grounding
22 | Phase C voltage |  | 22 | Low Insulation Resistance
23 | Phase A current |  | 23 | Cabinet Overtemperature
24 | Phase B current |  | 24 | Device Fault
25 | Phase C current |  | 25 | Upgrade Failed
26 | Grid frequency |  | 26 | License Expired
27 | Active power |  | 27 | Faulty Monitoring Unit
28 | Reactive power |  | 28 | Faulty Power Collector
29 | Power factor |  | 29 | ESS Abnormal
30 | Total input power |  | 30 | Active Islanding
31 | Cabinet temperature |  | 31 | Passive Islanding
32 | Inverter efficiency |  | 32 | Transient AC Overvoltage
33 | Daily energy yield |  | 33 | Peripheral port short circuit
34 | Total energy yield |  | 34 | Off-grid output overload
35 | Reduced CO2 emission |  | 35 | Abnormal PV module configuration
36 | Inverter Operating Status |  | 36 | Standby |  | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
37 | Startup time |  | 37 | On-grid
38 | Shutdown time |  | 38 | Normal grid connection
39 | Monthly energy yield |  | 39 | Grid connection with derating due to power rationing
40 | Yearly energy yield |  | 40 | Grid connection with derating due to inverter internal causes
41 | Inverter Operating Status (Tianjin, China) |  | 41 | Normal shutdown
42 | Reserved |  | 42 | Faulty
43 | Reserved |  | 43 | Shutdown due to power rationing
44 | Reserved |  | 44 | Shutdown
45 | Reserved |  | 45 | Spot-check
46 | Reserved |  | 46 | Optimizer fault
47 | Reserved |  | 47 | Built-in PID operation abnormal
48 | Reserved |  | 48 | High input string voltage to ground
49 | Inverter running status (Hubei) |  | 49 | External fan abnormal |  | <-Note: | Inverter running status (Tianjin)
|  |  | 50 | Battery Reverse Connection |  |  | 0: Grid-tied
|  |  | 51 | Grid-tied/Off-grid controller abnormal |  |  | 1: Standby
|  |  | 52 | PV String Loss |  |  | 2: Power limiting
|  |  | 53 | Reserved |  |  | 3: Shut down (including shutdown due to faults)
|  |  | 54 | Reserved
|  |  | 55 | Reserved
|  |  | 56 | Reserved
|  |  | 57 | Reserved
|  |  | 58 | Reserved
|  |  | 59 | Reserved
|  |  | 60 | Reserved
|  |  | 61 | Reserved
|  |  | 62 | Reserved
|  |  | 63 | Reserved
|  |  | 64 | Reserved
|  |  | 65 | Reserved
|  |  | 66 | Reserved
|  |  | 67 | Reserved
|  |  | 68 | Reserved
|  |  | 69 | Reserved
|  |  | 70 | Reserved
|  |  | 71 | Reserved
|  |  | 72 | Reserved
|  |  | 73 | Reserved
|  |  | 74 | Reserved | /
|  |  | 75 | Reserved | /
|  |  | 76 | Reserved | /
|  |  | 77 | Reserved | /
|  |  | 78 | Reserved | /
|  |  | 79 | Reserved | /
|  |  | 80 | Reserved | /
|  |  | 81 | Reserved | /
|  |  | 82 | Reserved | /
|  |  | 83 | Reserved | /
|  |  | 84 | Indicates the enabling status of the high voltage ride through function. | 0: disabled; 1: enabled
|  |  | 85 | Indicates the enabling status of the bottom pressure traversal function. | 0: disabled; 1: enabled

## FAT Procedure
No. | Test / Activity | Method / Procedure | Acceptance Criteria | Records / Evidence | IEC Standard Reference | Intervention / Responsible Party
1 | Pre-FAT Check | Confirm latest approved Signal List/Tag List, Modbus mapping, IP plan, and software versions (Web Server/HMI + PLC). | All documents are available, correct, and match project scope. | Document check list, version list. | IEC 61082-1; IEC 61131-3 | Both
2 | FAT Setup & Visual Inspection | Power ON server/PC, PLC/ET-200S, network switch. Check wiring, labeling, and Ethernet connections. Verify connectivity Server ↔ PLC/ET-200S and Server ↔ Modbus Simulator. | All devices are powered, online, and network communication is stable. | Visual inspection checklist, photos | IEC 60204-1; IEC 61158 / IEC 61784 | Vendor
3 | Web Server / HMI Basic Test | Start the local web server. Open HMI from client browser. Check screens, navigation, and data refresh. | HMI loads without errors. Pages open correctly and values are displayed/updated. | Screenshots, FAT log. | IEC 61131-3; IEC 61158 / IEC 61784 | Vendor
4 | Modbus TCP Simulation (Modbus Slave) | Run Modbus Slave simulator with required IP/Port. Create registers based on mapping. Change values (0→1 for bits, different analog values). Verify values on HMI. | All Modbus tags are read correctly. Displayed values match simulator values. | Tag verification sheet, screenshots. | IEC 61158 / IEC 61784; Modbus Application Protocol (non-IEC) | Both
5 | Modbus Communication Loss Test | Stop simulator / disconnect network, then reconnect. Observe HMI behavior. | Communication alarm/indication appears on disconnection. Data returns correctly after reconnection. | Event/alarm log, screenshot, FAT log. | IEC 61158 / IEC 61784; Modbus Application Protocol (non-IEC) | Both
6 | Alarms & Events Test | Generate alarms using Modbus status bits and/or ET-200S DI signals. Verify alarm display, time stamp, and acknowledge/clear (if included). | Alarms/events appear correctly with correct time stamp. Acknowledge/clear works (if applicable). | Alarm/event log export, screenshots. | IEC 62682; IEC 61131-3 | Both
7 | Historian / Trends Quick Check | Change analog values and DI states for a short period. Open trends/historian screen and verify data recording. | Trend/historian shows correct values for the test period. | Trend screenshots, historian log/export (if available). | IEC 61131-3; IEC 61158 / IEC 61784 | Vendor
References
Ref ID | Standard / Document | Link | Used In (Tests) / Notes
R1 | IEC 61082-1:2014 — Preparation of documents used in electrotechnology | https://webstore.iec.ch/en/publication/4469 | Test 1 (documentation check)
R2 | IEC 61131-3:2025 — Programmable controllers – Part 3: Programming languages | https://webstore.iec.ch/en/publication/68533 | Tests 1, 3, 6, 7 (PLC application / data handling)
R3 | IEC 60204-1:2016 — Safety of machinery – Electrical equipment of machines | https://webstore.iec.ch/en/publication/26037 | Test 2 (power-up, wiring/inspection context)
R4 | IEC 61158-1:2023 — Industrial communication networks – Fieldbus specifications (overview) | https://webstore.iec.ch/en/publication/66931 | Tests 2, 3, 4, 5, 7 (industrial comm context)
R5 | IEC 61784-1-1:2023 — Industrial communication networks – Profiles (CPF 1) | https://webstore.iec.ch/en/publication/83454 | Tests 2, 3, 4, 5, 7 (comm profiles context)
R6 | IEC 62682:2022 — Management of alarm systems for the process industries | https://webstore.iec.ch/en/publication/65543 | Test 6 (alarms/events) + Test 5 (alarm behavior on comm loss)
R7 | Modbus Application Protocol Specification V1.1b3 (Modbus Organization) | https://www.modbus.org/file/secure/modbusprotocolspecification.pdf | Tests 4 & 5 (Modbus TCP verification; addressing/function codes)

## Energy_Meter
Modbus
Item | Address of Register
Phase A Voltage | 9001
Phase B Voltage | 9003
Phase C Voltage | 9005
Phase A Current | 9007
Phase B Current | 9009
Phase C Current | 9011
Phase A Watts | 9019
Phase B Watts | 9021
Phase C Watts | 9023
Phase A Vars | 9025
Phase B Vars | 9027
Phase C Vars | 9029
Phase A VA | 9031
Phase B VA | 9033
Phase C VA | 9035
Frequency | 9037
Power Factor | 9043

## Weather_Station
Modbus
Item | Address of Register | Resolution
Ambient temperature | 0 | 0.1 | Default serial port communication parameters: Serial port baud rate: 9600 Stop bit: 1 Data bit: 8 Check bit: Null Default device address: 01
Temperature 1 (Bracket) | 1 | 0.1
Instantaneous wind direction | 15 | 1
Instantaneous wind speed | 16 | 0.1
Dew-point Temperature | 6 | 0.1
Ambient Humidity | 7 | 0.1
Wind speed in 2 minutes | 17 | 0.1
Instantaneous value of total radiation 1 | 000E | 1
Cumulative value of sunshine duration | 001A | 1
Cumulative value of total radiation 1 | 001B | 0.001
Cumulative value of scattered radiation | 001C | 0.001
Cumulative value of direct radiation | 001D | 0.001
Cumulative value of photosynthetic | 20 | 0.001
Daily sunshine duration | 23 | 1
Daily cumulative value of total radiation 1 | 24 | 0.001
Daily cumulative value of scattered radiation | 25 | 0.001
Daily cumulative value of direct radiation | 26 | 0.001
Daily cumulative value of net radiation | 28 | 0.001
Daily cumulative value of photosynthetic radiation | 29 | 0.001

## Protection_Relay
| Name | BitA | RegA
| Circuit breaker close position | 175.04 | 2804
| Circuit breaker open position | 175.05 | 2805
| Circuit breaker tripMaster1 | 171.06 | 2742
| Circuit breaker tripMaster2 | 171.1 | 2746
| Spring charged/discharged Alarm | 178.02 | 2850
SSR2 System status register (2) protection relay's mode and state | Test/service position status | 129
| Remote/local control status | 170 | 2720 | ملحوظه الفرق بين ال BitA و RegA هو انه ف حاله ال BitA بتستخدمو مع 0x and 1x بينما لو محتاج تستخدمه 3X بتستخدم العنوان بتاع REGA
| Earth switch close position (1) | 175.01 | 2801
| Earth switch open position (1) | 175.02 | 2802
| Earth switch close position (2) | 175.07 | 2807
| Earth switch open position (2) | 175.08 | 2808
| Relay trip Flag | NON
| AC Trip Flag | NON
| DC Trip Flag | NON
| MCB Trip Flag | NON
SSR1 System status register (1) device health | Protection Relay Status ( Alarm) | 128
SSR1 System status register (1) device health | Protection Relay Status ( Error) | 128.01
Protection Relay Status ( Alarm / Trip / Reset )
| - (67) Directional overcurrent high stage (1) | 189.1 | 3034
| - (67) Directional overcurrent low stage (1) | 188.06 | 3014
| - (67) Directional overcurrent low stage (2) | 189 | 3024
| - (46) Negative-sequence overcurrent protection (1) | 196 | 3136
Three-phase non-directional overcurrent protection, high stage (2) | - (50) instantaneous overcurrent | 181.12 | 2908
- (51) Time Overcurrent
| - (86) Lockout Relay Status | 191.04 | 3060
| - (67N) Directional Earth Fault | 182.1 | 2922
| - (51BF) Circuit breaker failure Timer running | 176.12 | 2828
| - (51BF) Circuit breaker failure Fail, external trip | 176.14 | 2830
| - (51BF) Circuit breaker failure Internal re-trip | 177 | 2832
SSR2 System status register (2) protection relay's mode and state | Remote/local control status | 129.02

## INV
IEC104
العناوين المطلوبه | Numebr | العناويبن المقابله IEC | Real Address
Active Power (per inverter and total) | 27 | TELEMERTY | 78 | Teleindication: (0x0001 – 1) + (Start teleindication signal address – 1) + Teleindication No. Telemetry: (0x4001 – 1) + (Start telemetry signal address – 1) + Telemetry No.
Reactive Power | 28 | TELEMERTY | 79
Apparent Power
Power Factor | 29 | TELEMERTY | 80
AC Voltage (L-L or L-N) | 19 | TELEMERTY | 70
AC Current (per phase) | 23 | TELEMERTY | 74
Frequency | 26 | TELEMERTY | 77
DC Voltage ( String Level) | 1 | TELEMERTY | 52
DC Current | 11 | TELEMERTY | 62
DC Power
Inverter Efficiency | 32 | TELEMERTY | 83
Daily Energy Yield | 33 | TELEMERTY | 84
Total Energy Yield | 34 | TELEMERTY | 85
Inverter Running / Stopped | 49 | TELEMERTY | 100
Inverter Grid Connection Status (Connected / Disconnected) | 40 | Teleindication | 91
Communication Status (Healthy / Lost) | 1 | Teleindication | 52
Remote ON/OFF Status
Active Power Control Mode
Reactive Power Control Mode
Islanding Detection Status
Power Curtailment Status
General Fault Trip | 24 | Teleindication | 75
Warning Active (Derating, Overtemperature) | 42 | Teleindication | 93
DC Insulation Fault | 22 | Teleindication | 73
Ground Fault | 21 | Teleindication | 72
AC Overvoltage | 13 | Teleindication | 64
AC Undervoltage | 12 | Teleindication | 63
Grid Overfrequency | 15 | Teleindication | 66
Grid Underfrequency | 16 | Teleindication | 67
DC Overvoltage
Inverter Over temperature | 23 | Teleindication | 74
String Reverse Polarity | 6 | Teleindication | 57
Fan Failure | 49 | Teleindication | 100
Communication Failure | 1 | Teleindication | 52
Power Limitation Active due to Grid Command
Inverter Trip History Available

## INv Modbus
العناوين المطلوبه | REG Address | QUNTITY | Gain | %
Active Power (per inverter and total) | 40525 | 2 | 1000 | 40428 | 40388
Reactive Power | 40544 | 2 | 1000 |  | 40390 |  | Register Definitions for the Logger
Apparent Power
Power Factor | 40532 | 1 | 1000
Frequency
DC Voltage ( String Level)
DC Current | 40500 | 1 | 10 | 38100
DC Power
Inverter Efficiency | 40685 | 1 | 100
Daily Energy Yield
Total Energy Yield | 40560 | 2 | 10
Inverter Running / Stopped
Inverter Grid Connection Status (Connected / Disconnected)
Communication Status (Healthy / Lost)
Remote ON/OFF Status
Active Power Control Mode | 40737 | 1 | 1 |  |  | 41889
Reactive Power Control Mode | 40740 | 1 |  | 44165 |  | 44165
Islanding Detection Status
Power Curtailment Status
General Fault Trip
Warning Active (Derating, Overtemperature)
DC Insulation Fault
Ground Fault
AC Overvoltage
AC Undervoltage
Grid Overfrequency
Grid Underfrequency
DC Overvoltage
Inverter Over temperature
String Reverse Polarity
Fan Failure
Communication Failure
Power Limitation Active due to Grid Command
Inverter Trip History Available
Quantity OF PV Running | 40206
Input Power | 40521 | 2 | 1000
DC Current2 | 40554 | 2 | 10
PHASE A Current | 40572 | 1 | 1
PHASE B Current | 40573 | 1 | 1
PHASE C Current | 40574 | 1 | 1
A-B Line Voltage | 40575 | 1 | 10
B-C Line Voltage | 40576 | 1 | 10
C-A Line Voltage | 40577 | 1 | 10
Working Mode | 42256
Grid Connection Status | 44376 | 1
Current Daily Energy Yield | 38004 |  | 100

## INV Modbus-2
العناوين المطلوبه | offset | quantity | Gain
Active Power (per inverter and total) | 0 | 2 | 1000 |  | Register Definitions for the SUN2000
Reactive Power | 2 | 2 | 1000
Apparent Power
Power Factor | 8 | 1
● Register address = Initial register address + (25 * (Device address – 1)) + Offset address ● Initial register address = 51000 ● For the registers must be set in sequence, the device address must be in strict accordance with the continuous number to avoid waste of registers.
Frequency
DC Voltage ( String Level)
DC Current | 4 | 1 | 100
DC Power | 5 | 2 | 100
Inverter Efficiency
Daily Energy Yield
Total Energy Yield
Inverter Running / Stopped
Inverter Grid Connection Status (Connected / Disconnected)
Communication Status (Healthy / Lost)
Remote ON/OFF Status
Active Power Control Mode
Reactive Power Control Mode
Islanding Detection Status
Power Curtailment Status
General Fault Trip
Warning Active (Derating, Overtemperature)
DC Insulation Fault
Ground Fault
AC Overvoltage
AC Undervoltage
Grid Overfrequency
Grid Underfrequency
DC Overvoltage
Inverter Over temperature
String Reverse Polarity
Fan Failure
Communication Failure
Power Limitation Active due to Grid Command
Inverter Trip History Available
Quantity OF PV Running
Input Power
DC Current2
PHASE A Current
PHASE B Current
PHASE C Current
A-B Line Voltage
B-C Line Voltage
C-A Line Voltage
Working Mode
Grid Connection Status
Current Daily Energy Yield

## Fautl Data of P_Relay
Fault record data Of Protection Realy
RegA | Type | Scale | Description | Values
Fault record data
9409 | u32 | 1 | Fault record number (high) | 0..999999
9411 | i16 | 1 | Protection function | -32768...327 67
9412 | u16 | 100 | Frequency | 30…80.00 [Hz]
9413 | u16 | 100 | Start duration | 0 100.00 [%]
9414 | u32 | 1000 | Operate time [ms] (high) | 0...999999.99 9
9416 | u32 | 100 | Fault resistance | 0.00… 1000000.00 ohms
9418 | u32 | 100 | Fault distance | 0.00… 9999.99 pu
9420 | u16 | 1 | Active setting group | 1…6
9421 | u16 | 1 | AR shot pointer value | 0...7
9422 | u16 | 1000 | Max. diff. current phs A | 0.000...80.00 0 [pu]
9423 | u16 | 1000 | Max. diff. current phs B | 0.000...80.00 0 [pu]
9424 | u16 | 1000 | Max. diff. current phs C | 0.000...80.00 0 [pu]
9425 | u16 | 1000 | Max. bias current phs A | 0.000… 50.000 [pu]
9426 | u16 | 1000 | Max. bias current phs B | 0.000… 50.000 [pu]
9427 | u16 | 1000 | Max. bias current phs C | 0.000… 50.000 [pu]
9428 | u16 | 1000 | Diff. current phs A | 0.000...80.00 0 [pu]
9429 | u16 | 1000 | Diff. current phs B | 0.000...80.00 0 [pu]
9430 | u16 | 1000 | Diff. current phs C | 0.000...80.00 0 [pu]
9431 | u16 | 1000 | Bias current phs A | 0.000… 50.000 [pu]
9432 | u16 | 1000 | Bias current phs B | 0.000… 50.000 [pu]
9433 | u16 | 1000 | Bias current phs C | 0.000… 50.000 [pu]
9434 | u16 | 1000 | Diff. current Io | 0.000...80.00 0 [pu]
9435 | u16 | 1000 | Bias current Io | 0.000… 50.000 [pu]
9436 | u16 | 1000 | Max. current phs A(1) | 0.000… 50.000 [×In]
9437 | u16 | 1000 | Max. current phs B(1) | 0.000… 50.000 [×In]
9438 | u16 | 1000 | Max. current phs C(1) | 0.000… 50.000 [×In]
9439 | u16 | 1000 | Max. current Io(1) | 0.000… 50.000 [×In]
9440 | u16 | 1000 | Current phs A(1) | 0.000… 50.000 [×In]
9441 | u16 | 1000 | Current phs B(1) | 0.000… 50.000 [×In]
9442 | u16 | 1000 | Current phs C(1) | 0.000… 50.000 [×In]
9443 | u16 | 1000 | Current Io(1) | 0.000… 50.000 [×In]
9444 | u16 | 1000 | Current Io-Calc(1) | 0.000… 50.000 [×In]
9445 | u16 | 1000 | Current Ps-Seq(1) | 0.000… 50.000 [×In]
9446 | u16 | 1000 | Current Ng-Seq(1) | 0.000… 50.000 [×In]
9447 | u16 | 1000 | Voltage phs A(1) | 0.000...4.000 [×Un]
9448 | u16 | 1000 | Voltage phs B(1) | 0.000...4.000 [×Un]
9449 | u16 | 1000 | Voltage phs C(1) | 0.000...4.000 [×Un]
9450 | u16 | 1000 | Voltage phs AB(1) | 0.000...4.000 [×Un]
9451 | u16 | 1000 | Voltage phs BC(1) | 0.000...4.000 [×Un]
9452 | u16 | 1000 | Voltage phs CA(1) | 0.000...4.000 [×Un]
9453 | u16 | 1000 | Voltage Uo(1) | 0.000...4.000 [×Un]
9454 | u16 | 1000 | Voltage Zro-Seq(1) | 0.000...4.000 [×Un]
9455 | u16 | 1000 | Voltage Ps-Seq(1) | 0.000...4.000 [×Un]
9456 | u16 | 1000 | Voltage Ng-Seq(1) | 0.000...4.000 [×Un]
9457 | u16 | 100 | PTTR thermal level | 0.00...99.99
9458 | u16 | 100 | PDNSPTOC1 ratio I2/I1 | 0.00...999.99 [%]
9459 | i16 | 100 | Frequency gradient | -10.00...10.0 0 [Hz/s]
9460 | i16 | 100 | Conductance Yo | -1000.00...10 00.00 [mS]
9461 | i16 | 100 | Susceptance Yo | -1000.00...10 00.00 [mS]
9462 | i32 | 100 | Fault loop resistance | -1000.00...10 00.00 [ohm]
9464 | i32 | 100 | Fault loop reactance | -1000.00...10 00.00 [ohm]
9466 | u16 | 1000 | Breaker clear time | 0.000...3.000 [s]
9467 | u16 | 1000 | Current phs A(2) | 0.000… 50.000 [×In]
9468 | u16 | 1000 | Current phs B(2) | 0.000… 50.000 [×In]
9469 | u16 | 1000 | Current phs C(2) | 0.000… 50.000 [×In]
9470 | u16 | 1000 | Current Io(2) | 0.000… 50.000 [×In]
9471 | u16 | 1000 | Current Io-Calc(2) | 0.000… 50.000 [×In]
9472 | u16 | 1000 | Current Ps-Seq(2) | 0.000… 50.000 [×In]
9473 | u16 | 1000 | Current Ng-Seq(2) | 0.000… 50.000 [×In]
9474 | u16 | 1000 | Voltage phs A(2) | 0.000...4.000 [×Un]
9475 | u16 | 1000 | Voltage phs B(2) | 0.000...4.000 [×Un]
9476 | u16 | 1000 | Voltage phs C(2) | 0.000...4.000 [×Un]
9477 | u16 | 1000 | Voltage phs AB(2) | 0.000...4.000 [×Un]
9478 | u16 | 1000 | Voltage phs BC(2) | 0.000...4.000 [×Un]
9479 | u16 | 1000 | Voltage phs CA(2) | 0.000...4.000 [×Un]
9480 | u16 | 1000 | Voltage Uo(2) | 0.000...4.000 [×Un]
9481 | u16 | 1000 | Voltage Zro-Seq(2) | 0.000...4.000 [×Un]
9482 | u16 | 1000 | Voltage Ps-Seq(2) | 0.000...4.000 [×Un]
9483 | u16 | 1000 | Voltage Ng-Seq(2) | 0.000...4.000 [×Un]
9485 | i16 | 100 | Angle UBC-IA(1) | -180.00… 180.00 [deg]
9486 | i16 | 100 | Angle UCA-IB(1) | -180.00… 180.00 [deg]
9487 | i16 | 100 | Angle UAB-IC(1) | -180.00… 180.00 [deg]

## P_Realy Alarm
Alarm Of Protection Realy
RegA | Bit A | Message
3002 | 187.1 | Current circuit supervision (1) | HIGH_ALARM
3316 | 207.04 | Current total demand distortion (1) | HIGH_ALARM
2752 | 172 | Three-phase current measurement (1 | HIGH_ALARM
2754 | 172.02 |  | HIGH_WARN
2756 | 172.04 |  | LOW_WARN
2758 | 172.06 |  | LOW_ALARM
2760 | 172.08 | Residual current measurement (1 | HIGH_ALARM
2764 | 172.12 | Residual voltage measurement (1 | HIGH_ALARM
Circuit-breaker condition monitoring (1
2848 | 178 | Opn travel time alarm | HIGH_ALARM
2849 | 178.01 | Cls travel time alarm | HIGH_ALARM
2850 | 178.02 | Spring charge alarm | HIGH_ALARM
2851 | 178.03 | CB operations alarm | HIGH_ALARM
2853 | 178.05 | CB inactive alarm | HIGH_ALARM
2854 | 178.06 | Low pressure alarm | HIGH_ALARM
2858 | 178.1 | CB lifetime alarm | HIGH_ALARM
2974 | 185.14 | Three-phase thermal protection for feeders, cables and distribution transformers (1) | HIGH_ALARM
2780 | 173.12 | Trip circuit supervision (1 | HIGH_ALARM
2782 | 173.14 | Trip circuit supervision (2 | HIGH_ALARM
3318 | 207.06 | Voltage total harmonic distortion (1) | HIGH_ALARM
2784 | 174 | Three-phase voltage measurement (1) | HIGH_ALARM
2786 | 174.02 |  | HIGH_WARN
2788 | 174.04 |  | LOW_WARN
2790 | 174.06 |  | LOW_ALARM

## Alarm
Alarm Of Smart Logger
Alarm ID | Alarm Name | Alar m Sub- ID | Alarm Cause | Severi ty | Regist er Addre ss | Bi t
1100 | Abnormal Active Schedule | 5 | In remote communication scheduling mode, the Logger cannot receive active power scheduling commands or the received active power scheduling commands are abnormal. | Major | 50000 | 4
1101 | Abnormal Reactive Schedule | 4 | If Reactive Power Control Mode is set to Dry contact remote control, the four DI ports read instruction combinations not configured. | Major | 50000 | 11
1101 | Abnormal Reactive Schedule | 5 | In remote reactive power scheduling mode, the Logger cannot receive reactive power scheduling commands or the received commands are abnormal. | Major | 50000 | 12
1103 | MCB Disconnec t | 1 | The general AC circuit breaker at the grid- connection point is OFF. | Major | 50001 | 1
1104 | Abnormal Cubicle | 1 | The Cubicle device has detected an exception at the grid-connection point. | Major | 50001 | 2
1105 | Device Address Conflict | 1 | The address set on the SmartLogger conflicts with an existing access device address. | Major | 50001 | 3
1106 | AC SPD fault | 1 | Communication box SPD fault | Major | 50001 | 4
1115 | 24V power failure | 1 | Communication box 24V power failure | Major | 50001 | 13
1116 | WebUI server certificate invalid | 1 | WebUI server certificate invalid | Warni ng | 50002 | 0
1117 | WebUI server certificate to expire | 1 | WebUI server certificate to expire | Warni ng | 50002 | 1
1118 | WebUI server certificate expired | 1 | WebUI server certificate expired | Major | 50002 | 2
1119 | License Expired | 1 | 1. The privilege certificate has entered the grace period. 2. The privilege feature will be invalid soon. | Warni ng | 50001 | 14
1120 | Managem ent system certificate invalid | 1 | The management system certificate is not yet valid. | Warni ng | 50002 | 3
1121 | Managem ent system certificate to expire | 1 | The management system certificate is about to expire. | Warni ng | 50002 | 4
1122 | Managem ent system certificate expired | 1 | The management system certificate has expired. | Major | 50002 | 6
1120 | Managem ent System Certificate Invalid | 3 | SPPC's digital signature certificate Is About to Expire | Warni ng | 50003 | 5
1120 | Managem ent System Certificate Invalid | 2 | The digital signature certificate of management system 1 has not taken effect. | Warni ng | 50003 | 0
1121 | Managem ent System Certificate to Expire | 2 | The digital signature certificate of management system 1 is about to expire. | Warni ng | 50003 | 1
1121 | Managem ent System Certificate to Expire | 1 | The digital signature certificate of management system 1 is about to expire. | Warni ng | 50002 | 4
1122 | Managem ent System Certificate Expired | 2 | The digital signature certificate of management system 1 has expired. | Major | 50003 | 2
1122 | Managem ent System Certificate Expired | 1 | The digital signature certificate of management system 1 has expired. | Major | 50002 | 5
1123 | Remote Control Certificate invalid | 1 | Remote output control certificate invalid | Warni ng | 50002 | 6
1124 | Remote Control Certificate to expire | 1 | Remote output control certificate to expire | Warni ng | 50002 | 7
1125 | Remote Control Certificate expired | 1 | Remote output control certificate expired | Major | 50002 | 8
1126 | ESGCC Certificate invalid | 1 | Poverty alleviation monitoring center certificate invalid | Warni ng | 50002 | 9
1127 | ESGCC Certificate to expire | 1 | Poverty alleviation monitoring center certificate to expire | Warni ng | 50002 | 10
1128 | ESGCC Certificate expired | 1 | Poverty alleviation monitoring center certificate expired | Major | 50002 | 11
1129 | SmartLog ger Certificate Invalid | 1 | SmartLogger Certificate Invalid | Warni ng | 50002 | 12
1130 | SmartLog ger Certificate About to Expire | 1 | SmartLogger Certificate About to Expire | Warni ng | 50002 | 13
1131 | SmartLog ger Certificate Expired | 1 | SmartLogger Certificate Expired | Major | 50002 | 14
1132 | One or Two Smart Rack Controller Cables Not Connecte d to DC Bus | 1 | One or two cables of a Smart Rack Controller are not connected to the DC bus. | Major | 50002 | 15
1133 | Smart Tracker Out of Control | 1 | One or more trackers in the array are not controlled by the smart tracking algorithm. | Major | 50004 | 0
1134 | One or Two Smart PCS Cables Not Connecte d to DC Bus | 1 | One or two cables of a Smart PCS are not connected to the DC bus. | Major | 50003 | 3
1135 | Insufficie nt SDS License Capacity | 1 | The license capacity of the SDS is insufficient. | Major | 50004 | 1
1140 | Array Black Start Failed | 1 | The black start command is not delivered in the correct time sequence. | Minor | 50005 | 0
1140 | Array Black Start Failed | 2 | The array running status does not meet the condition for a black start. | Minor | 50005 | 1
1140 | Array Black Start Failed | 3 | No available ESS. | Minor | 50005 | 2
1140 | Array Black Start Failed | 4 | The ESS does not support black start. | Minor | 50005 | 3
1140 | Array Black Start Failed | 5 | The PCS does not support black start. | Minor | 50005 | 4
1140 | Array Black Start Failed | 6 | The black start of the ESS failed. | Minor | 50005 | 5
1140 | Array Black Start Failed | 7 | No available PCS. | Minor | 50005 | 6
1140 | Array Black Start Failed | 8 | The black start of the PCS failed. | Minor | 50005 | 7
1141 | The STS is switched off, and the ESS shutdown protection is triggered. | 1 | The medium-voltage side or low-voltage side of the STS is switched off, causing the shutdown of PCSs and ESS devices in the PV array. | Major | 50005 | 8
1141 | The STS is switched off, and the ESS shutdown protection is triggered. | 2 | The PV array PCS shuts down due to a dry contact fault in the battery compartment or a startup disallowed command sent by the BMS. | Major | 50005 | 13
1141 | The STS is switched off, and the ESS shutdown protection is triggered. | 3 | Array PCS Shutdown Triggered by BMS Communication Disconnection | Major | 50005 | 14
1142 | Switch Control Failed at Grid Connectio n Point | 1 | Failed to turn off the dry contact. | Major | 50005 | 9
1142 | Switch Control Failed at Grid Connectio n Point | 2 | Failed to turn on the dry contact. | Major | 50005 | 10
1142 | Switch Control Failed at Grid Connectio n Point | 3 | Failed to turn off the switch through the relay protection device. | Major | 50005 | 11
1142 | Switch Control Failed at Grid Connectio n Point | 4 | Failed to turn on the switch through the relay protection device. | Major | 50005 | 12
1142 | Switch Control Failed at Grid Connectio n Point | 5 | Third-party relay protection synchronization check failed. | Major | 50005 | 13
1143 | The system- to-ground insulation capability of the system has decreased . | 1 | The system-to-ground insulation capability of the system has decreased. | Major | 50005 | 14
1144 | Load Switch Control Failed | 1 | Failed to turn off the load switch. | Major | 50006 | 0
1144 | Load Switch Control Failed | 2 | Failed to turn on the load switch. | Major | 50006 | 1
1145 | Genset Control Failed | 1 | Failed to start up the genset through the dry contact. | Major | 50005 | 15
1145 | Genset Control Failed | 2 | Failed to stop the genset through the dry contact. | Major | 50006 | 6
1146 | Adjustme nt Failed During On/Off- grid Switching | 1 | Failed to synchronize parameters during the switching from off-grid to on-grid. | Major | 50006 | 2
1146 | Adjustme nt Failed During On/Off- grid Switching | 2 | Failed to adjust the power during the switching from on-grid to off-grid. | Major | 50006 | 3
1147 | System Black Start Failed | 1 | The average ESS SOC is lower than the minimum SOC required for the black start. | Major | 50006 | 4
1148 | Array fault shutdown | 1 | The communication between the Logger and the PPC/NMS is abnormal, which triggers the shutdown due to an array fault. | Major | 50006 | 5
1149 | The temperat ure inside the communi cations cabinet is too high. | 1 | The ambient temperature is too high, and the fan in the communication box is faulty. | Minor | 50006 | 9
1150 | Power Control Abnormal at Grid Connectio n Point | 1 | Current limit control abnormality | Major | 50006 | 7
1152 | ESS Control Abnormal | 1 | The connected ESS does not support the configured control mode (TOU, maximum self- consumption, power boost limit, or peak shaving). | Major | 50006 | 8
1154 | Southbou nd device communi cation is abnormal. | 5 | The meter communication is abnormal. | Major | 50007 | 9
1161 | Battery cluster input test failed | 1 | There are devices that do not report the battery cluster cable connection detection result. | Major | 50006 | 11
1162 | Battery cluster Fast IO test failed | 1 | Some devices do not report the FastIO cable connection check result. | Major | 50006 | 12
1166 | SOC equalizati on failed. | 1 | SOC equalization failed. | Minor | 50007 | 14