## Summary
SCADA Tag / Signal / Alarm / Event / Historian Package
Project Inputs
Inverters | 75
Protection Relays | 14 (ABB Ref615)
Energy Meters | 14 (GENIUS Mk6ESL)
Weather Station | 1
Tag naming convention | <DeviceID>_<SignalBase>

## Signal_List
Signal List (Template Level)
Device Type | Signal Description | Tag Base | Template Scope | Quantity | Device Prefix | Point Code | Point Type | Protocol | Point Category | Engineering Unit | Register / Point Ref | Column1
Energy Meter | Active power | ActivePower | Per Device | 14 | EM | AI | Analog | Modbus |  | kW | E033
Energy Meter | Apparent Power | ApparentPower | Per Device | 14 | EM | AI | Analog | Modbus |  | kVA | E053
Energy Meter | Frequency | Frequency | Per Device | 14 | EM | AI | Analog | Modbus |  | Hz | E060
Energy Meter | Phase A Current | PhaseACurrent | Per Device | 14 | EM | AI | Analog | Modbus |  | A | E010
Energy Meter | Phase B Current | PhaseBCurrent | Per Device | 14 | EM | AI | Analog | Modbus |  | A | E011
Energy Meter | Phase C Current | PhaseCCurrent | Per Device | 14 | EM | AI | Analog | Modbus |  | A | E012
Energy Meter | Power Factor | PowerFactor | Per Device | 14 | EM | AI | Analog | Modbus |  | p.u. | E026
Energy Meter | Reactive Power | ReactivePower | Per Device | 14 | EM | AI | Analog | Modbus |  | kvar | E043
Energy Meter | Total export Wh | TotalExportWh | Per Device | 14 | EM | AI | Analog | Modbus |  | Wh | E097
Energy Meter | Total export varh | TotalExportVarh | Per Device | 14 | EM | AI | Analog | Modbus |  | varh | E09F
Energy Meter | Total import Wh | TotalImportWh | Per Device | 14 | EM | AI | Analog | Modbus |  | Wh | E093
Energy Meter | Total import varh | TotalImportVarh | Per Device | 14 | EM | AI | Analog | Modbus |  | varh | E09B
Inverter | AC Current (per phase) | ACCurrent | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | A | 23
Inverter | AC Overvoltage | ACOvervoltage | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 13
Inverter | AC Undervoltage | ACUndervoltage | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 12
Inverter | AC Voltage (L-L or L-N) | ACVoltage | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | V | 19
Inverter | AFCI Self-Check Failure | AFCISelfCheckFailure | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 9
Inverter | Abnormal Grounding | AbnormalGrounding | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 21
Inverter | Abnormal PV module configuration | AbnormalPVModuleConfiguration | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 35
Inverter | Abnormal Residual Current | AbnormalResidualCurrent | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 20
Inverter | Abnormal String Power | AbnormalStringPower | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 8
Inverter | Active Islanding | ActiveIslanding | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 30
Inverter | Active Power (per inverter and total) | ActivePower | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | kW | 27
Inverter | Apparent Power | ApparentPower | Per Device | 75 | INV | Calc | Analog | Derived | Calculated | kVA
Inverter | Built-in PID operation abnormal | BuiltPIDOperationAbnormal | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 47
Inverter | Cabinet Overtemperature | CabinetOvertemperature | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 23
Inverter | Communication Failure | CommunicationFailure | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 1
Inverter | Communication Status (Healthy / Lost) | CommunicationStatus | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 1
Inverter | DC Arc Fault | DCArcFault | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 5
Inverter | DC Current | DCCurrent | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | A | 11
Inverter | DC Insulation Fault | DCInsulationFault | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 22
Inverter | DC Overvoltage | DCOvervoltage | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 19
Inverter | DC Power | DCPower | Per Device | 75 | INV | Calc | Analog | Derived | Calculated
Inverter | DC Voltage ( String Level) | DCVoltage | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | V | 1
Inverter | Daily Energy Yield | DailyEnergyYield | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | kWh | 33
Inverter | Device Fault | DeviceFault | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 24
Inverter | External fan abnormal | ExternalFanAbnormal | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 49
Inverter | Fan Failure | FanFailure | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 49
Inverter | Faulty | Faulty | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 42
Inverter | Faulty Monitoring Unit | FaultyMonitoringUnit | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 27
Inverter | Faulty Power Collector | FaultyPowerCollector | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 28
Inverter | Frequency | Frequency | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | Hz | 26
Inverter | General Fault Trip | GeneralFaultTrip | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 24
Inverter | Grid Loss | GridLoss | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 11
Inverter | Grid Overfrequency | GridOverfrequency | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 15
Inverter | Grid Overvoltage | GridOvervoltage | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 13
Inverter | Grid Underfrequency | GridUnderfrequency | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 16
Inverter | Grid Undervoltage | GridUndervoltage | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 12
Inverter | Grid Voltage Imbalance | GridVoltageImbalance | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 14
Inverter | Grid connection with derating due to inverter internal causes | GridConnectionDeratingInverterInternalCauses | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 40
Inverter | Grid connection with derating due to power rationing | GridConnectionDeratingPowerRationing | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 39
Inverter | Grid-tied/Off-grid controller abnormal | GridTiedOffGridControllerAbnormal | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 51
Inverter | Ground Fault | GroundFault | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 21
Inverter | High input string voltage to ground | HighInputStringVoltageGround | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 48
Inverter | High string input voltage | HighStringInputVoltage | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 4
Inverter | Inverter Efficiency | InverterEfficiency | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | % | 32
Inverter | Inverter Grid Connection Status (Connected / Disconnected) | InverterGridConnectionStatus | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 40
Inverter | Inverter Over temperature | InverterOverTemperature | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 23
Inverter | Inverter Running / Stopped | InverterRunningStopped | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY |  | 49
Inverter | Inverter Trip History Available | InverterTripHistoryAvailable | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 24
Inverter | Inverter startup/shutdown status | InverterStartupShutdownStatus | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 3
Inverter | Islanding Detection Status | IslandingDetectionStatus | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 30 , 31
Inverter | License Expired | LicenseExpired | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 26
Inverter | Locking status | LockingStatus | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 2
Inverter | Low Insulation Resistance | LowInsulationResistance | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 22
Inverter | Normal grid connection | NormalGridConnection | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 38
Inverter | Normal shutdown | NormalShutdown | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 41
Inverter | Off-grid output overload | OffGridOutputOverload | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 34
Inverter | On-grid | Grid | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 37
Inverter | Optimizer fault | OptimizerFault | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 46
Inverter | Output DC Component Overhigh | OutputDCComponentOverhigh | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 19
Inverter | Output Overcurrent | OutputOvercurrent | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 18
Inverter | PV String Loss | PVStringLoss | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 52
Inverter | Passive Islanding | PassiveIslanding | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 31
Inverter | Peripheral port short circuit | PeripheralPortShortCircuit | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 33
Inverter | Phase Wire Short-Circuited to PE | PhaseWireShortCircuitedPE | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 10
Inverter | Power Curtailment Status | PowerCurtailmentStatus | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 39 ,40,43
Inverter | Power Factor | PowerFactor | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | p.u. | 29
Inverter | Power Limitation Active due to Grid Command | PowerLimitationActiveGridCommand | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 39
Inverter | Reactive Power | ReactivePower | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | kvar | 28
Inverter | Remote ON/OFF Status | RemoteOFFStatus | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 3
Inverter | Shutdown | Shutdown | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 44
Inverter | Shutdown due to power rationing | ShutdownPowerRationing | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 43
Inverter | Spot-check | SpotCheck | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 45
Inverter | Standby | Standby | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 36
Inverter | String Reverse Connection | StringReverseConnection | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 6
Inverter | String Reverse Polarity | StringReversePolarity | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 6
Inverter | String current backfeed | StringCurrentBackfeed | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 7
Inverter | Total Energy Yield | TotalEnergyYield | Per Device | 75 | INV | AI | Analog | IEC 104 | TELEMERTY | kWh | 34
Inverter | Transient AC Overvoltage | TransientACOvervoltage | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 32
Inverter | Unstable Grid Frequency | UnstableGridFrequency | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 17
Inverter | Upgrade Failed | UpgradeFailed | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 25
Inverter | Warning Active (Derating, Overtemperature) | WarningActive | Per Device | 75 | INV | DI | Digital | IEC 104 | Teleindication | State | 42
Protection Relay | - (46) Negative-sequence overcurrent protection (1) | NegativeSequenceOvercurrentProtection | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 196.0
Protection Relay | - (50) instantaneous overcurrent | InstantaneousOvercurrent | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 181.12
Protection Relay | - (51) Time Overcurrent | TimeOvercurrent | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 180.8
Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | CircuitBreakerFailureFailExternalTrip | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 176.14
Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | CircuitBreakerFailureInternalReTrip | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 177.0
Protection Relay | - (51BF) Circuit breaker failure Timer running | CircuitBreakerFailureTimerRunning | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 176.12
Protection Relay | - (67) Directional overcurrent high stage (1) | DirectionalOvercurrentHighStage | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 189.1
Protection Relay | - (67) Directional overcurrent low stage (1) | DirectionalOvercurrentLowStage | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 188.06
Protection Relay | - (67N) Directional Earth Fault | DirectionalEarthFault | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 182.1
Protection Relay | - (86) Lockout Relay Status | LockoutRelayStatus | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 191.04
Protection Relay | Circuit breaker close position | CircuitBreakerClosePosition | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 175.04
Protection Relay | Circuit breaker open position | CircuitBreakerOpenPosition | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 175.05
Protection Relay | Circuit breaker tripMaster1 | CircuitBreakerTripMaster1 | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 171.06
Protection Relay | Earth switch close position (1) | EarthSwitchClosePosition | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 175.01
Protection Relay | Earth switch open position (1) | EarthSwitchOpenPosition | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 175.02
Protection Relay | Protection Relay Status ( Alarm) | ProtectionRelayStatus | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 128.0
Protection Relay | Remote/local control status | RemoteLocalControlStatus | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 170.0
Protection Relay | Remote/local control status | RemoteLocalControlStatusR129_02 | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 129.02
Protection Relay | Spring charged/discharged Alarm | SpringChargedDischargedAlarm | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 178.02
Protection Relay | Test/service position status | TestServicePositionStatus | Per Device | 14 | PR | DI | Digital | Modbus |  | State | 129.0
Protection Relay | AC Trip Flag | ACTripFlag | Per Device | 14 | PR | DI | Digital | Modbus |  | State
Protection Relay | DC Trip Flag | DCTripFlag | Per Device | 14 | PR | DI | Digital | Modbus |  | State
Protection Relay | MCB Trip Flag | MCBTripFlag | Per Device | 14 | PR | DI | Digital | Modbus |  | State
Protection Relay | Relay trip Flag | RelayTripFlag | Per Device | 14 | PR | DI | Digital | Modbus |  | State
Weather Station | Ambient Humidity | AmbientHumidity | Single | 1 | WS | AI | Analog | Modbus |  | % | 7 | 7
Weather Station | Ambient temperature | AmbientTemperature | Single | 1 | WS | AI | Analog | Modbus |  | °C | 0 | 0
Weather Station | Cumulative value of direct radiation | CumulativeValueDirectRadiation | Single | 1 | WS | AI | Analog | Modbus |  | Accumulated | 001D | 29
Weather Station | Cumulative value of photosynthetic | CumulativeValuePhotosynthetic | Single | 1 | WS | AI | Analog | Modbus |  |  | 20 | 32
Weather Station | Cumulative value of scattered radiation | CumulativeValueScatteredRadiation | Single | 1 | WS | AI | Analog | Modbus |  | Accumulated | 001C | 28
Weather Station | Cumulative value of sunshine duration | CumulativeValueSunshineDuration | Single | 1 | WS | AI | Analog | Modbus |  | h | 001A | 26
Weather Station | Cumulative value of total radiation 1 | CumulativeValueTotalRadiation1 | Single | 1 | WS | AI | Analog | Modbus |  | Accumulated | 001B | 27
Weather Station | Daily cumulative value of direct radiation | DailyCumulativeValueDirectRadiation | Single | 1 | WS | AI | Analog | Modbus |  | Accumulated | 26 | 38
Weather Station | Daily cumulative value of net radiation | DailyCumulativeValueNetRadiation | Single | 1 | WS | AI | Analog | Modbus |  | Accumulated | 28 | 40
Weather Station | Daily cumulative value of photosynthetic radiation | DailyCumulativeValuePhotosyntheticRadiation | Single | 1 | WS | AI | Analog | Modbus |  | Accumulated | 29 | 41
Weather Station | Daily cumulative value of scattered radiation | DailyCumulativeValueScatteredRadiation | Single | 1 | WS | AI | Analog | Modbus |  | Accumulated | 25 | 37
Weather Station | Daily cumulative value of total radiation 1 | DailyCumulativeValueTotalRadiation1 | Single | 1 | WS | AI | Analog | Modbus |  | Accumulated | 24 | 36
Weather Station | Daily sunshine duration | DailySunshineDuration | Single | 1 | WS | AI | Analog | Modbus |  | h | 23 | 35
Weather Station | Dew-point Temperature | DewPointTemperature | Single | 1 | WS | AI | Analog | Modbus |  | °C | 6 | 6
Weather Station | Instantaneous value of total radiation 1 | InstantaneousValueTotalRadiation1 | Single | 1 | WS | AI | Analog | Modbus |  | W/m² | 000E | 14
Weather Station | Instantaneous wind direction | InstantaneousWindDirection | Single | 1 | WS | AI | Analog | Modbus |  | deg | 15 | 21
Weather Station | Instantaneous wind speed | InstantaneousWindSpeed | Single | 1 | WS | AI | Analog | Modbus |  | m/s | 16 | 22
Weather Station | Temperature 1 (Bracket) | Temperature1 | Single | 1 | WS | AI | Analog | Modbus |  | °C | 1 | 1
Weather Station | Wind speed in 2 minutes | WindSpeed2Minutes | Single | 1 | WS | AI | Analog | Modbus |  | m/s | 17 | 23

## Sheet1
connection
protection relay | Device Health | 40128
Weather station | No Address

## Tag_List
Tag List (Expanded)
Tag Name | Device ID | Device Name | Device Type | Signal Description | Point Code | Point Type | Protocol | Source Mode | Point Category | Archive Mode | Sample / Trigger
EM001_ActivePower | EM001 | Energy Meter 001 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM001_ApparentPower | EM001 | Energy Meter 001 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM001_Frequency | EM001 | Energy Meter 001 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM001_PhaseACurrent | EM001 | Energy Meter 001 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM001_PhaseBCurrent | EM001 | Energy Meter 001 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM001_PhaseCCurrent | EM001 | Energy Meter 001 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM001_PowerFactor | EM001 | Energy Meter 001 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM001_ReactivePower | EM001 | Energy Meter 001 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM001_TotalExportVarh | EM001 | Energy Meter 001 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM001_TotalExportWh | EM001 | Energy Meter 001 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM001_TotalImportVarh | EM001 | Energy Meter 001 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM001_TotalImportWh | EM001 | Energy Meter 001 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM002_ActivePower | EM002 | Energy Meter 002 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM002_ApparentPower | EM002 | Energy Meter 002 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM002_Frequency | EM002 | Energy Meter 002 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM002_PhaseACurrent | EM002 | Energy Meter 002 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM002_PhaseBCurrent | EM002 | Energy Meter 002 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM002_PhaseCCurrent | EM002 | Energy Meter 002 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM002_PowerFactor | EM002 | Energy Meter 002 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM002_ReactivePower | EM002 | Energy Meter 002 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM002_TotalExportVarh | EM002 | Energy Meter 002 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM002_TotalExportWh | EM002 | Energy Meter 002 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM002_TotalImportVarh | EM002 | Energy Meter 002 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM002_TotalImportWh | EM002 | Energy Meter 002 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM003_ActivePower | EM003 | Energy Meter 003 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM003_ApparentPower | EM003 | Energy Meter 003 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM003_Frequency | EM003 | Energy Meter 003 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM003_PhaseACurrent | EM003 | Energy Meter 003 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM003_PhaseBCurrent | EM003 | Energy Meter 003 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM003_PhaseCCurrent | EM003 | Energy Meter 003 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM003_PowerFactor | EM003 | Energy Meter 003 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM003_ReactivePower | EM003 | Energy Meter 003 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM003_TotalExportVarh | EM003 | Energy Meter 003 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM003_TotalExportWh | EM003 | Energy Meter 003 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM003_TotalImportVarh | EM003 | Energy Meter 003 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM003_TotalImportWh | EM003 | Energy Meter 003 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM004_ActivePower | EM004 | Energy Meter 004 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM004_ApparentPower | EM004 | Energy Meter 004 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM004_Frequency | EM004 | Energy Meter 004 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM004_PhaseACurrent | EM004 | Energy Meter 004 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM004_PhaseBCurrent | EM004 | Energy Meter 004 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM004_PhaseCCurrent | EM004 | Energy Meter 004 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM004_PowerFactor | EM004 | Energy Meter 004 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM004_ReactivePower | EM004 | Energy Meter 004 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM004_TotalExportVarh | EM004 | Energy Meter 004 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM004_TotalExportWh | EM004 | Energy Meter 004 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM004_TotalImportVarh | EM004 | Energy Meter 004 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM004_TotalImportWh | EM004 | Energy Meter 004 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM005_ActivePower | EM005 | Energy Meter 005 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM005_ApparentPower | EM005 | Energy Meter 005 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM005_Frequency | EM005 | Energy Meter 005 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM005_PhaseACurrent | EM005 | Energy Meter 005 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM005_PhaseBCurrent | EM005 | Energy Meter 005 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM005_PhaseCCurrent | EM005 | Energy Meter 005 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM005_PowerFactor | EM005 | Energy Meter 005 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM005_ReactivePower | EM005 | Energy Meter 005 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM005_TotalExportVarh | EM005 | Energy Meter 005 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM005_TotalExportWh | EM005 | Energy Meter 005 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM005_TotalImportVarh | EM005 | Energy Meter 005 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM005_TotalImportWh | EM005 | Energy Meter 005 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM006_ActivePower | EM006 | Energy Meter 006 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM006_ApparentPower | EM006 | Energy Meter 006 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM006_Frequency | EM006 | Energy Meter 006 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM006_PhaseACurrent | EM006 | Energy Meter 006 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM006_PhaseBCurrent | EM006 | Energy Meter 006 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM006_PhaseCCurrent | EM006 | Energy Meter 006 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM006_PowerFactor | EM006 | Energy Meter 006 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM006_ReactivePower | EM006 | Energy Meter 006 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM006_TotalExportVarh | EM006 | Energy Meter 006 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM006_TotalExportWh | EM006 | Energy Meter 006 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM006_TotalImportVarh | EM006 | Energy Meter 006 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM006_TotalImportWh | EM006 | Energy Meter 006 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM007_ActivePower | EM007 | Energy Meter 007 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM007_ApparentPower | EM007 | Energy Meter 007 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM007_Frequency | EM007 | Energy Meter 007 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM007_PhaseACurrent | EM007 | Energy Meter 007 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM007_PhaseBCurrent | EM007 | Energy Meter 007 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM007_PhaseCCurrent | EM007 | Energy Meter 007 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM007_PowerFactor | EM007 | Energy Meter 007 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM007_ReactivePower | EM007 | Energy Meter 007 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM007_TotalExportVarh | EM007 | Energy Meter 007 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM007_TotalExportWh | EM007 | Energy Meter 007 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM007_TotalImportVarh | EM007 | Energy Meter 007 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM007_TotalImportWh | EM007 | Energy Meter 007 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM008_ActivePower | EM008 | Energy Meter 008 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM008_ApparentPower | EM008 | Energy Meter 008 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM008_Frequency | EM008 | Energy Meter 008 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM008_PhaseACurrent | EM008 | Energy Meter 008 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM008_PhaseBCurrent | EM008 | Energy Meter 008 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM008_PhaseCCurrent | EM008 | Energy Meter 008 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM008_PowerFactor | EM008 | Energy Meter 008 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM008_ReactivePower | EM008 | Energy Meter 008 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM008_TotalExportVarh | EM008 | Energy Meter 008 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM008_TotalExportWh | EM008 | Energy Meter 008 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM008_TotalImportVarh | EM008 | Energy Meter 008 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM008_TotalImportWh | EM008 | Energy Meter 008 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM009_ActivePower | EM009 | Energy Meter 009 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM009_ApparentPower | EM009 | Energy Meter 009 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM009_Frequency | EM009 | Energy Meter 009 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM009_PhaseACurrent | EM009 | Energy Meter 009 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM009_PhaseBCurrent | EM009 | Energy Meter 009 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM009_PhaseCCurrent | EM009 | Energy Meter 009 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM009_PowerFactor | EM009 | Energy Meter 009 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM009_ReactivePower | EM009 | Energy Meter 009 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM009_TotalExportVarh | EM009 | Energy Meter 009 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM009_TotalExportWh | EM009 | Energy Meter 009 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM009_TotalImportVarh | EM009 | Energy Meter 009 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM009_TotalImportWh | EM009 | Energy Meter 009 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM010_ActivePower | EM010 | Energy Meter 010 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM010_ApparentPower | EM010 | Energy Meter 010 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM010_Frequency | EM010 | Energy Meter 010 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM010_PhaseACurrent | EM010 | Energy Meter 010 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM010_PhaseBCurrent | EM010 | Energy Meter 010 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM010_PhaseCCurrent | EM010 | Energy Meter 010 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM010_PowerFactor | EM010 | Energy Meter 010 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM010_ReactivePower | EM010 | Energy Meter 010 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM010_TotalExportVarh | EM010 | Energy Meter 010 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM010_TotalExportWh | EM010 | Energy Meter 010 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM010_TotalImportVarh | EM010 | Energy Meter 010 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM010_TotalImportWh | EM010 | Energy Meter 010 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM011_ActivePower | EM011 | Energy Meter 011 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM011_ApparentPower | EM011 | Energy Meter 011 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM011_Frequency | EM011 | Energy Meter 011 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM011_PhaseACurrent | EM011 | Energy Meter 011 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM011_PhaseBCurrent | EM011 | Energy Meter 011 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM011_PhaseCCurrent | EM011 | Energy Meter 011 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM011_PowerFactor | EM011 | Energy Meter 011 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM011_ReactivePower | EM011 | Energy Meter 011 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM011_TotalExportVarh | EM011 | Energy Meter 011 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM011_TotalExportWh | EM011 | Energy Meter 011 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM011_TotalImportVarh | EM011 | Energy Meter 011 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM011_TotalImportWh | EM011 | Energy Meter 011 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM012_ActivePower | EM012 | Energy Meter 012 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM012_ApparentPower | EM012 | Energy Meter 012 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM012_Frequency | EM012 | Energy Meter 012 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM012_PhaseACurrent | EM012 | Energy Meter 012 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM012_PhaseBCurrent | EM012 | Energy Meter 012 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM012_PhaseCCurrent | EM012 | Energy Meter 012 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM012_PowerFactor | EM012 | Energy Meter 012 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM012_ReactivePower | EM012 | Energy Meter 012 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM012_TotalExportVarh | EM012 | Energy Meter 012 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM012_TotalExportWh | EM012 | Energy Meter 012 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM012_TotalImportVarh | EM012 | Energy Meter 012 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM012_TotalImportWh | EM012 | Energy Meter 012 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM013_ActivePower | EM013 | Energy Meter 013 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM013_ApparentPower | EM013 | Energy Meter 013 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM013_Frequency | EM013 | Energy Meter 013 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM013_PhaseACurrent | EM013 | Energy Meter 013 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM013_PhaseBCurrent | EM013 | Energy Meter 013 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM013_PhaseCCurrent | EM013 | Energy Meter 013 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM013_PowerFactor | EM013 | Energy Meter 013 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM013_ReactivePower | EM013 | Energy Meter 013 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM013_TotalExportVarh | EM013 | Energy Meter 013 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM013_TotalExportWh | EM013 | Energy Meter 013 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM013_TotalImportVarh | EM013 | Energy Meter 013 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM013_TotalImportWh | EM013 | Energy Meter 013 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM014_ActivePower | EM014 | Energy Meter 014 | Energy Meter | Active power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM014_ApparentPower | EM014 | Energy Meter 014 | Energy Meter | Apparent Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM014_Frequency | EM014 | Energy Meter 014 | Energy Meter | Frequency | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM014_PhaseACurrent | EM014 | Energy Meter 014 | Energy Meter | Phase A Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM014_PhaseBCurrent | EM014 | Energy Meter 014 | Energy Meter | Phase B Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM014_PhaseCCurrent | EM014 | Energy Meter 014 | Energy Meter | Phase C Current | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM014_PowerFactor | EM014 | Energy Meter 014 | Energy Meter | Power Factor | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM014_ReactivePower | EM014 | Energy Meter 014 | Energy Meter | Reactive Power | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
EM014_TotalExportVarh | EM014 | Energy Meter 014 | Energy Meter | Total export varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM014_TotalExportWh | EM014 | Energy Meter 014 | Energy Meter | Total export Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM014_TotalImportVarh | EM014 | Energy Meter 014 | Energy Meter | Total import varh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
EM014_TotalImportWh | EM014 | Energy Meter 014 | Energy Meter | Total import Wh | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
INV001_ACCurrent | INV001 | Inverter 001 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_ACOvervoltage | INV001 | Inverter 001 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_ACUndervoltage | INV001 | Inverter 001 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_ACVoltage | INV001 | Inverter 001 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_AFCISelfCheckFailure | INV001 | Inverter 001 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_AbnormalGrounding | INV001 | Inverter 001 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_AbnormalPVModuleConfiguration | INV001 | Inverter 001 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_AbnormalResidualCurrent | INV001 | Inverter 001 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_AbnormalStringPower | INV001 | Inverter 001 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_ActiveIslanding | INV001 | Inverter 001 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_ActivePower | INV001 | Inverter 001 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_ApparentPower | INV001 | Inverter 001 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV001_BuiltPIDOperationAbnormal | INV001 | Inverter 001 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_CabinetOvertemperature | INV001 | Inverter 001 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_CommunicationFailure | INV001 | Inverter 001 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_CommunicationStatus | INV001 | Inverter 001 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_DCArcFault | INV001 | Inverter 001 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_DCCurrent | INV001 | Inverter 001 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_DCInsulationFault | INV001 | Inverter 001 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_DCOvervoltage | INV001 | Inverter 001 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_DCPower | INV001 | Inverter 001 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV001_DCVoltage | INV001 | Inverter 001 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_DailyEnergyYield | INV001 | Inverter 001 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV001_DeviceFault | INV001 | Inverter 001 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_ExternalFanAbnormal | INV001 | Inverter 001 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_FanFailure | INV001 | Inverter 001 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_Faulty | INV001 | Inverter 001 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_FaultyMonitoringUnit | INV001 | Inverter 001 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_FaultyPowerCollector | INV001 | Inverter 001 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_Frequency | INV001 | Inverter 001 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_GeneralFaultTrip | INV001 | Inverter 001 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_Grid | INV001 | Inverter 001 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GridConnectionDeratingInverterInternalCauses | INV001 | Inverter 001 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GridConnectionDeratingPowerRationing | INV001 | Inverter 001 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GridLoss | INV001 | Inverter 001 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GridOverfrequency | INV001 | Inverter 001 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GridOvervoltage | INV001 | Inverter 001 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GridTiedOffGridControllerAbnormal | INV001 | Inverter 001 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GridUnderfrequency | INV001 | Inverter 001 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GridUndervoltage | INV001 | Inverter 001 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GridVoltageImbalance | INV001 | Inverter 001 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_GroundFault | INV001 | Inverter 001 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_HighInputStringVoltageGround | INV001 | Inverter 001 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_HighStringInputVoltage | INV001 | Inverter 001 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_InverterEfficiency | INV001 | Inverter 001 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_InverterGridConnectionStatus | INV001 | Inverter 001 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_InverterOverTemperature | INV001 | Inverter 001 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_InverterRunningStopped | INV001 | Inverter 001 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_InverterStartupShutdownStatus | INV001 | Inverter 001 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_InverterTripHistoryAvailable | INV001 | Inverter 001 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_IslandingDetectionStatus | INV001 | Inverter 001 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_LicenseExpired | INV001 | Inverter 001 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_LockingStatus | INV001 | Inverter 001 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_LowInsulationResistance | INV001 | Inverter 001 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_NormalGridConnection | INV001 | Inverter 001 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_NormalShutdown | INV001 | Inverter 001 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_OffGridOutputOverload | INV001 | Inverter 001 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_OptimizerFault | INV001 | Inverter 001 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_OutputDCComponentOverhigh | INV001 | Inverter 001 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_OutputOvercurrent | INV001 | Inverter 001 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_PVStringLoss | INV001 | Inverter 001 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_PassiveIslanding | INV001 | Inverter 001 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_PeripheralPortShortCircuit | INV001 | Inverter 001 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_PhaseWireShortCircuitedPE | INV001 | Inverter 001 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_PowerCurtailmentStatus | INV001 | Inverter 001 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_PowerFactor | INV001 | Inverter 001 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_PowerLimitationActiveGridCommand | INV001 | Inverter 001 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_ReactivePower | INV001 | Inverter 001 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV001_RemoteOFFStatus | INV001 | Inverter 001 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_Shutdown | INV001 | Inverter 001 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_ShutdownPowerRationing | INV001 | Inverter 001 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_SpotCheck | INV001 | Inverter 001 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_Standby | INV001 | Inverter 001 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_StringCurrentBackfeed | INV001 | Inverter 001 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_StringReverseConnection | INV001 | Inverter 001 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_StringReversePolarity | INV001 | Inverter 001 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_TotalEnergyYield | INV001 | Inverter 001 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV001_TransientACOvervoltage | INV001 | Inverter 001 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_UnstableGridFrequency | INV001 | Inverter 001 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_UpgradeFailed | INV001 | Inverter 001 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV001_WarningActive | INV001 | Inverter 001 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_ACCurrent | INV002 | Inverter 002 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_ACOvervoltage | INV002 | Inverter 002 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_ACUndervoltage | INV002 | Inverter 002 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_ACVoltage | INV002 | Inverter 002 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_AFCISelfCheckFailure | INV002 | Inverter 002 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_AbnormalGrounding | INV002 | Inverter 002 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_AbnormalPVModuleConfiguration | INV002 | Inverter 002 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_AbnormalResidualCurrent | INV002 | Inverter 002 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_AbnormalStringPower | INV002 | Inverter 002 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_ActiveIslanding | INV002 | Inverter 002 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_ActivePower | INV002 | Inverter 002 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_ApparentPower | INV002 | Inverter 002 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV002_BuiltPIDOperationAbnormal | INV002 | Inverter 002 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_CabinetOvertemperature | INV002 | Inverter 002 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_CommunicationFailure | INV002 | Inverter 002 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_CommunicationStatus | INV002 | Inverter 002 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_DCArcFault | INV002 | Inverter 002 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_DCCurrent | INV002 | Inverter 002 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_DCInsulationFault | INV002 | Inverter 002 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_DCOvervoltage | INV002 | Inverter 002 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_DCPower | INV002 | Inverter 002 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV002_DCVoltage | INV002 | Inverter 002 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_DailyEnergyYield | INV002 | Inverter 002 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV002_DeviceFault | INV002 | Inverter 002 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_ExternalFanAbnormal | INV002 | Inverter 002 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_FanFailure | INV002 | Inverter 002 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_Faulty | INV002 | Inverter 002 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_FaultyMonitoringUnit | INV002 | Inverter 002 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_FaultyPowerCollector | INV002 | Inverter 002 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_Frequency | INV002 | Inverter 002 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_GeneralFaultTrip | INV002 | Inverter 002 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_Grid | INV002 | Inverter 002 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GridConnectionDeratingInverterInternalCauses | INV002 | Inverter 002 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GridConnectionDeratingPowerRationing | INV002 | Inverter 002 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GridLoss | INV002 | Inverter 002 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GridOverfrequency | INV002 | Inverter 002 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GridOvervoltage | INV002 | Inverter 002 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GridTiedOffGridControllerAbnormal | INV002 | Inverter 002 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GridUnderfrequency | INV002 | Inverter 002 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GridUndervoltage | INV002 | Inverter 002 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GridVoltageImbalance | INV002 | Inverter 002 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_GroundFault | INV002 | Inverter 002 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_HighInputStringVoltageGround | INV002 | Inverter 002 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_HighStringInputVoltage | INV002 | Inverter 002 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_InverterEfficiency | INV002 | Inverter 002 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_InverterGridConnectionStatus | INV002 | Inverter 002 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_InverterOverTemperature | INV002 | Inverter 002 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_InverterRunningStopped | INV002 | Inverter 002 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_InverterStartupShutdownStatus | INV002 | Inverter 002 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_InverterTripHistoryAvailable | INV002 | Inverter 002 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_IslandingDetectionStatus | INV002 | Inverter 002 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_LicenseExpired | INV002 | Inverter 002 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_LockingStatus | INV002 | Inverter 002 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_LowInsulationResistance | INV002 | Inverter 002 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_NormalGridConnection | INV002 | Inverter 002 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_NormalShutdown | INV002 | Inverter 002 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_OffGridOutputOverload | INV002 | Inverter 002 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_OptimizerFault | INV002 | Inverter 002 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_OutputDCComponentOverhigh | INV002 | Inverter 002 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_OutputOvercurrent | INV002 | Inverter 002 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_PVStringLoss | INV002 | Inverter 002 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_PassiveIslanding | INV002 | Inverter 002 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_PeripheralPortShortCircuit | INV002 | Inverter 002 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_PhaseWireShortCircuitedPE | INV002 | Inverter 002 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_PowerCurtailmentStatus | INV002 | Inverter 002 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_PowerFactor | INV002 | Inverter 002 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_PowerLimitationActiveGridCommand | INV002 | Inverter 002 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_ReactivePower | INV002 | Inverter 002 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV002_RemoteOFFStatus | INV002 | Inverter 002 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_Shutdown | INV002 | Inverter 002 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_ShutdownPowerRationing | INV002 | Inverter 002 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_SpotCheck | INV002 | Inverter 002 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_Standby | INV002 | Inverter 002 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_StringCurrentBackfeed | INV002 | Inverter 002 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_StringReverseConnection | INV002 | Inverter 002 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_StringReversePolarity | INV002 | Inverter 002 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_TotalEnergyYield | INV002 | Inverter 002 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV002_TransientACOvervoltage | INV002 | Inverter 002 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_UnstableGridFrequency | INV002 | Inverter 002 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_UpgradeFailed | INV002 | Inverter 002 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV002_WarningActive | INV002 | Inverter 002 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_ACCurrent | INV003 | Inverter 003 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_ACOvervoltage | INV003 | Inverter 003 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_ACUndervoltage | INV003 | Inverter 003 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_ACVoltage | INV003 | Inverter 003 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_AFCISelfCheckFailure | INV003 | Inverter 003 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_AbnormalGrounding | INV003 | Inverter 003 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_AbnormalPVModuleConfiguration | INV003 | Inverter 003 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_AbnormalResidualCurrent | INV003 | Inverter 003 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_AbnormalStringPower | INV003 | Inverter 003 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_ActiveIslanding | INV003 | Inverter 003 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_ActivePower | INV003 | Inverter 003 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_ApparentPower | INV003 | Inverter 003 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV003_BuiltPIDOperationAbnormal | INV003 | Inverter 003 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_CabinetOvertemperature | INV003 | Inverter 003 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_CommunicationFailure | INV003 | Inverter 003 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_CommunicationStatus | INV003 | Inverter 003 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_DCArcFault | INV003 | Inverter 003 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_DCCurrent | INV003 | Inverter 003 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_DCInsulationFault | INV003 | Inverter 003 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_DCOvervoltage | INV003 | Inverter 003 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_DCPower | INV003 | Inverter 003 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV003_DCVoltage | INV003 | Inverter 003 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_DailyEnergyYield | INV003 | Inverter 003 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV003_DeviceFault | INV003 | Inverter 003 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_ExternalFanAbnormal | INV003 | Inverter 003 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_FanFailure | INV003 | Inverter 003 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_Faulty | INV003 | Inverter 003 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_FaultyMonitoringUnit | INV003 | Inverter 003 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_FaultyPowerCollector | INV003 | Inverter 003 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_Frequency | INV003 | Inverter 003 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_GeneralFaultTrip | INV003 | Inverter 003 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_Grid | INV003 | Inverter 003 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GridConnectionDeratingInverterInternalCauses | INV003 | Inverter 003 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GridConnectionDeratingPowerRationing | INV003 | Inverter 003 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GridLoss | INV003 | Inverter 003 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GridOverfrequency | INV003 | Inverter 003 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GridOvervoltage | INV003 | Inverter 003 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GridTiedOffGridControllerAbnormal | INV003 | Inverter 003 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GridUnderfrequency | INV003 | Inverter 003 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GridUndervoltage | INV003 | Inverter 003 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GridVoltageImbalance | INV003 | Inverter 003 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_GroundFault | INV003 | Inverter 003 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_HighInputStringVoltageGround | INV003 | Inverter 003 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_HighStringInputVoltage | INV003 | Inverter 003 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_InverterEfficiency | INV003 | Inverter 003 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_InverterGridConnectionStatus | INV003 | Inverter 003 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_InverterOverTemperature | INV003 | Inverter 003 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_InverterRunningStopped | INV003 | Inverter 003 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_InverterStartupShutdownStatus | INV003 | Inverter 003 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_InverterTripHistoryAvailable | INV003 | Inverter 003 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_IslandingDetectionStatus | INV003 | Inverter 003 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_LicenseExpired | INV003 | Inverter 003 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_LockingStatus | INV003 | Inverter 003 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_LowInsulationResistance | INV003 | Inverter 003 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_NormalGridConnection | INV003 | Inverter 003 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_NormalShutdown | INV003 | Inverter 003 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_OffGridOutputOverload | INV003 | Inverter 003 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_OptimizerFault | INV003 | Inverter 003 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_OutputDCComponentOverhigh | INV003 | Inverter 003 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_OutputOvercurrent | INV003 | Inverter 003 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_PVStringLoss | INV003 | Inverter 003 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_PassiveIslanding | INV003 | Inverter 003 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_PeripheralPortShortCircuit | INV003 | Inverter 003 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_PhaseWireShortCircuitedPE | INV003 | Inverter 003 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_PowerCurtailmentStatus | INV003 | Inverter 003 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_PowerFactor | INV003 | Inverter 003 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_PowerLimitationActiveGridCommand | INV003 | Inverter 003 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_ReactivePower | INV003 | Inverter 003 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV003_RemoteOFFStatus | INV003 | Inverter 003 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_Shutdown | INV003 | Inverter 003 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_ShutdownPowerRationing | INV003 | Inverter 003 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_SpotCheck | INV003 | Inverter 003 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_Standby | INV003 | Inverter 003 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_StringCurrentBackfeed | INV003 | Inverter 003 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_StringReverseConnection | INV003 | Inverter 003 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_StringReversePolarity | INV003 | Inverter 003 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_TotalEnergyYield | INV003 | Inverter 003 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV003_TransientACOvervoltage | INV003 | Inverter 003 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_UnstableGridFrequency | INV003 | Inverter 003 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_UpgradeFailed | INV003 | Inverter 003 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV003_WarningActive | INV003 | Inverter 003 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_ACCurrent | INV004 | Inverter 004 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_ACOvervoltage | INV004 | Inverter 004 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_ACUndervoltage | INV004 | Inverter 004 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_ACVoltage | INV004 | Inverter 004 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_AFCISelfCheckFailure | INV004 | Inverter 004 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_AbnormalGrounding | INV004 | Inverter 004 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_AbnormalPVModuleConfiguration | INV004 | Inverter 004 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_AbnormalResidualCurrent | INV004 | Inverter 004 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_AbnormalStringPower | INV004 | Inverter 004 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_ActiveIslanding | INV004 | Inverter 004 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_ActivePower | INV004 | Inverter 004 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_ApparentPower | INV004 | Inverter 004 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV004_BuiltPIDOperationAbnormal | INV004 | Inverter 004 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_CabinetOvertemperature | INV004 | Inverter 004 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_CommunicationFailure | INV004 | Inverter 004 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_CommunicationStatus | INV004 | Inverter 004 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_DCArcFault | INV004 | Inverter 004 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_DCCurrent | INV004 | Inverter 004 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_DCInsulationFault | INV004 | Inverter 004 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_DCOvervoltage | INV004 | Inverter 004 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_DCPower | INV004 | Inverter 004 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV004_DCVoltage | INV004 | Inverter 004 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_DailyEnergyYield | INV004 | Inverter 004 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV004_DeviceFault | INV004 | Inverter 004 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_ExternalFanAbnormal | INV004 | Inverter 004 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_FanFailure | INV004 | Inverter 004 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_Faulty | INV004 | Inverter 004 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_FaultyMonitoringUnit | INV004 | Inverter 004 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_FaultyPowerCollector | INV004 | Inverter 004 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_Frequency | INV004 | Inverter 004 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_GeneralFaultTrip | INV004 | Inverter 004 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_Grid | INV004 | Inverter 004 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GridConnectionDeratingInverterInternalCauses | INV004 | Inverter 004 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GridConnectionDeratingPowerRationing | INV004 | Inverter 004 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GridLoss | INV004 | Inverter 004 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GridOverfrequency | INV004 | Inverter 004 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GridOvervoltage | INV004 | Inverter 004 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GridTiedOffGridControllerAbnormal | INV004 | Inverter 004 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GridUnderfrequency | INV004 | Inverter 004 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GridUndervoltage | INV004 | Inverter 004 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GridVoltageImbalance | INV004 | Inverter 004 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_GroundFault | INV004 | Inverter 004 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_HighInputStringVoltageGround | INV004 | Inverter 004 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_HighStringInputVoltage | INV004 | Inverter 004 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_InverterEfficiency | INV004 | Inverter 004 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_InverterGridConnectionStatus | INV004 | Inverter 004 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_InverterOverTemperature | INV004 | Inverter 004 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_InverterRunningStopped | INV004 | Inverter 004 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_InverterStartupShutdownStatus | INV004 | Inverter 004 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_InverterTripHistoryAvailable | INV004 | Inverter 004 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_IslandingDetectionStatus | INV004 | Inverter 004 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_LicenseExpired | INV004 | Inverter 004 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_LockingStatus | INV004 | Inverter 004 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_LowInsulationResistance | INV004 | Inverter 004 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_NormalGridConnection | INV004 | Inverter 004 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_NormalShutdown | INV004 | Inverter 004 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_OffGridOutputOverload | INV004 | Inverter 004 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_OptimizerFault | INV004 | Inverter 004 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_OutputDCComponentOverhigh | INV004 | Inverter 004 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_OutputOvercurrent | INV004 | Inverter 004 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_PVStringLoss | INV004 | Inverter 004 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_PassiveIslanding | INV004 | Inverter 004 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_PeripheralPortShortCircuit | INV004 | Inverter 004 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_PhaseWireShortCircuitedPE | INV004 | Inverter 004 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_PowerCurtailmentStatus | INV004 | Inverter 004 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_PowerFactor | INV004 | Inverter 004 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_PowerLimitationActiveGridCommand | INV004 | Inverter 004 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_ReactivePower | INV004 | Inverter 004 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV004_RemoteOFFStatus | INV004 | Inverter 004 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_Shutdown | INV004 | Inverter 004 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_ShutdownPowerRationing | INV004 | Inverter 004 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_SpotCheck | INV004 | Inverter 004 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_Standby | INV004 | Inverter 004 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_StringCurrentBackfeed | INV004 | Inverter 004 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_StringReverseConnection | INV004 | Inverter 004 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_StringReversePolarity | INV004 | Inverter 004 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_TotalEnergyYield | INV004 | Inverter 004 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV004_TransientACOvervoltage | INV004 | Inverter 004 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_UnstableGridFrequency | INV004 | Inverter 004 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_UpgradeFailed | INV004 | Inverter 004 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV004_WarningActive | INV004 | Inverter 004 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_ACCurrent | INV005 | Inverter 005 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_ACOvervoltage | INV005 | Inverter 005 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_ACUndervoltage | INV005 | Inverter 005 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_ACVoltage | INV005 | Inverter 005 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_AFCISelfCheckFailure | INV005 | Inverter 005 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_AbnormalGrounding | INV005 | Inverter 005 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_AbnormalPVModuleConfiguration | INV005 | Inverter 005 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_AbnormalResidualCurrent | INV005 | Inverter 005 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_AbnormalStringPower | INV005 | Inverter 005 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_ActiveIslanding | INV005 | Inverter 005 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_ActivePower | INV005 | Inverter 005 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_ApparentPower | INV005 | Inverter 005 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV005_BuiltPIDOperationAbnormal | INV005 | Inverter 005 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_CabinetOvertemperature | INV005 | Inverter 005 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_CommunicationFailure | INV005 | Inverter 005 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_CommunicationStatus | INV005 | Inverter 005 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_DCArcFault | INV005 | Inverter 005 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_DCCurrent | INV005 | Inverter 005 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_DCInsulationFault | INV005 | Inverter 005 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_DCOvervoltage | INV005 | Inverter 005 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_DCPower | INV005 | Inverter 005 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV005_DCVoltage | INV005 | Inverter 005 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_DailyEnergyYield | INV005 | Inverter 005 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV005_DeviceFault | INV005 | Inverter 005 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_ExternalFanAbnormal | INV005 | Inverter 005 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_FanFailure | INV005 | Inverter 005 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_Faulty | INV005 | Inverter 005 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_FaultyMonitoringUnit | INV005 | Inverter 005 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_FaultyPowerCollector | INV005 | Inverter 005 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_Frequency | INV005 | Inverter 005 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_GeneralFaultTrip | INV005 | Inverter 005 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_Grid | INV005 | Inverter 005 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GridConnectionDeratingInverterInternalCauses | INV005 | Inverter 005 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GridConnectionDeratingPowerRationing | INV005 | Inverter 005 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GridLoss | INV005 | Inverter 005 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GridOverfrequency | INV005 | Inverter 005 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GridOvervoltage | INV005 | Inverter 005 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GridTiedOffGridControllerAbnormal | INV005 | Inverter 005 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GridUnderfrequency | INV005 | Inverter 005 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GridUndervoltage | INV005 | Inverter 005 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GridVoltageImbalance | INV005 | Inverter 005 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_GroundFault | INV005 | Inverter 005 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_HighInputStringVoltageGround | INV005 | Inverter 005 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_HighStringInputVoltage | INV005 | Inverter 005 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_InverterEfficiency | INV005 | Inverter 005 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_InverterGridConnectionStatus | INV005 | Inverter 005 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_InverterOverTemperature | INV005 | Inverter 005 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_InverterRunningStopped | INV005 | Inverter 005 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_InverterStartupShutdownStatus | INV005 | Inverter 005 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_InverterTripHistoryAvailable | INV005 | Inverter 005 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_IslandingDetectionStatus | INV005 | Inverter 005 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_LicenseExpired | INV005 | Inverter 005 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_LockingStatus | INV005 | Inverter 005 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_LowInsulationResistance | INV005 | Inverter 005 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_NormalGridConnection | INV005 | Inverter 005 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_NormalShutdown | INV005 | Inverter 005 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_OffGridOutputOverload | INV005 | Inverter 005 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_OptimizerFault | INV005 | Inverter 005 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_OutputDCComponentOverhigh | INV005 | Inverter 005 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_OutputOvercurrent | INV005 | Inverter 005 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_PVStringLoss | INV005 | Inverter 005 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_PassiveIslanding | INV005 | Inverter 005 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_PeripheralPortShortCircuit | INV005 | Inverter 005 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_PhaseWireShortCircuitedPE | INV005 | Inverter 005 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_PowerCurtailmentStatus | INV005 | Inverter 005 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_PowerFactor | INV005 | Inverter 005 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_PowerLimitationActiveGridCommand | INV005 | Inverter 005 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_ReactivePower | INV005 | Inverter 005 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV005_RemoteOFFStatus | INV005 | Inverter 005 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_Shutdown | INV005 | Inverter 005 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_ShutdownPowerRationing | INV005 | Inverter 005 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_SpotCheck | INV005 | Inverter 005 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_Standby | INV005 | Inverter 005 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_StringCurrentBackfeed | INV005 | Inverter 005 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_StringReverseConnection | INV005 | Inverter 005 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_StringReversePolarity | INV005 | Inverter 005 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_TotalEnergyYield | INV005 | Inverter 005 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV005_TransientACOvervoltage | INV005 | Inverter 005 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_UnstableGridFrequency | INV005 | Inverter 005 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_UpgradeFailed | INV005 | Inverter 005 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV005_WarningActive | INV005 | Inverter 005 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_ACCurrent | INV006 | Inverter 006 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_ACOvervoltage | INV006 | Inverter 006 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_ACUndervoltage | INV006 | Inverter 006 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_ACVoltage | INV006 | Inverter 006 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_AFCISelfCheckFailure | INV006 | Inverter 006 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_AbnormalGrounding | INV006 | Inverter 006 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_AbnormalPVModuleConfiguration | INV006 | Inverter 006 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_AbnormalResidualCurrent | INV006 | Inverter 006 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_AbnormalStringPower | INV006 | Inverter 006 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_ActiveIslanding | INV006 | Inverter 006 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_ActivePower | INV006 | Inverter 006 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_ApparentPower | INV006 | Inverter 006 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV006_BuiltPIDOperationAbnormal | INV006 | Inverter 006 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_CabinetOvertemperature | INV006 | Inverter 006 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_CommunicationFailure | INV006 | Inverter 006 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_CommunicationStatus | INV006 | Inverter 006 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_DCArcFault | INV006 | Inverter 006 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_DCCurrent | INV006 | Inverter 006 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_DCInsulationFault | INV006 | Inverter 006 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_DCOvervoltage | INV006 | Inverter 006 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_DCPower | INV006 | Inverter 006 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV006_DCVoltage | INV006 | Inverter 006 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_DailyEnergyYield | INV006 | Inverter 006 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV006_DeviceFault | INV006 | Inverter 006 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_ExternalFanAbnormal | INV006 | Inverter 006 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_FanFailure | INV006 | Inverter 006 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_Faulty | INV006 | Inverter 006 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_FaultyMonitoringUnit | INV006 | Inverter 006 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_FaultyPowerCollector | INV006 | Inverter 006 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_Frequency | INV006 | Inverter 006 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_GeneralFaultTrip | INV006 | Inverter 006 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_Grid | INV006 | Inverter 006 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GridConnectionDeratingInverterInternalCauses | INV006 | Inverter 006 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GridConnectionDeratingPowerRationing | INV006 | Inverter 006 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GridLoss | INV006 | Inverter 006 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GridOverfrequency | INV006 | Inverter 006 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GridOvervoltage | INV006 | Inverter 006 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GridTiedOffGridControllerAbnormal | INV006 | Inverter 006 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GridUnderfrequency | INV006 | Inverter 006 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GridUndervoltage | INV006 | Inverter 006 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GridVoltageImbalance | INV006 | Inverter 006 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_GroundFault | INV006 | Inverter 006 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_HighInputStringVoltageGround | INV006 | Inverter 006 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_HighStringInputVoltage | INV006 | Inverter 006 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_InverterEfficiency | INV006 | Inverter 006 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_InverterGridConnectionStatus | INV006 | Inverter 006 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_InverterOverTemperature | INV006 | Inverter 006 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_InverterRunningStopped | INV006 | Inverter 006 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_InverterStartupShutdownStatus | INV006 | Inverter 006 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_InverterTripHistoryAvailable | INV006 | Inverter 006 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_IslandingDetectionStatus | INV006 | Inverter 006 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_LicenseExpired | INV006 | Inverter 006 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_LockingStatus | INV006 | Inverter 006 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_LowInsulationResistance | INV006 | Inverter 006 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_NormalGridConnection | INV006 | Inverter 006 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_NormalShutdown | INV006 | Inverter 006 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_OffGridOutputOverload | INV006 | Inverter 006 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_OptimizerFault | INV006 | Inverter 006 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_OutputDCComponentOverhigh | INV006 | Inverter 006 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_OutputOvercurrent | INV006 | Inverter 006 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_PVStringLoss | INV006 | Inverter 006 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_PassiveIslanding | INV006 | Inverter 006 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_PeripheralPortShortCircuit | INV006 | Inverter 006 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_PhaseWireShortCircuitedPE | INV006 | Inverter 006 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_PowerCurtailmentStatus | INV006 | Inverter 006 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_PowerFactor | INV006 | Inverter 006 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_PowerLimitationActiveGridCommand | INV006 | Inverter 006 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_ReactivePower | INV006 | Inverter 006 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV006_RemoteOFFStatus | INV006 | Inverter 006 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_Shutdown | INV006 | Inverter 006 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_ShutdownPowerRationing | INV006 | Inverter 006 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_SpotCheck | INV006 | Inverter 006 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_Standby | INV006 | Inverter 006 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_StringCurrentBackfeed | INV006 | Inverter 006 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_StringReverseConnection | INV006 | Inverter 006 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_StringReversePolarity | INV006 | Inverter 006 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_TotalEnergyYield | INV006 | Inverter 006 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV006_TransientACOvervoltage | INV006 | Inverter 006 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_UnstableGridFrequency | INV006 | Inverter 006 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_UpgradeFailed | INV006 | Inverter 006 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV006_WarningActive | INV006 | Inverter 006 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_ACCurrent | INV007 | Inverter 007 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_ACOvervoltage | INV007 | Inverter 007 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_ACUndervoltage | INV007 | Inverter 007 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_ACVoltage | INV007 | Inverter 007 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_AFCISelfCheckFailure | INV007 | Inverter 007 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_AbnormalGrounding | INV007 | Inverter 007 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_AbnormalPVModuleConfiguration | INV007 | Inverter 007 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_AbnormalResidualCurrent | INV007 | Inverter 007 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_AbnormalStringPower | INV007 | Inverter 007 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_ActiveIslanding | INV007 | Inverter 007 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_ActivePower | INV007 | Inverter 007 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_ApparentPower | INV007 | Inverter 007 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV007_BuiltPIDOperationAbnormal | INV007 | Inverter 007 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_CabinetOvertemperature | INV007 | Inverter 007 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_CommunicationFailure | INV007 | Inverter 007 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_CommunicationStatus | INV007 | Inverter 007 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_DCArcFault | INV007 | Inverter 007 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_DCCurrent | INV007 | Inverter 007 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_DCInsulationFault | INV007 | Inverter 007 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_DCOvervoltage | INV007 | Inverter 007 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_DCPower | INV007 | Inverter 007 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV007_DCVoltage | INV007 | Inverter 007 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_DailyEnergyYield | INV007 | Inverter 007 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV007_DeviceFault | INV007 | Inverter 007 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_ExternalFanAbnormal | INV007 | Inverter 007 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_FanFailure | INV007 | Inverter 007 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_Faulty | INV007 | Inverter 007 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_FaultyMonitoringUnit | INV007 | Inverter 007 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_FaultyPowerCollector | INV007 | Inverter 007 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_Frequency | INV007 | Inverter 007 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_GeneralFaultTrip | INV007 | Inverter 007 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_Grid | INV007 | Inverter 007 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GridConnectionDeratingInverterInternalCauses | INV007 | Inverter 007 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GridConnectionDeratingPowerRationing | INV007 | Inverter 007 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GridLoss | INV007 | Inverter 007 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GridOverfrequency | INV007 | Inverter 007 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GridOvervoltage | INV007 | Inverter 007 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GridTiedOffGridControllerAbnormal | INV007 | Inverter 007 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GridUnderfrequency | INV007 | Inverter 007 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GridUndervoltage | INV007 | Inverter 007 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GridVoltageImbalance | INV007 | Inverter 007 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_GroundFault | INV007 | Inverter 007 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_HighInputStringVoltageGround | INV007 | Inverter 007 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_HighStringInputVoltage | INV007 | Inverter 007 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_InverterEfficiency | INV007 | Inverter 007 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_InverterGridConnectionStatus | INV007 | Inverter 007 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_InverterOverTemperature | INV007 | Inverter 007 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_InverterRunningStopped | INV007 | Inverter 007 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_InverterStartupShutdownStatus | INV007 | Inverter 007 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_InverterTripHistoryAvailable | INV007 | Inverter 007 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_IslandingDetectionStatus | INV007 | Inverter 007 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_LicenseExpired | INV007 | Inverter 007 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_LockingStatus | INV007 | Inverter 007 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_LowInsulationResistance | INV007 | Inverter 007 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_NormalGridConnection | INV007 | Inverter 007 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_NormalShutdown | INV007 | Inverter 007 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_OffGridOutputOverload | INV007 | Inverter 007 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_OptimizerFault | INV007 | Inverter 007 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_OutputDCComponentOverhigh | INV007 | Inverter 007 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_OutputOvercurrent | INV007 | Inverter 007 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_PVStringLoss | INV007 | Inverter 007 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_PassiveIslanding | INV007 | Inverter 007 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_PeripheralPortShortCircuit | INV007 | Inverter 007 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_PhaseWireShortCircuitedPE | INV007 | Inverter 007 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_PowerCurtailmentStatus | INV007 | Inverter 007 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_PowerFactor | INV007 | Inverter 007 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_PowerLimitationActiveGridCommand | INV007 | Inverter 007 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_ReactivePower | INV007 | Inverter 007 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV007_RemoteOFFStatus | INV007 | Inverter 007 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_Shutdown | INV007 | Inverter 007 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_ShutdownPowerRationing | INV007 | Inverter 007 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_SpotCheck | INV007 | Inverter 007 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_Standby | INV007 | Inverter 007 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_StringCurrentBackfeed | INV007 | Inverter 007 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_StringReverseConnection | INV007 | Inverter 007 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_StringReversePolarity | INV007 | Inverter 007 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_TotalEnergyYield | INV007 | Inverter 007 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV007_TransientACOvervoltage | INV007 | Inverter 007 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_UnstableGridFrequency | INV007 | Inverter 007 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_UpgradeFailed | INV007 | Inverter 007 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV007_WarningActive | INV007 | Inverter 007 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_ACCurrent | INV008 | Inverter 008 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_ACOvervoltage | INV008 | Inverter 008 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_ACUndervoltage | INV008 | Inverter 008 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_ACVoltage | INV008 | Inverter 008 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_AFCISelfCheckFailure | INV008 | Inverter 008 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_AbnormalGrounding | INV008 | Inverter 008 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_AbnormalPVModuleConfiguration | INV008 | Inverter 008 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_AbnormalResidualCurrent | INV008 | Inverter 008 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_AbnormalStringPower | INV008 | Inverter 008 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_ActiveIslanding | INV008 | Inverter 008 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_ActivePower | INV008 | Inverter 008 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_ApparentPower | INV008 | Inverter 008 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV008_BuiltPIDOperationAbnormal | INV008 | Inverter 008 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_CabinetOvertemperature | INV008 | Inverter 008 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_CommunicationFailure | INV008 | Inverter 008 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_CommunicationStatus | INV008 | Inverter 008 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_DCArcFault | INV008 | Inverter 008 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_DCCurrent | INV008 | Inverter 008 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_DCInsulationFault | INV008 | Inverter 008 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_DCOvervoltage | INV008 | Inverter 008 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_DCPower | INV008 | Inverter 008 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV008_DCVoltage | INV008 | Inverter 008 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_DailyEnergyYield | INV008 | Inverter 008 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV008_DeviceFault | INV008 | Inverter 008 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_ExternalFanAbnormal | INV008 | Inverter 008 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_FanFailure | INV008 | Inverter 008 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_Faulty | INV008 | Inverter 008 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_FaultyMonitoringUnit | INV008 | Inverter 008 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_FaultyPowerCollector | INV008 | Inverter 008 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_Frequency | INV008 | Inverter 008 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_GeneralFaultTrip | INV008 | Inverter 008 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_Grid | INV008 | Inverter 008 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GridConnectionDeratingInverterInternalCauses | INV008 | Inverter 008 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GridConnectionDeratingPowerRationing | INV008 | Inverter 008 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GridLoss | INV008 | Inverter 008 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GridOverfrequency | INV008 | Inverter 008 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GridOvervoltage | INV008 | Inverter 008 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GridTiedOffGridControllerAbnormal | INV008 | Inverter 008 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GridUnderfrequency | INV008 | Inverter 008 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GridUndervoltage | INV008 | Inverter 008 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GridVoltageImbalance | INV008 | Inverter 008 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_GroundFault | INV008 | Inverter 008 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_HighInputStringVoltageGround | INV008 | Inverter 008 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_HighStringInputVoltage | INV008 | Inverter 008 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_InverterEfficiency | INV008 | Inverter 008 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_InverterGridConnectionStatus | INV008 | Inverter 008 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_InverterOverTemperature | INV008 | Inverter 008 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_InverterRunningStopped | INV008 | Inverter 008 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_InverterStartupShutdownStatus | INV008 | Inverter 008 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_InverterTripHistoryAvailable | INV008 | Inverter 008 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_IslandingDetectionStatus | INV008 | Inverter 008 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_LicenseExpired | INV008 | Inverter 008 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_LockingStatus | INV008 | Inverter 008 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_LowInsulationResistance | INV008 | Inverter 008 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_NormalGridConnection | INV008 | Inverter 008 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_NormalShutdown | INV008 | Inverter 008 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_OffGridOutputOverload | INV008 | Inverter 008 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_OptimizerFault | INV008 | Inverter 008 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_OutputDCComponentOverhigh | INV008 | Inverter 008 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_OutputOvercurrent | INV008 | Inverter 008 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_PVStringLoss | INV008 | Inverter 008 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_PassiveIslanding | INV008 | Inverter 008 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_PeripheralPortShortCircuit | INV008 | Inverter 008 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_PhaseWireShortCircuitedPE | INV008 | Inverter 008 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_PowerCurtailmentStatus | INV008 | Inverter 008 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_PowerFactor | INV008 | Inverter 008 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_PowerLimitationActiveGridCommand | INV008 | Inverter 008 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_ReactivePower | INV008 | Inverter 008 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV008_RemoteOFFStatus | INV008 | Inverter 008 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_Shutdown | INV008 | Inverter 008 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_ShutdownPowerRationing | INV008 | Inverter 008 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_SpotCheck | INV008 | Inverter 008 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_Standby | INV008 | Inverter 008 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_StringCurrentBackfeed | INV008 | Inverter 008 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_StringReverseConnection | INV008 | Inverter 008 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_StringReversePolarity | INV008 | Inverter 008 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_TotalEnergyYield | INV008 | Inverter 008 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV008_TransientACOvervoltage | INV008 | Inverter 008 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_UnstableGridFrequency | INV008 | Inverter 008 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_UpgradeFailed | INV008 | Inverter 008 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV008_WarningActive | INV008 | Inverter 008 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_ACCurrent | INV009 | Inverter 009 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_ACOvervoltage | INV009 | Inverter 009 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_ACUndervoltage | INV009 | Inverter 009 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_ACVoltage | INV009 | Inverter 009 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_AFCISelfCheckFailure | INV009 | Inverter 009 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_AbnormalGrounding | INV009 | Inverter 009 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_AbnormalPVModuleConfiguration | INV009 | Inverter 009 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_AbnormalResidualCurrent | INV009 | Inverter 009 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_AbnormalStringPower | INV009 | Inverter 009 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_ActiveIslanding | INV009 | Inverter 009 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_ActivePower | INV009 | Inverter 009 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_ApparentPower | INV009 | Inverter 009 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV009_BuiltPIDOperationAbnormal | INV009 | Inverter 009 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_CabinetOvertemperature | INV009 | Inverter 009 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_CommunicationFailure | INV009 | Inverter 009 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_CommunicationStatus | INV009 | Inverter 009 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_DCArcFault | INV009 | Inverter 009 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_DCCurrent | INV009 | Inverter 009 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_DCInsulationFault | INV009 | Inverter 009 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_DCOvervoltage | INV009 | Inverter 009 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_DCPower | INV009 | Inverter 009 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV009_DCVoltage | INV009 | Inverter 009 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_DailyEnergyYield | INV009 | Inverter 009 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV009_DeviceFault | INV009 | Inverter 009 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_ExternalFanAbnormal | INV009 | Inverter 009 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_FanFailure | INV009 | Inverter 009 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_Faulty | INV009 | Inverter 009 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_FaultyMonitoringUnit | INV009 | Inverter 009 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_FaultyPowerCollector | INV009 | Inverter 009 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_Frequency | INV009 | Inverter 009 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_GeneralFaultTrip | INV009 | Inverter 009 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_Grid | INV009 | Inverter 009 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GridConnectionDeratingInverterInternalCauses | INV009 | Inverter 009 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GridConnectionDeratingPowerRationing | INV009 | Inverter 009 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GridLoss | INV009 | Inverter 009 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GridOverfrequency | INV009 | Inverter 009 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GridOvervoltage | INV009 | Inverter 009 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GridTiedOffGridControllerAbnormal | INV009 | Inverter 009 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GridUnderfrequency | INV009 | Inverter 009 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GridUndervoltage | INV009 | Inverter 009 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GridVoltageImbalance | INV009 | Inverter 009 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_GroundFault | INV009 | Inverter 009 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_HighInputStringVoltageGround | INV009 | Inverter 009 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_HighStringInputVoltage | INV009 | Inverter 009 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_InverterEfficiency | INV009 | Inverter 009 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_InverterGridConnectionStatus | INV009 | Inverter 009 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_InverterOverTemperature | INV009 | Inverter 009 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_InverterRunningStopped | INV009 | Inverter 009 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_InverterStartupShutdownStatus | INV009 | Inverter 009 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_InverterTripHistoryAvailable | INV009 | Inverter 009 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_IslandingDetectionStatus | INV009 | Inverter 009 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_LicenseExpired | INV009 | Inverter 009 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_LockingStatus | INV009 | Inverter 009 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_LowInsulationResistance | INV009 | Inverter 009 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_NormalGridConnection | INV009 | Inverter 009 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_NormalShutdown | INV009 | Inverter 009 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_OffGridOutputOverload | INV009 | Inverter 009 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_OptimizerFault | INV009 | Inverter 009 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_OutputDCComponentOverhigh | INV009 | Inverter 009 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_OutputOvercurrent | INV009 | Inverter 009 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_PVStringLoss | INV009 | Inverter 009 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_PassiveIslanding | INV009 | Inverter 009 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_PeripheralPortShortCircuit | INV009 | Inverter 009 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_PhaseWireShortCircuitedPE | INV009 | Inverter 009 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_PowerCurtailmentStatus | INV009 | Inverter 009 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_PowerFactor | INV009 | Inverter 009 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_PowerLimitationActiveGridCommand | INV009 | Inverter 009 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_ReactivePower | INV009 | Inverter 009 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV009_RemoteOFFStatus | INV009 | Inverter 009 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_Shutdown | INV009 | Inverter 009 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_ShutdownPowerRationing | INV009 | Inverter 009 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_SpotCheck | INV009 | Inverter 009 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_Standby | INV009 | Inverter 009 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_StringCurrentBackfeed | INV009 | Inverter 009 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_StringReverseConnection | INV009 | Inverter 009 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_StringReversePolarity | INV009 | Inverter 009 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_TotalEnergyYield | INV009 | Inverter 009 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV009_TransientACOvervoltage | INV009 | Inverter 009 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_UnstableGridFrequency | INV009 | Inverter 009 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_UpgradeFailed | INV009 | Inverter 009 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV009_WarningActive | INV009 | Inverter 009 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_ACCurrent | INV010 | Inverter 010 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_ACOvervoltage | INV010 | Inverter 010 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_ACUndervoltage | INV010 | Inverter 010 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_ACVoltage | INV010 | Inverter 010 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_AFCISelfCheckFailure | INV010 | Inverter 010 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_AbnormalGrounding | INV010 | Inverter 010 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_AbnormalPVModuleConfiguration | INV010 | Inverter 010 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_AbnormalResidualCurrent | INV010 | Inverter 010 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_AbnormalStringPower | INV010 | Inverter 010 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_ActiveIslanding | INV010 | Inverter 010 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_ActivePower | INV010 | Inverter 010 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_ApparentPower | INV010 | Inverter 010 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV010_BuiltPIDOperationAbnormal | INV010 | Inverter 010 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_CabinetOvertemperature | INV010 | Inverter 010 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_CommunicationFailure | INV010 | Inverter 010 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_CommunicationStatus | INV010 | Inverter 010 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_DCArcFault | INV010 | Inverter 010 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_DCCurrent | INV010 | Inverter 010 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_DCInsulationFault | INV010 | Inverter 010 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_DCOvervoltage | INV010 | Inverter 010 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_DCPower | INV010 | Inverter 010 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV010_DCVoltage | INV010 | Inverter 010 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_DailyEnergyYield | INV010 | Inverter 010 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV010_DeviceFault | INV010 | Inverter 010 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_ExternalFanAbnormal | INV010 | Inverter 010 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_FanFailure | INV010 | Inverter 010 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_Faulty | INV010 | Inverter 010 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_FaultyMonitoringUnit | INV010 | Inverter 010 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_FaultyPowerCollector | INV010 | Inverter 010 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_Frequency | INV010 | Inverter 010 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_GeneralFaultTrip | INV010 | Inverter 010 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_Grid | INV010 | Inverter 010 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GridConnectionDeratingInverterInternalCauses | INV010 | Inverter 010 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GridConnectionDeratingPowerRationing | INV010 | Inverter 010 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GridLoss | INV010 | Inverter 010 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GridOverfrequency | INV010 | Inverter 010 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GridOvervoltage | INV010 | Inverter 010 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GridTiedOffGridControllerAbnormal | INV010 | Inverter 010 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GridUnderfrequency | INV010 | Inverter 010 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GridUndervoltage | INV010 | Inverter 010 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GridVoltageImbalance | INV010 | Inverter 010 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_GroundFault | INV010 | Inverter 010 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_HighInputStringVoltageGround | INV010 | Inverter 010 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_HighStringInputVoltage | INV010 | Inverter 010 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_InverterEfficiency | INV010 | Inverter 010 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_InverterGridConnectionStatus | INV010 | Inverter 010 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_InverterOverTemperature | INV010 | Inverter 010 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_InverterRunningStopped | INV010 | Inverter 010 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_InverterStartupShutdownStatus | INV010 | Inverter 010 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_InverterTripHistoryAvailable | INV010 | Inverter 010 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_IslandingDetectionStatus | INV010 | Inverter 010 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_LicenseExpired | INV010 | Inverter 010 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_LockingStatus | INV010 | Inverter 010 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_LowInsulationResistance | INV010 | Inverter 010 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_NormalGridConnection | INV010 | Inverter 010 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_NormalShutdown | INV010 | Inverter 010 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_OffGridOutputOverload | INV010 | Inverter 010 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_OptimizerFault | INV010 | Inverter 010 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_OutputDCComponentOverhigh | INV010 | Inverter 010 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_OutputOvercurrent | INV010 | Inverter 010 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_PVStringLoss | INV010 | Inverter 010 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_PassiveIslanding | INV010 | Inverter 010 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_PeripheralPortShortCircuit | INV010 | Inverter 010 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_PhaseWireShortCircuitedPE | INV010 | Inverter 010 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_PowerCurtailmentStatus | INV010 | Inverter 010 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_PowerFactor | INV010 | Inverter 010 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_PowerLimitationActiveGridCommand | INV010 | Inverter 010 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_ReactivePower | INV010 | Inverter 010 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV010_RemoteOFFStatus | INV010 | Inverter 010 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_Shutdown | INV010 | Inverter 010 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_ShutdownPowerRationing | INV010 | Inverter 010 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_SpotCheck | INV010 | Inverter 010 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_Standby | INV010 | Inverter 010 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_StringCurrentBackfeed | INV010 | Inverter 010 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_StringReverseConnection | INV010 | Inverter 010 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_StringReversePolarity | INV010 | Inverter 010 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_TotalEnergyYield | INV010 | Inverter 010 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV010_TransientACOvervoltage | INV010 | Inverter 010 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_UnstableGridFrequency | INV010 | Inverter 010 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_UpgradeFailed | INV010 | Inverter 010 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV010_WarningActive | INV010 | Inverter 010 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_ACCurrent | INV011 | Inverter 011 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_ACOvervoltage | INV011 | Inverter 011 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_ACUndervoltage | INV011 | Inverter 011 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_ACVoltage | INV011 | Inverter 011 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_AFCISelfCheckFailure | INV011 | Inverter 011 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_AbnormalGrounding | INV011 | Inverter 011 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_AbnormalPVModuleConfiguration | INV011 | Inverter 011 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_AbnormalResidualCurrent | INV011 | Inverter 011 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_AbnormalStringPower | INV011 | Inverter 011 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_ActiveIslanding | INV011 | Inverter 011 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_ActivePower | INV011 | Inverter 011 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_ApparentPower | INV011 | Inverter 011 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV011_BuiltPIDOperationAbnormal | INV011 | Inverter 011 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_CabinetOvertemperature | INV011 | Inverter 011 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_CommunicationFailure | INV011 | Inverter 011 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_CommunicationStatus | INV011 | Inverter 011 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_DCArcFault | INV011 | Inverter 011 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_DCCurrent | INV011 | Inverter 011 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_DCInsulationFault | INV011 | Inverter 011 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_DCOvervoltage | INV011 | Inverter 011 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_DCPower | INV011 | Inverter 011 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV011_DCVoltage | INV011 | Inverter 011 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_DailyEnergyYield | INV011 | Inverter 011 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV011_DeviceFault | INV011 | Inverter 011 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_ExternalFanAbnormal | INV011 | Inverter 011 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_FanFailure | INV011 | Inverter 011 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_Faulty | INV011 | Inverter 011 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_FaultyMonitoringUnit | INV011 | Inverter 011 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_FaultyPowerCollector | INV011 | Inverter 011 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_Frequency | INV011 | Inverter 011 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_GeneralFaultTrip | INV011 | Inverter 011 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_Grid | INV011 | Inverter 011 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GridConnectionDeratingInverterInternalCauses | INV011 | Inverter 011 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GridConnectionDeratingPowerRationing | INV011 | Inverter 011 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GridLoss | INV011 | Inverter 011 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GridOverfrequency | INV011 | Inverter 011 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GridOvervoltage | INV011 | Inverter 011 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GridTiedOffGridControllerAbnormal | INV011 | Inverter 011 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GridUnderfrequency | INV011 | Inverter 011 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GridUndervoltage | INV011 | Inverter 011 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GridVoltageImbalance | INV011 | Inverter 011 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_GroundFault | INV011 | Inverter 011 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_HighInputStringVoltageGround | INV011 | Inverter 011 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_HighStringInputVoltage | INV011 | Inverter 011 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_InverterEfficiency | INV011 | Inverter 011 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_InverterGridConnectionStatus | INV011 | Inverter 011 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_InverterOverTemperature | INV011 | Inverter 011 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_InverterRunningStopped | INV011 | Inverter 011 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_InverterStartupShutdownStatus | INV011 | Inverter 011 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_InverterTripHistoryAvailable | INV011 | Inverter 011 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_IslandingDetectionStatus | INV011 | Inverter 011 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_LicenseExpired | INV011 | Inverter 011 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_LockingStatus | INV011 | Inverter 011 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_LowInsulationResistance | INV011 | Inverter 011 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_NormalGridConnection | INV011 | Inverter 011 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_NormalShutdown | INV011 | Inverter 011 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_OffGridOutputOverload | INV011 | Inverter 011 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_OptimizerFault | INV011 | Inverter 011 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_OutputDCComponentOverhigh | INV011 | Inverter 011 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_OutputOvercurrent | INV011 | Inverter 011 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_PVStringLoss | INV011 | Inverter 011 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_PassiveIslanding | INV011 | Inverter 011 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_PeripheralPortShortCircuit | INV011 | Inverter 011 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_PhaseWireShortCircuitedPE | INV011 | Inverter 011 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_PowerCurtailmentStatus | INV011 | Inverter 011 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_PowerFactor | INV011 | Inverter 011 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_PowerLimitationActiveGridCommand | INV011 | Inverter 011 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_ReactivePower | INV011 | Inverter 011 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV011_RemoteOFFStatus | INV011 | Inverter 011 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_Shutdown | INV011 | Inverter 011 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_ShutdownPowerRationing | INV011 | Inverter 011 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_SpotCheck | INV011 | Inverter 011 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_Standby | INV011 | Inverter 011 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_StringCurrentBackfeed | INV011 | Inverter 011 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_StringReverseConnection | INV011 | Inverter 011 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_StringReversePolarity | INV011 | Inverter 011 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_TotalEnergyYield | INV011 | Inverter 011 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV011_TransientACOvervoltage | INV011 | Inverter 011 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_UnstableGridFrequency | INV011 | Inverter 011 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_UpgradeFailed | INV011 | Inverter 011 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV011_WarningActive | INV011 | Inverter 011 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_ACCurrent | INV012 | Inverter 012 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_ACOvervoltage | INV012 | Inverter 012 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_ACUndervoltage | INV012 | Inverter 012 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_ACVoltage | INV012 | Inverter 012 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_AFCISelfCheckFailure | INV012 | Inverter 012 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_AbnormalGrounding | INV012 | Inverter 012 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_AbnormalPVModuleConfiguration | INV012 | Inverter 012 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_AbnormalResidualCurrent | INV012 | Inverter 012 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_AbnormalStringPower | INV012 | Inverter 012 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_ActiveIslanding | INV012 | Inverter 012 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_ActivePower | INV012 | Inverter 012 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_ApparentPower | INV012 | Inverter 012 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV012_BuiltPIDOperationAbnormal | INV012 | Inverter 012 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_CabinetOvertemperature | INV012 | Inverter 012 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_CommunicationFailure | INV012 | Inverter 012 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_CommunicationStatus | INV012 | Inverter 012 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_DCArcFault | INV012 | Inverter 012 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_DCCurrent | INV012 | Inverter 012 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_DCInsulationFault | INV012 | Inverter 012 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_DCOvervoltage | INV012 | Inverter 012 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_DCPower | INV012 | Inverter 012 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV012_DCVoltage | INV012 | Inverter 012 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_DailyEnergyYield | INV012 | Inverter 012 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV012_DeviceFault | INV012 | Inverter 012 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_ExternalFanAbnormal | INV012 | Inverter 012 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_FanFailure | INV012 | Inverter 012 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_Faulty | INV012 | Inverter 012 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_FaultyMonitoringUnit | INV012 | Inverter 012 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_FaultyPowerCollector | INV012 | Inverter 012 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_Frequency | INV012 | Inverter 012 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_GeneralFaultTrip | INV012 | Inverter 012 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_Grid | INV012 | Inverter 012 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GridConnectionDeratingInverterInternalCauses | INV012 | Inverter 012 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GridConnectionDeratingPowerRationing | INV012 | Inverter 012 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GridLoss | INV012 | Inverter 012 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GridOverfrequency | INV012 | Inverter 012 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GridOvervoltage | INV012 | Inverter 012 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GridTiedOffGridControllerAbnormal | INV012 | Inverter 012 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GridUnderfrequency | INV012 | Inverter 012 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GridUndervoltage | INV012 | Inverter 012 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GridVoltageImbalance | INV012 | Inverter 012 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_GroundFault | INV012 | Inverter 012 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_HighInputStringVoltageGround | INV012 | Inverter 012 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_HighStringInputVoltage | INV012 | Inverter 012 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_InverterEfficiency | INV012 | Inverter 012 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_InverterGridConnectionStatus | INV012 | Inverter 012 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_InverterOverTemperature | INV012 | Inverter 012 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_InverterRunningStopped | INV012 | Inverter 012 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_InverterStartupShutdownStatus | INV012 | Inverter 012 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_InverterTripHistoryAvailable | INV012 | Inverter 012 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_IslandingDetectionStatus | INV012 | Inverter 012 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_LicenseExpired | INV012 | Inverter 012 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_LockingStatus | INV012 | Inverter 012 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_LowInsulationResistance | INV012 | Inverter 012 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_NormalGridConnection | INV012 | Inverter 012 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_NormalShutdown | INV012 | Inverter 012 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_OffGridOutputOverload | INV012 | Inverter 012 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_OptimizerFault | INV012 | Inverter 012 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_OutputDCComponentOverhigh | INV012 | Inverter 012 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_OutputOvercurrent | INV012 | Inverter 012 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_PVStringLoss | INV012 | Inverter 012 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_PassiveIslanding | INV012 | Inverter 012 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_PeripheralPortShortCircuit | INV012 | Inverter 012 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_PhaseWireShortCircuitedPE | INV012 | Inverter 012 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_PowerCurtailmentStatus | INV012 | Inverter 012 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_PowerFactor | INV012 | Inverter 012 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_PowerLimitationActiveGridCommand | INV012 | Inverter 012 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_ReactivePower | INV012 | Inverter 012 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV012_RemoteOFFStatus | INV012 | Inverter 012 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_Shutdown | INV012 | Inverter 012 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_ShutdownPowerRationing | INV012 | Inverter 012 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_SpotCheck | INV012 | Inverter 012 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_Standby | INV012 | Inverter 012 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_StringCurrentBackfeed | INV012 | Inverter 012 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_StringReverseConnection | INV012 | Inverter 012 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_StringReversePolarity | INV012 | Inverter 012 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_TotalEnergyYield | INV012 | Inverter 012 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV012_TransientACOvervoltage | INV012 | Inverter 012 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_UnstableGridFrequency | INV012 | Inverter 012 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_UpgradeFailed | INV012 | Inverter 012 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV012_WarningActive | INV012 | Inverter 012 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_ACCurrent | INV013 | Inverter 013 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_ACOvervoltage | INV013 | Inverter 013 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_ACUndervoltage | INV013 | Inverter 013 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_ACVoltage | INV013 | Inverter 013 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_AFCISelfCheckFailure | INV013 | Inverter 013 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_AbnormalGrounding | INV013 | Inverter 013 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_AbnormalPVModuleConfiguration | INV013 | Inverter 013 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_AbnormalResidualCurrent | INV013 | Inverter 013 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_AbnormalStringPower | INV013 | Inverter 013 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_ActiveIslanding | INV013 | Inverter 013 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_ActivePower | INV013 | Inverter 013 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_ApparentPower | INV013 | Inverter 013 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV013_BuiltPIDOperationAbnormal | INV013 | Inverter 013 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_CabinetOvertemperature | INV013 | Inverter 013 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_CommunicationFailure | INV013 | Inverter 013 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_CommunicationStatus | INV013 | Inverter 013 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_DCArcFault | INV013 | Inverter 013 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_DCCurrent | INV013 | Inverter 013 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_DCInsulationFault | INV013 | Inverter 013 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_DCOvervoltage | INV013 | Inverter 013 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_DCPower | INV013 | Inverter 013 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV013_DCVoltage | INV013 | Inverter 013 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_DailyEnergyYield | INV013 | Inverter 013 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV013_DeviceFault | INV013 | Inverter 013 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_ExternalFanAbnormal | INV013 | Inverter 013 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_FanFailure | INV013 | Inverter 013 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_Faulty | INV013 | Inverter 013 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_FaultyMonitoringUnit | INV013 | Inverter 013 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_FaultyPowerCollector | INV013 | Inverter 013 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_Frequency | INV013 | Inverter 013 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_GeneralFaultTrip | INV013 | Inverter 013 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_Grid | INV013 | Inverter 013 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GridConnectionDeratingInverterInternalCauses | INV013 | Inverter 013 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GridConnectionDeratingPowerRationing | INV013 | Inverter 013 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GridLoss | INV013 | Inverter 013 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GridOverfrequency | INV013 | Inverter 013 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GridOvervoltage | INV013 | Inverter 013 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GridTiedOffGridControllerAbnormal | INV013 | Inverter 013 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GridUnderfrequency | INV013 | Inverter 013 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GridUndervoltage | INV013 | Inverter 013 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GridVoltageImbalance | INV013 | Inverter 013 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_GroundFault | INV013 | Inverter 013 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_HighInputStringVoltageGround | INV013 | Inverter 013 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_HighStringInputVoltage | INV013 | Inverter 013 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_InverterEfficiency | INV013 | Inverter 013 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_InverterGridConnectionStatus | INV013 | Inverter 013 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_InverterOverTemperature | INV013 | Inverter 013 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_InverterRunningStopped | INV013 | Inverter 013 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_InverterStartupShutdownStatus | INV013 | Inverter 013 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_InverterTripHistoryAvailable | INV013 | Inverter 013 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_IslandingDetectionStatus | INV013 | Inverter 013 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_LicenseExpired | INV013 | Inverter 013 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_LockingStatus | INV013 | Inverter 013 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_LowInsulationResistance | INV013 | Inverter 013 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_NormalGridConnection | INV013 | Inverter 013 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_NormalShutdown | INV013 | Inverter 013 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_OffGridOutputOverload | INV013 | Inverter 013 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_OptimizerFault | INV013 | Inverter 013 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_OutputDCComponentOverhigh | INV013 | Inverter 013 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_OutputOvercurrent | INV013 | Inverter 013 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_PVStringLoss | INV013 | Inverter 013 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_PassiveIslanding | INV013 | Inverter 013 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_PeripheralPortShortCircuit | INV013 | Inverter 013 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_PhaseWireShortCircuitedPE | INV013 | Inverter 013 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_PowerCurtailmentStatus | INV013 | Inverter 013 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_PowerFactor | INV013 | Inverter 013 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_PowerLimitationActiveGridCommand | INV013 | Inverter 013 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_ReactivePower | INV013 | Inverter 013 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV013_RemoteOFFStatus | INV013 | Inverter 013 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_Shutdown | INV013 | Inverter 013 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_ShutdownPowerRationing | INV013 | Inverter 013 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_SpotCheck | INV013 | Inverter 013 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_Standby | INV013 | Inverter 013 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_StringCurrentBackfeed | INV013 | Inverter 013 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_StringReverseConnection | INV013 | Inverter 013 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_StringReversePolarity | INV013 | Inverter 013 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_TotalEnergyYield | INV013 | Inverter 013 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV013_TransientACOvervoltage | INV013 | Inverter 013 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_UnstableGridFrequency | INV013 | Inverter 013 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_UpgradeFailed | INV013 | Inverter 013 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV013_WarningActive | INV013 | Inverter 013 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_ACCurrent | INV014 | Inverter 014 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_ACOvervoltage | INV014 | Inverter 014 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_ACUndervoltage | INV014 | Inverter 014 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_ACVoltage | INV014 | Inverter 014 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_AFCISelfCheckFailure | INV014 | Inverter 014 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_AbnormalGrounding | INV014 | Inverter 014 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_AbnormalPVModuleConfiguration | INV014 | Inverter 014 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_AbnormalResidualCurrent | INV014 | Inverter 014 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_AbnormalStringPower | INV014 | Inverter 014 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_ActiveIslanding | INV014 | Inverter 014 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_ActivePower | INV014 | Inverter 014 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_ApparentPower | INV014 | Inverter 014 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV014_BuiltPIDOperationAbnormal | INV014 | Inverter 014 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_CabinetOvertemperature | INV014 | Inverter 014 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_CommunicationFailure | INV014 | Inverter 014 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_CommunicationStatus | INV014 | Inverter 014 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_DCArcFault | INV014 | Inverter 014 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_DCCurrent | INV014 | Inverter 014 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_DCInsulationFault | INV014 | Inverter 014 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_DCOvervoltage | INV014 | Inverter 014 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_DCPower | INV014 | Inverter 014 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV014_DCVoltage | INV014 | Inverter 014 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_DailyEnergyYield | INV014 | Inverter 014 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV014_DeviceFault | INV014 | Inverter 014 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_ExternalFanAbnormal | INV014 | Inverter 014 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_FanFailure | INV014 | Inverter 014 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_Faulty | INV014 | Inverter 014 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_FaultyMonitoringUnit | INV014 | Inverter 014 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_FaultyPowerCollector | INV014 | Inverter 014 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_Frequency | INV014 | Inverter 014 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_GeneralFaultTrip | INV014 | Inverter 014 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_Grid | INV014 | Inverter 014 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GridConnectionDeratingInverterInternalCauses | INV014 | Inverter 014 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GridConnectionDeratingPowerRationing | INV014 | Inverter 014 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GridLoss | INV014 | Inverter 014 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GridOverfrequency | INV014 | Inverter 014 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GridOvervoltage | INV014 | Inverter 014 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GridTiedOffGridControllerAbnormal | INV014 | Inverter 014 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GridUnderfrequency | INV014 | Inverter 014 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GridUndervoltage | INV014 | Inverter 014 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GridVoltageImbalance | INV014 | Inverter 014 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_GroundFault | INV014 | Inverter 014 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_HighInputStringVoltageGround | INV014 | Inverter 014 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_HighStringInputVoltage | INV014 | Inverter 014 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_InverterEfficiency | INV014 | Inverter 014 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_InverterGridConnectionStatus | INV014 | Inverter 014 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_InverterOverTemperature | INV014 | Inverter 014 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_InverterRunningStopped | INV014 | Inverter 014 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_InverterStartupShutdownStatus | INV014 | Inverter 014 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_InverterTripHistoryAvailable | INV014 | Inverter 014 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_IslandingDetectionStatus | INV014 | Inverter 014 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_LicenseExpired | INV014 | Inverter 014 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_LockingStatus | INV014 | Inverter 014 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_LowInsulationResistance | INV014 | Inverter 014 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_NormalGridConnection | INV014 | Inverter 014 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_NormalShutdown | INV014 | Inverter 014 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_OffGridOutputOverload | INV014 | Inverter 014 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_OptimizerFault | INV014 | Inverter 014 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_OutputDCComponentOverhigh | INV014 | Inverter 014 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_OutputOvercurrent | INV014 | Inverter 014 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_PVStringLoss | INV014 | Inverter 014 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_PassiveIslanding | INV014 | Inverter 014 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_PeripheralPortShortCircuit | INV014 | Inverter 014 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_PhaseWireShortCircuitedPE | INV014 | Inverter 014 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_PowerCurtailmentStatus | INV014 | Inverter 014 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_PowerFactor | INV014 | Inverter 014 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_PowerLimitationActiveGridCommand | INV014 | Inverter 014 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_ReactivePower | INV014 | Inverter 014 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV014_RemoteOFFStatus | INV014 | Inverter 014 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_Shutdown | INV014 | Inverter 014 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_ShutdownPowerRationing | INV014 | Inverter 014 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_SpotCheck | INV014 | Inverter 014 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_Standby | INV014 | Inverter 014 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_StringCurrentBackfeed | INV014 | Inverter 014 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_StringReverseConnection | INV014 | Inverter 014 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_StringReversePolarity | INV014 | Inverter 014 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_TotalEnergyYield | INV014 | Inverter 014 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV014_TransientACOvervoltage | INV014 | Inverter 014 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_UnstableGridFrequency | INV014 | Inverter 014 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_UpgradeFailed | INV014 | Inverter 014 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV014_WarningActive | INV014 | Inverter 014 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_ACCurrent | INV015 | Inverter 015 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_ACOvervoltage | INV015 | Inverter 015 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_ACUndervoltage | INV015 | Inverter 015 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_ACVoltage | INV015 | Inverter 015 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_AFCISelfCheckFailure | INV015 | Inverter 015 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_AbnormalGrounding | INV015 | Inverter 015 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_AbnormalPVModuleConfiguration | INV015 | Inverter 015 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_AbnormalResidualCurrent | INV015 | Inverter 015 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_AbnormalStringPower | INV015 | Inverter 015 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_ActiveIslanding | INV015 | Inverter 015 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_ActivePower | INV015 | Inverter 015 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_ApparentPower | INV015 | Inverter 015 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV015_BuiltPIDOperationAbnormal | INV015 | Inverter 015 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_CabinetOvertemperature | INV015 | Inverter 015 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_CommunicationFailure | INV015 | Inverter 015 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_CommunicationStatus | INV015 | Inverter 015 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_DCArcFault | INV015 | Inverter 015 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_DCCurrent | INV015 | Inverter 015 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_DCInsulationFault | INV015 | Inverter 015 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_DCOvervoltage | INV015 | Inverter 015 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_DCPower | INV015 | Inverter 015 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV015_DCVoltage | INV015 | Inverter 015 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_DailyEnergyYield | INV015 | Inverter 015 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV015_DeviceFault | INV015 | Inverter 015 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_ExternalFanAbnormal | INV015 | Inverter 015 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_FanFailure | INV015 | Inverter 015 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_Faulty | INV015 | Inverter 015 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_FaultyMonitoringUnit | INV015 | Inverter 015 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_FaultyPowerCollector | INV015 | Inverter 015 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_Frequency | INV015 | Inverter 015 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_GeneralFaultTrip | INV015 | Inverter 015 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_Grid | INV015 | Inverter 015 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GridConnectionDeratingInverterInternalCauses | INV015 | Inverter 015 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GridConnectionDeratingPowerRationing | INV015 | Inverter 015 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GridLoss | INV015 | Inverter 015 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GridOverfrequency | INV015 | Inverter 015 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GridOvervoltage | INV015 | Inverter 015 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GridTiedOffGridControllerAbnormal | INV015 | Inverter 015 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GridUnderfrequency | INV015 | Inverter 015 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GridUndervoltage | INV015 | Inverter 015 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GridVoltageImbalance | INV015 | Inverter 015 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_GroundFault | INV015 | Inverter 015 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_HighInputStringVoltageGround | INV015 | Inverter 015 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_HighStringInputVoltage | INV015 | Inverter 015 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_InverterEfficiency | INV015 | Inverter 015 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_InverterGridConnectionStatus | INV015 | Inverter 015 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_InverterOverTemperature | INV015 | Inverter 015 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_InverterRunningStopped | INV015 | Inverter 015 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_InverterStartupShutdownStatus | INV015 | Inverter 015 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_InverterTripHistoryAvailable | INV015 | Inverter 015 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_IslandingDetectionStatus | INV015 | Inverter 015 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_LicenseExpired | INV015 | Inverter 015 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_LockingStatus | INV015 | Inverter 015 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_LowInsulationResistance | INV015 | Inverter 015 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_NormalGridConnection | INV015 | Inverter 015 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_NormalShutdown | INV015 | Inverter 015 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_OffGridOutputOverload | INV015 | Inverter 015 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_OptimizerFault | INV015 | Inverter 015 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_OutputDCComponentOverhigh | INV015 | Inverter 015 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_OutputOvercurrent | INV015 | Inverter 015 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_PVStringLoss | INV015 | Inverter 015 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_PassiveIslanding | INV015 | Inverter 015 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_PeripheralPortShortCircuit | INV015 | Inverter 015 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_PhaseWireShortCircuitedPE | INV015 | Inverter 015 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_PowerCurtailmentStatus | INV015 | Inverter 015 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_PowerFactor | INV015 | Inverter 015 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_PowerLimitationActiveGridCommand | INV015 | Inverter 015 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_ReactivePower | INV015 | Inverter 015 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV015_RemoteOFFStatus | INV015 | Inverter 015 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_Shutdown | INV015 | Inverter 015 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_ShutdownPowerRationing | INV015 | Inverter 015 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_SpotCheck | INV015 | Inverter 015 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_Standby | INV015 | Inverter 015 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_StringCurrentBackfeed | INV015 | Inverter 015 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_StringReverseConnection | INV015 | Inverter 015 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_StringReversePolarity | INV015 | Inverter 015 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_TotalEnergyYield | INV015 | Inverter 015 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV015_TransientACOvervoltage | INV015 | Inverter 015 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_UnstableGridFrequency | INV015 | Inverter 015 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_UpgradeFailed | INV015 | Inverter 015 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV015_WarningActive | INV015 | Inverter 015 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_ACCurrent | INV016 | Inverter 016 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_ACOvervoltage | INV016 | Inverter 016 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_ACUndervoltage | INV016 | Inverter 016 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_ACVoltage | INV016 | Inverter 016 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_AFCISelfCheckFailure | INV016 | Inverter 016 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_AbnormalGrounding | INV016 | Inverter 016 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_AbnormalPVModuleConfiguration | INV016 | Inverter 016 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_AbnormalResidualCurrent | INV016 | Inverter 016 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_AbnormalStringPower | INV016 | Inverter 016 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_ActiveIslanding | INV016 | Inverter 016 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_ActivePower | INV016 | Inverter 016 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_ApparentPower | INV016 | Inverter 016 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV016_BuiltPIDOperationAbnormal | INV016 | Inverter 016 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_CabinetOvertemperature | INV016 | Inverter 016 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_CommunicationFailure | INV016 | Inverter 016 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_CommunicationStatus | INV016 | Inverter 016 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_DCArcFault | INV016 | Inverter 016 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_DCCurrent | INV016 | Inverter 016 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_DCInsulationFault | INV016 | Inverter 016 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_DCOvervoltage | INV016 | Inverter 016 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_DCPower | INV016 | Inverter 016 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV016_DCVoltage | INV016 | Inverter 016 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_DailyEnergyYield | INV016 | Inverter 016 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV016_DeviceFault | INV016 | Inverter 016 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_ExternalFanAbnormal | INV016 | Inverter 016 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_FanFailure | INV016 | Inverter 016 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_Faulty | INV016 | Inverter 016 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_FaultyMonitoringUnit | INV016 | Inverter 016 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_FaultyPowerCollector | INV016 | Inverter 016 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_Frequency | INV016 | Inverter 016 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_GeneralFaultTrip | INV016 | Inverter 016 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_Grid | INV016 | Inverter 016 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GridConnectionDeratingInverterInternalCauses | INV016 | Inverter 016 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GridConnectionDeratingPowerRationing | INV016 | Inverter 016 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GridLoss | INV016 | Inverter 016 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GridOverfrequency | INV016 | Inverter 016 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GridOvervoltage | INV016 | Inverter 016 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GridTiedOffGridControllerAbnormal | INV016 | Inverter 016 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GridUnderfrequency | INV016 | Inverter 016 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GridUndervoltage | INV016 | Inverter 016 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GridVoltageImbalance | INV016 | Inverter 016 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_GroundFault | INV016 | Inverter 016 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_HighInputStringVoltageGround | INV016 | Inverter 016 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_HighStringInputVoltage | INV016 | Inverter 016 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_InverterEfficiency | INV016 | Inverter 016 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_InverterGridConnectionStatus | INV016 | Inverter 016 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_InverterOverTemperature | INV016 | Inverter 016 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_InverterRunningStopped | INV016 | Inverter 016 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_InverterStartupShutdownStatus | INV016 | Inverter 016 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_InverterTripHistoryAvailable | INV016 | Inverter 016 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_IslandingDetectionStatus | INV016 | Inverter 016 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_LicenseExpired | INV016 | Inverter 016 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_LockingStatus | INV016 | Inverter 016 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_LowInsulationResistance | INV016 | Inverter 016 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_NormalGridConnection | INV016 | Inverter 016 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_NormalShutdown | INV016 | Inverter 016 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_OffGridOutputOverload | INV016 | Inverter 016 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_OptimizerFault | INV016 | Inverter 016 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_OutputDCComponentOverhigh | INV016 | Inverter 016 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_OutputOvercurrent | INV016 | Inverter 016 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_PVStringLoss | INV016 | Inverter 016 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_PassiveIslanding | INV016 | Inverter 016 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_PeripheralPortShortCircuit | INV016 | Inverter 016 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_PhaseWireShortCircuitedPE | INV016 | Inverter 016 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_PowerCurtailmentStatus | INV016 | Inverter 016 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_PowerFactor | INV016 | Inverter 016 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_PowerLimitationActiveGridCommand | INV016 | Inverter 016 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_ReactivePower | INV016 | Inverter 016 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV016_RemoteOFFStatus | INV016 | Inverter 016 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_Shutdown | INV016 | Inverter 016 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_ShutdownPowerRationing | INV016 | Inverter 016 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_SpotCheck | INV016 | Inverter 016 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_Standby | INV016 | Inverter 016 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_StringCurrentBackfeed | INV016 | Inverter 016 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_StringReverseConnection | INV016 | Inverter 016 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_StringReversePolarity | INV016 | Inverter 016 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_TotalEnergyYield | INV016 | Inverter 016 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV016_TransientACOvervoltage | INV016 | Inverter 016 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_UnstableGridFrequency | INV016 | Inverter 016 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_UpgradeFailed | INV016 | Inverter 016 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV016_WarningActive | INV016 | Inverter 016 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_ACCurrent | INV017 | Inverter 017 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_ACOvervoltage | INV017 | Inverter 017 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_ACUndervoltage | INV017 | Inverter 017 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_ACVoltage | INV017 | Inverter 017 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_AFCISelfCheckFailure | INV017 | Inverter 017 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_AbnormalGrounding | INV017 | Inverter 017 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_AbnormalPVModuleConfiguration | INV017 | Inverter 017 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_AbnormalResidualCurrent | INV017 | Inverter 017 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_AbnormalStringPower | INV017 | Inverter 017 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_ActiveIslanding | INV017 | Inverter 017 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_ActivePower | INV017 | Inverter 017 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_ApparentPower | INV017 | Inverter 017 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV017_BuiltPIDOperationAbnormal | INV017 | Inverter 017 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_CabinetOvertemperature | INV017 | Inverter 017 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_CommunicationFailure | INV017 | Inverter 017 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_CommunicationStatus | INV017 | Inverter 017 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_DCArcFault | INV017 | Inverter 017 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_DCCurrent | INV017 | Inverter 017 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_DCInsulationFault | INV017 | Inverter 017 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_DCOvervoltage | INV017 | Inverter 017 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_DCPower | INV017 | Inverter 017 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV017_DCVoltage | INV017 | Inverter 017 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_DailyEnergyYield | INV017 | Inverter 017 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV017_DeviceFault | INV017 | Inverter 017 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_ExternalFanAbnormal | INV017 | Inverter 017 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_FanFailure | INV017 | Inverter 017 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_Faulty | INV017 | Inverter 017 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_FaultyMonitoringUnit | INV017 | Inverter 017 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_FaultyPowerCollector | INV017 | Inverter 017 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_Frequency | INV017 | Inverter 017 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_GeneralFaultTrip | INV017 | Inverter 017 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_Grid | INV017 | Inverter 017 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GridConnectionDeratingInverterInternalCauses | INV017 | Inverter 017 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GridConnectionDeratingPowerRationing | INV017 | Inverter 017 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GridLoss | INV017 | Inverter 017 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GridOverfrequency | INV017 | Inverter 017 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GridOvervoltage | INV017 | Inverter 017 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GridTiedOffGridControllerAbnormal | INV017 | Inverter 017 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GridUnderfrequency | INV017 | Inverter 017 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GridUndervoltage | INV017 | Inverter 017 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GridVoltageImbalance | INV017 | Inverter 017 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_GroundFault | INV017 | Inverter 017 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_HighInputStringVoltageGround | INV017 | Inverter 017 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_HighStringInputVoltage | INV017 | Inverter 017 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_InverterEfficiency | INV017 | Inverter 017 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_InverterGridConnectionStatus | INV017 | Inverter 017 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_InverterOverTemperature | INV017 | Inverter 017 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_InverterRunningStopped | INV017 | Inverter 017 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_InverterStartupShutdownStatus | INV017 | Inverter 017 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_InverterTripHistoryAvailable | INV017 | Inverter 017 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_IslandingDetectionStatus | INV017 | Inverter 017 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_LicenseExpired | INV017 | Inverter 017 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_LockingStatus | INV017 | Inverter 017 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_LowInsulationResistance | INV017 | Inverter 017 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_NormalGridConnection | INV017 | Inverter 017 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_NormalShutdown | INV017 | Inverter 017 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_OffGridOutputOverload | INV017 | Inverter 017 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_OptimizerFault | INV017 | Inverter 017 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_OutputDCComponentOverhigh | INV017 | Inverter 017 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_OutputOvercurrent | INV017 | Inverter 017 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_PVStringLoss | INV017 | Inverter 017 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_PassiveIslanding | INV017 | Inverter 017 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_PeripheralPortShortCircuit | INV017 | Inverter 017 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_PhaseWireShortCircuitedPE | INV017 | Inverter 017 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_PowerCurtailmentStatus | INV017 | Inverter 017 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_PowerFactor | INV017 | Inverter 017 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_PowerLimitationActiveGridCommand | INV017 | Inverter 017 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_ReactivePower | INV017 | Inverter 017 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV017_RemoteOFFStatus | INV017 | Inverter 017 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_Shutdown | INV017 | Inverter 017 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_ShutdownPowerRationing | INV017 | Inverter 017 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_SpotCheck | INV017 | Inverter 017 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_Standby | INV017 | Inverter 017 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_StringCurrentBackfeed | INV017 | Inverter 017 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_StringReverseConnection | INV017 | Inverter 017 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_StringReversePolarity | INV017 | Inverter 017 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_TotalEnergyYield | INV017 | Inverter 017 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV017_TransientACOvervoltage | INV017 | Inverter 017 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_UnstableGridFrequency | INV017 | Inverter 017 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_UpgradeFailed | INV017 | Inverter 017 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV017_WarningActive | INV017 | Inverter 017 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_ACCurrent | INV018 | Inverter 018 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_ACOvervoltage | INV018 | Inverter 018 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_ACUndervoltage | INV018 | Inverter 018 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_ACVoltage | INV018 | Inverter 018 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_AFCISelfCheckFailure | INV018 | Inverter 018 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_AbnormalGrounding | INV018 | Inverter 018 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_AbnormalPVModuleConfiguration | INV018 | Inverter 018 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_AbnormalResidualCurrent | INV018 | Inverter 018 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_AbnormalStringPower | INV018 | Inverter 018 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_ActiveIslanding | INV018 | Inverter 018 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_ActivePower | INV018 | Inverter 018 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_ApparentPower | INV018 | Inverter 018 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV018_BuiltPIDOperationAbnormal | INV018 | Inverter 018 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_CabinetOvertemperature | INV018 | Inverter 018 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_CommunicationFailure | INV018 | Inverter 018 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_CommunicationStatus | INV018 | Inverter 018 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_DCArcFault | INV018 | Inverter 018 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_DCCurrent | INV018 | Inverter 018 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_DCInsulationFault | INV018 | Inverter 018 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_DCOvervoltage | INV018 | Inverter 018 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_DCPower | INV018 | Inverter 018 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV018_DCVoltage | INV018 | Inverter 018 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_DailyEnergyYield | INV018 | Inverter 018 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV018_DeviceFault | INV018 | Inverter 018 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_ExternalFanAbnormal | INV018 | Inverter 018 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_FanFailure | INV018 | Inverter 018 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_Faulty | INV018 | Inverter 018 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_FaultyMonitoringUnit | INV018 | Inverter 018 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_FaultyPowerCollector | INV018 | Inverter 018 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_Frequency | INV018 | Inverter 018 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_GeneralFaultTrip | INV018 | Inverter 018 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_Grid | INV018 | Inverter 018 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GridConnectionDeratingInverterInternalCauses | INV018 | Inverter 018 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GridConnectionDeratingPowerRationing | INV018 | Inverter 018 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GridLoss | INV018 | Inverter 018 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GridOverfrequency | INV018 | Inverter 018 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GridOvervoltage | INV018 | Inverter 018 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GridTiedOffGridControllerAbnormal | INV018 | Inverter 018 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GridUnderfrequency | INV018 | Inverter 018 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GridUndervoltage | INV018 | Inverter 018 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GridVoltageImbalance | INV018 | Inverter 018 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_GroundFault | INV018 | Inverter 018 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_HighInputStringVoltageGround | INV018 | Inverter 018 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_HighStringInputVoltage | INV018 | Inverter 018 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_InverterEfficiency | INV018 | Inverter 018 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_InverterGridConnectionStatus | INV018 | Inverter 018 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_InverterOverTemperature | INV018 | Inverter 018 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_InverterRunningStopped | INV018 | Inverter 018 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_InverterStartupShutdownStatus | INV018 | Inverter 018 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_InverterTripHistoryAvailable | INV018 | Inverter 018 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_IslandingDetectionStatus | INV018 | Inverter 018 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_LicenseExpired | INV018 | Inverter 018 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_LockingStatus | INV018 | Inverter 018 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_LowInsulationResistance | INV018 | Inverter 018 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_NormalGridConnection | INV018 | Inverter 018 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_NormalShutdown | INV018 | Inverter 018 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_OffGridOutputOverload | INV018 | Inverter 018 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_OptimizerFault | INV018 | Inverter 018 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_OutputDCComponentOverhigh | INV018 | Inverter 018 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_OutputOvercurrent | INV018 | Inverter 018 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_PVStringLoss | INV018 | Inverter 018 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_PassiveIslanding | INV018 | Inverter 018 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_PeripheralPortShortCircuit | INV018 | Inverter 018 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_PhaseWireShortCircuitedPE | INV018 | Inverter 018 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_PowerCurtailmentStatus | INV018 | Inverter 018 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_PowerFactor | INV018 | Inverter 018 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_PowerLimitationActiveGridCommand | INV018 | Inverter 018 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_ReactivePower | INV018 | Inverter 018 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV018_RemoteOFFStatus | INV018 | Inverter 018 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_Shutdown | INV018 | Inverter 018 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_ShutdownPowerRationing | INV018 | Inverter 018 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_SpotCheck | INV018 | Inverter 018 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_Standby | INV018 | Inverter 018 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_StringCurrentBackfeed | INV018 | Inverter 018 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_StringReverseConnection | INV018 | Inverter 018 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_StringReversePolarity | INV018 | Inverter 018 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_TotalEnergyYield | INV018 | Inverter 018 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV018_TransientACOvervoltage | INV018 | Inverter 018 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_UnstableGridFrequency | INV018 | Inverter 018 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_UpgradeFailed | INV018 | Inverter 018 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV018_WarningActive | INV018 | Inverter 018 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_ACCurrent | INV019 | Inverter 019 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_ACOvervoltage | INV019 | Inverter 019 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_ACUndervoltage | INV019 | Inverter 019 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_ACVoltage | INV019 | Inverter 019 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_AFCISelfCheckFailure | INV019 | Inverter 019 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_AbnormalGrounding | INV019 | Inverter 019 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_AbnormalPVModuleConfiguration | INV019 | Inverter 019 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_AbnormalResidualCurrent | INV019 | Inverter 019 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_AbnormalStringPower | INV019 | Inverter 019 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_ActiveIslanding | INV019 | Inverter 019 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_ActivePower | INV019 | Inverter 019 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_ApparentPower | INV019 | Inverter 019 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV019_BuiltPIDOperationAbnormal | INV019 | Inverter 019 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_CabinetOvertemperature | INV019 | Inverter 019 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_CommunicationFailure | INV019 | Inverter 019 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_CommunicationStatus | INV019 | Inverter 019 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_DCArcFault | INV019 | Inverter 019 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_DCCurrent | INV019 | Inverter 019 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_DCInsulationFault | INV019 | Inverter 019 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_DCOvervoltage | INV019 | Inverter 019 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_DCPower | INV019 | Inverter 019 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV019_DCVoltage | INV019 | Inverter 019 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_DailyEnergyYield | INV019 | Inverter 019 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV019_DeviceFault | INV019 | Inverter 019 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_ExternalFanAbnormal | INV019 | Inverter 019 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_FanFailure | INV019 | Inverter 019 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_Faulty | INV019 | Inverter 019 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_FaultyMonitoringUnit | INV019 | Inverter 019 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_FaultyPowerCollector | INV019 | Inverter 019 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_Frequency | INV019 | Inverter 019 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_GeneralFaultTrip | INV019 | Inverter 019 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_Grid | INV019 | Inverter 019 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GridConnectionDeratingInverterInternalCauses | INV019 | Inverter 019 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GridConnectionDeratingPowerRationing | INV019 | Inverter 019 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GridLoss | INV019 | Inverter 019 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GridOverfrequency | INV019 | Inverter 019 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GridOvervoltage | INV019 | Inverter 019 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GridTiedOffGridControllerAbnormal | INV019 | Inverter 019 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GridUnderfrequency | INV019 | Inverter 019 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GridUndervoltage | INV019 | Inverter 019 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GridVoltageImbalance | INV019 | Inverter 019 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_GroundFault | INV019 | Inverter 019 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_HighInputStringVoltageGround | INV019 | Inverter 019 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_HighStringInputVoltage | INV019 | Inverter 019 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_InverterEfficiency | INV019 | Inverter 019 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_InverterGridConnectionStatus | INV019 | Inverter 019 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_InverterOverTemperature | INV019 | Inverter 019 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_InverterRunningStopped | INV019 | Inverter 019 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_InverterStartupShutdownStatus | INV019 | Inverter 019 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_InverterTripHistoryAvailable | INV019 | Inverter 019 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_IslandingDetectionStatus | INV019 | Inverter 019 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_LicenseExpired | INV019 | Inverter 019 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_LockingStatus | INV019 | Inverter 019 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_LowInsulationResistance | INV019 | Inverter 019 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_NormalGridConnection | INV019 | Inverter 019 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_NormalShutdown | INV019 | Inverter 019 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_OffGridOutputOverload | INV019 | Inverter 019 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_OptimizerFault | INV019 | Inverter 019 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_OutputDCComponentOverhigh | INV019 | Inverter 019 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_OutputOvercurrent | INV019 | Inverter 019 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_PVStringLoss | INV019 | Inverter 019 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_PassiveIslanding | INV019 | Inverter 019 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_PeripheralPortShortCircuit | INV019 | Inverter 019 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_PhaseWireShortCircuitedPE | INV019 | Inverter 019 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_PowerCurtailmentStatus | INV019 | Inverter 019 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_PowerFactor | INV019 | Inverter 019 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_PowerLimitationActiveGridCommand | INV019 | Inverter 019 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_ReactivePower | INV019 | Inverter 019 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV019_RemoteOFFStatus | INV019 | Inverter 019 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_Shutdown | INV019 | Inverter 019 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_ShutdownPowerRationing | INV019 | Inverter 019 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_SpotCheck | INV019 | Inverter 019 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_Standby | INV019 | Inverter 019 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_StringCurrentBackfeed | INV019 | Inverter 019 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_StringReverseConnection | INV019 | Inverter 019 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_StringReversePolarity | INV019 | Inverter 019 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_TotalEnergyYield | INV019 | Inverter 019 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV019_TransientACOvervoltage | INV019 | Inverter 019 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_UnstableGridFrequency | INV019 | Inverter 019 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_UpgradeFailed | INV019 | Inverter 019 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV019_WarningActive | INV019 | Inverter 019 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_ACCurrent | INV020 | Inverter 020 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_ACOvervoltage | INV020 | Inverter 020 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_ACUndervoltage | INV020 | Inverter 020 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_ACVoltage | INV020 | Inverter 020 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_AFCISelfCheckFailure | INV020 | Inverter 020 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_AbnormalGrounding | INV020 | Inverter 020 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_AbnormalPVModuleConfiguration | INV020 | Inverter 020 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_AbnormalResidualCurrent | INV020 | Inverter 020 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_AbnormalStringPower | INV020 | Inverter 020 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_ActiveIslanding | INV020 | Inverter 020 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_ActivePower | INV020 | Inverter 020 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_ApparentPower | INV020 | Inverter 020 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV020_BuiltPIDOperationAbnormal | INV020 | Inverter 020 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_CabinetOvertemperature | INV020 | Inverter 020 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_CommunicationFailure | INV020 | Inverter 020 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_CommunicationStatus | INV020 | Inverter 020 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_DCArcFault | INV020 | Inverter 020 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_DCCurrent | INV020 | Inverter 020 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_DCInsulationFault | INV020 | Inverter 020 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_DCOvervoltage | INV020 | Inverter 020 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_DCPower | INV020 | Inverter 020 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV020_DCVoltage | INV020 | Inverter 020 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_DailyEnergyYield | INV020 | Inverter 020 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV020_DeviceFault | INV020 | Inverter 020 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_ExternalFanAbnormal | INV020 | Inverter 020 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_FanFailure | INV020 | Inverter 020 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_Faulty | INV020 | Inverter 020 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_FaultyMonitoringUnit | INV020 | Inverter 020 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_FaultyPowerCollector | INV020 | Inverter 020 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_Frequency | INV020 | Inverter 020 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_GeneralFaultTrip | INV020 | Inverter 020 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_Grid | INV020 | Inverter 020 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GridConnectionDeratingInverterInternalCauses | INV020 | Inverter 020 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GridConnectionDeratingPowerRationing | INV020 | Inverter 020 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GridLoss | INV020 | Inverter 020 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GridOverfrequency | INV020 | Inverter 020 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GridOvervoltage | INV020 | Inverter 020 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GridTiedOffGridControllerAbnormal | INV020 | Inverter 020 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GridUnderfrequency | INV020 | Inverter 020 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GridUndervoltage | INV020 | Inverter 020 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GridVoltageImbalance | INV020 | Inverter 020 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_GroundFault | INV020 | Inverter 020 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_HighInputStringVoltageGround | INV020 | Inverter 020 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_HighStringInputVoltage | INV020 | Inverter 020 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_InverterEfficiency | INV020 | Inverter 020 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_InverterGridConnectionStatus | INV020 | Inverter 020 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_InverterOverTemperature | INV020 | Inverter 020 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_InverterRunningStopped | INV020 | Inverter 020 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_InverterStartupShutdownStatus | INV020 | Inverter 020 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_InverterTripHistoryAvailable | INV020 | Inverter 020 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_IslandingDetectionStatus | INV020 | Inverter 020 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_LicenseExpired | INV020 | Inverter 020 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_LockingStatus | INV020 | Inverter 020 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_LowInsulationResistance | INV020 | Inverter 020 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_NormalGridConnection | INV020 | Inverter 020 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_NormalShutdown | INV020 | Inverter 020 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_OffGridOutputOverload | INV020 | Inverter 020 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_OptimizerFault | INV020 | Inverter 020 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_OutputDCComponentOverhigh | INV020 | Inverter 020 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_OutputOvercurrent | INV020 | Inverter 020 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_PVStringLoss | INV020 | Inverter 020 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_PassiveIslanding | INV020 | Inverter 020 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_PeripheralPortShortCircuit | INV020 | Inverter 020 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_PhaseWireShortCircuitedPE | INV020 | Inverter 020 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_PowerCurtailmentStatus | INV020 | Inverter 020 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_PowerFactor | INV020 | Inverter 020 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_PowerLimitationActiveGridCommand | INV020 | Inverter 020 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_ReactivePower | INV020 | Inverter 020 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV020_RemoteOFFStatus | INV020 | Inverter 020 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_Shutdown | INV020 | Inverter 020 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_ShutdownPowerRationing | INV020 | Inverter 020 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_SpotCheck | INV020 | Inverter 020 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_Standby | INV020 | Inverter 020 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_StringCurrentBackfeed | INV020 | Inverter 020 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_StringReverseConnection | INV020 | Inverter 020 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_StringReversePolarity | INV020 | Inverter 020 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_TotalEnergyYield | INV020 | Inverter 020 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV020_TransientACOvervoltage | INV020 | Inverter 020 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_UnstableGridFrequency | INV020 | Inverter 020 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_UpgradeFailed | INV020 | Inverter 020 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV020_WarningActive | INV020 | Inverter 020 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_ACCurrent | INV021 | Inverter 021 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_ACOvervoltage | INV021 | Inverter 021 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_ACUndervoltage | INV021 | Inverter 021 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_ACVoltage | INV021 | Inverter 021 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_AFCISelfCheckFailure | INV021 | Inverter 021 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_AbnormalGrounding | INV021 | Inverter 021 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_AbnormalPVModuleConfiguration | INV021 | Inverter 021 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_AbnormalResidualCurrent | INV021 | Inverter 021 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_AbnormalStringPower | INV021 | Inverter 021 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_ActiveIslanding | INV021 | Inverter 021 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_ActivePower | INV021 | Inverter 021 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_ApparentPower | INV021 | Inverter 021 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV021_BuiltPIDOperationAbnormal | INV021 | Inverter 021 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_CabinetOvertemperature | INV021 | Inverter 021 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_CommunicationFailure | INV021 | Inverter 021 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_CommunicationStatus | INV021 | Inverter 021 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_DCArcFault | INV021 | Inverter 021 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_DCCurrent | INV021 | Inverter 021 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_DCInsulationFault | INV021 | Inverter 021 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_DCOvervoltage | INV021 | Inverter 021 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_DCPower | INV021 | Inverter 021 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV021_DCVoltage | INV021 | Inverter 021 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_DailyEnergyYield | INV021 | Inverter 021 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV021_DeviceFault | INV021 | Inverter 021 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_ExternalFanAbnormal | INV021 | Inverter 021 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_FanFailure | INV021 | Inverter 021 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_Faulty | INV021 | Inverter 021 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_FaultyMonitoringUnit | INV021 | Inverter 021 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_FaultyPowerCollector | INV021 | Inverter 021 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_Frequency | INV021 | Inverter 021 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_GeneralFaultTrip | INV021 | Inverter 021 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_Grid | INV021 | Inverter 021 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GridConnectionDeratingInverterInternalCauses | INV021 | Inverter 021 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GridConnectionDeratingPowerRationing | INV021 | Inverter 021 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GridLoss | INV021 | Inverter 021 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GridOverfrequency | INV021 | Inverter 021 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GridOvervoltage | INV021 | Inverter 021 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GridTiedOffGridControllerAbnormal | INV021 | Inverter 021 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GridUnderfrequency | INV021 | Inverter 021 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GridUndervoltage | INV021 | Inverter 021 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GridVoltageImbalance | INV021 | Inverter 021 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_GroundFault | INV021 | Inverter 021 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_HighInputStringVoltageGround | INV021 | Inverter 021 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_HighStringInputVoltage | INV021 | Inverter 021 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_InverterEfficiency | INV021 | Inverter 021 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_InverterGridConnectionStatus | INV021 | Inverter 021 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_InverterOverTemperature | INV021 | Inverter 021 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_InverterRunningStopped | INV021 | Inverter 021 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_InverterStartupShutdownStatus | INV021 | Inverter 021 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_InverterTripHistoryAvailable | INV021 | Inverter 021 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_IslandingDetectionStatus | INV021 | Inverter 021 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_LicenseExpired | INV021 | Inverter 021 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_LockingStatus | INV021 | Inverter 021 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_LowInsulationResistance | INV021 | Inverter 021 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_NormalGridConnection | INV021 | Inverter 021 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_NormalShutdown | INV021 | Inverter 021 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_OffGridOutputOverload | INV021 | Inverter 021 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_OptimizerFault | INV021 | Inverter 021 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_OutputDCComponentOverhigh | INV021 | Inverter 021 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_OutputOvercurrent | INV021 | Inverter 021 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_PVStringLoss | INV021 | Inverter 021 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_PassiveIslanding | INV021 | Inverter 021 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_PeripheralPortShortCircuit | INV021 | Inverter 021 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_PhaseWireShortCircuitedPE | INV021 | Inverter 021 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_PowerCurtailmentStatus | INV021 | Inverter 021 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_PowerFactor | INV021 | Inverter 021 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_PowerLimitationActiveGridCommand | INV021 | Inverter 021 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_ReactivePower | INV021 | Inverter 021 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV021_RemoteOFFStatus | INV021 | Inverter 021 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_Shutdown | INV021 | Inverter 021 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_ShutdownPowerRationing | INV021 | Inverter 021 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_SpotCheck | INV021 | Inverter 021 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_Standby | INV021 | Inverter 021 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_StringCurrentBackfeed | INV021 | Inverter 021 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_StringReverseConnection | INV021 | Inverter 021 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_StringReversePolarity | INV021 | Inverter 021 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_TotalEnergyYield | INV021 | Inverter 021 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV021_TransientACOvervoltage | INV021 | Inverter 021 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_UnstableGridFrequency | INV021 | Inverter 021 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_UpgradeFailed | INV021 | Inverter 021 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV021_WarningActive | INV021 | Inverter 021 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_ACCurrent | INV022 | Inverter 022 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_ACOvervoltage | INV022 | Inverter 022 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_ACUndervoltage | INV022 | Inverter 022 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_ACVoltage | INV022 | Inverter 022 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_AFCISelfCheckFailure | INV022 | Inverter 022 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_AbnormalGrounding | INV022 | Inverter 022 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_AbnormalPVModuleConfiguration | INV022 | Inverter 022 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_AbnormalResidualCurrent | INV022 | Inverter 022 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_AbnormalStringPower | INV022 | Inverter 022 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_ActiveIslanding | INV022 | Inverter 022 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_ActivePower | INV022 | Inverter 022 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_ApparentPower | INV022 | Inverter 022 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV022_BuiltPIDOperationAbnormal | INV022 | Inverter 022 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_CabinetOvertemperature | INV022 | Inverter 022 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_CommunicationFailure | INV022 | Inverter 022 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_CommunicationStatus | INV022 | Inverter 022 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_DCArcFault | INV022 | Inverter 022 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_DCCurrent | INV022 | Inverter 022 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_DCInsulationFault | INV022 | Inverter 022 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_DCOvervoltage | INV022 | Inverter 022 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_DCPower | INV022 | Inverter 022 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV022_DCVoltage | INV022 | Inverter 022 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_DailyEnergyYield | INV022 | Inverter 022 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV022_DeviceFault | INV022 | Inverter 022 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_ExternalFanAbnormal | INV022 | Inverter 022 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_FanFailure | INV022 | Inverter 022 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_Faulty | INV022 | Inverter 022 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_FaultyMonitoringUnit | INV022 | Inverter 022 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_FaultyPowerCollector | INV022 | Inverter 022 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_Frequency | INV022 | Inverter 022 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_GeneralFaultTrip | INV022 | Inverter 022 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_Grid | INV022 | Inverter 022 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GridConnectionDeratingInverterInternalCauses | INV022 | Inverter 022 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GridConnectionDeratingPowerRationing | INV022 | Inverter 022 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GridLoss | INV022 | Inverter 022 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GridOverfrequency | INV022 | Inverter 022 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GridOvervoltage | INV022 | Inverter 022 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GridTiedOffGridControllerAbnormal | INV022 | Inverter 022 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GridUnderfrequency | INV022 | Inverter 022 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GridUndervoltage | INV022 | Inverter 022 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GridVoltageImbalance | INV022 | Inverter 022 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_GroundFault | INV022 | Inverter 022 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_HighInputStringVoltageGround | INV022 | Inverter 022 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_HighStringInputVoltage | INV022 | Inverter 022 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_InverterEfficiency | INV022 | Inverter 022 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_InverterGridConnectionStatus | INV022 | Inverter 022 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_InverterOverTemperature | INV022 | Inverter 022 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_InverterRunningStopped | INV022 | Inverter 022 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_InverterStartupShutdownStatus | INV022 | Inverter 022 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_InverterTripHistoryAvailable | INV022 | Inverter 022 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_IslandingDetectionStatus | INV022 | Inverter 022 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_LicenseExpired | INV022 | Inverter 022 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_LockingStatus | INV022 | Inverter 022 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_LowInsulationResistance | INV022 | Inverter 022 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_NormalGridConnection | INV022 | Inverter 022 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_NormalShutdown | INV022 | Inverter 022 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_OffGridOutputOverload | INV022 | Inverter 022 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_OptimizerFault | INV022 | Inverter 022 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_OutputDCComponentOverhigh | INV022 | Inverter 022 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_OutputOvercurrent | INV022 | Inverter 022 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_PVStringLoss | INV022 | Inverter 022 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_PassiveIslanding | INV022 | Inverter 022 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_PeripheralPortShortCircuit | INV022 | Inverter 022 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_PhaseWireShortCircuitedPE | INV022 | Inverter 022 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_PowerCurtailmentStatus | INV022 | Inverter 022 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_PowerFactor | INV022 | Inverter 022 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_PowerLimitationActiveGridCommand | INV022 | Inverter 022 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_ReactivePower | INV022 | Inverter 022 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV022_RemoteOFFStatus | INV022 | Inverter 022 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_Shutdown | INV022 | Inverter 022 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_ShutdownPowerRationing | INV022 | Inverter 022 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_SpotCheck | INV022 | Inverter 022 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_Standby | INV022 | Inverter 022 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_StringCurrentBackfeed | INV022 | Inverter 022 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_StringReverseConnection | INV022 | Inverter 022 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_StringReversePolarity | INV022 | Inverter 022 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_TotalEnergyYield | INV022 | Inverter 022 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV022_TransientACOvervoltage | INV022 | Inverter 022 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_UnstableGridFrequency | INV022 | Inverter 022 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_UpgradeFailed | INV022 | Inverter 022 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV022_WarningActive | INV022 | Inverter 022 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_ACCurrent | INV023 | Inverter 023 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_ACOvervoltage | INV023 | Inverter 023 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_ACUndervoltage | INV023 | Inverter 023 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_ACVoltage | INV023 | Inverter 023 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_AFCISelfCheckFailure | INV023 | Inverter 023 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_AbnormalGrounding | INV023 | Inverter 023 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_AbnormalPVModuleConfiguration | INV023 | Inverter 023 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_AbnormalResidualCurrent | INV023 | Inverter 023 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_AbnormalStringPower | INV023 | Inverter 023 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_ActiveIslanding | INV023 | Inverter 023 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_ActivePower | INV023 | Inverter 023 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_ApparentPower | INV023 | Inverter 023 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV023_BuiltPIDOperationAbnormal | INV023 | Inverter 023 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_CabinetOvertemperature | INV023 | Inverter 023 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_CommunicationFailure | INV023 | Inverter 023 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_CommunicationStatus | INV023 | Inverter 023 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_DCArcFault | INV023 | Inverter 023 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_DCCurrent | INV023 | Inverter 023 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_DCInsulationFault | INV023 | Inverter 023 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_DCOvervoltage | INV023 | Inverter 023 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_DCPower | INV023 | Inverter 023 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV023_DCVoltage | INV023 | Inverter 023 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_DailyEnergyYield | INV023 | Inverter 023 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV023_DeviceFault | INV023 | Inverter 023 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_ExternalFanAbnormal | INV023 | Inverter 023 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_FanFailure | INV023 | Inverter 023 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_Faulty | INV023 | Inverter 023 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_FaultyMonitoringUnit | INV023 | Inverter 023 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_FaultyPowerCollector | INV023 | Inverter 023 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_Frequency | INV023 | Inverter 023 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_GeneralFaultTrip | INV023 | Inverter 023 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_Grid | INV023 | Inverter 023 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GridConnectionDeratingInverterInternalCauses | INV023 | Inverter 023 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GridConnectionDeratingPowerRationing | INV023 | Inverter 023 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GridLoss | INV023 | Inverter 023 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GridOverfrequency | INV023 | Inverter 023 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GridOvervoltage | INV023 | Inverter 023 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GridTiedOffGridControllerAbnormal | INV023 | Inverter 023 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GridUnderfrequency | INV023 | Inverter 023 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GridUndervoltage | INV023 | Inverter 023 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GridVoltageImbalance | INV023 | Inverter 023 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_GroundFault | INV023 | Inverter 023 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_HighInputStringVoltageGround | INV023 | Inverter 023 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_HighStringInputVoltage | INV023 | Inverter 023 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_InverterEfficiency | INV023 | Inverter 023 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_InverterGridConnectionStatus | INV023 | Inverter 023 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_InverterOverTemperature | INV023 | Inverter 023 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_InverterRunningStopped | INV023 | Inverter 023 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_InverterStartupShutdownStatus | INV023 | Inverter 023 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_InverterTripHistoryAvailable | INV023 | Inverter 023 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_IslandingDetectionStatus | INV023 | Inverter 023 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_LicenseExpired | INV023 | Inverter 023 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_LockingStatus | INV023 | Inverter 023 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_LowInsulationResistance | INV023 | Inverter 023 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_NormalGridConnection | INV023 | Inverter 023 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_NormalShutdown | INV023 | Inverter 023 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_OffGridOutputOverload | INV023 | Inverter 023 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_OptimizerFault | INV023 | Inverter 023 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_OutputDCComponentOverhigh | INV023 | Inverter 023 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_OutputOvercurrent | INV023 | Inverter 023 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_PVStringLoss | INV023 | Inverter 023 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_PassiveIslanding | INV023 | Inverter 023 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_PeripheralPortShortCircuit | INV023 | Inverter 023 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_PhaseWireShortCircuitedPE | INV023 | Inverter 023 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_PowerCurtailmentStatus | INV023 | Inverter 023 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_PowerFactor | INV023 | Inverter 023 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_PowerLimitationActiveGridCommand | INV023 | Inverter 023 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_ReactivePower | INV023 | Inverter 023 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV023_RemoteOFFStatus | INV023 | Inverter 023 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_Shutdown | INV023 | Inverter 023 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_ShutdownPowerRationing | INV023 | Inverter 023 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_SpotCheck | INV023 | Inverter 023 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_Standby | INV023 | Inverter 023 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_StringCurrentBackfeed | INV023 | Inverter 023 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_StringReverseConnection | INV023 | Inverter 023 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_StringReversePolarity | INV023 | Inverter 023 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_TotalEnergyYield | INV023 | Inverter 023 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV023_TransientACOvervoltage | INV023 | Inverter 023 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_UnstableGridFrequency | INV023 | Inverter 023 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_UpgradeFailed | INV023 | Inverter 023 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV023_WarningActive | INV023 | Inverter 023 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_ACCurrent | INV024 | Inverter 024 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_ACOvervoltage | INV024 | Inverter 024 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_ACUndervoltage | INV024 | Inverter 024 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_ACVoltage | INV024 | Inverter 024 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_AFCISelfCheckFailure | INV024 | Inverter 024 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_AbnormalGrounding | INV024 | Inverter 024 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_AbnormalPVModuleConfiguration | INV024 | Inverter 024 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_AbnormalResidualCurrent | INV024 | Inverter 024 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_AbnormalStringPower | INV024 | Inverter 024 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_ActiveIslanding | INV024 | Inverter 024 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_ActivePower | INV024 | Inverter 024 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_ApparentPower | INV024 | Inverter 024 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV024_BuiltPIDOperationAbnormal | INV024 | Inverter 024 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_CabinetOvertemperature | INV024 | Inverter 024 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_CommunicationFailure | INV024 | Inverter 024 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_CommunicationStatus | INV024 | Inverter 024 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_DCArcFault | INV024 | Inverter 024 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_DCCurrent | INV024 | Inverter 024 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_DCInsulationFault | INV024 | Inverter 024 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_DCOvervoltage | INV024 | Inverter 024 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_DCPower | INV024 | Inverter 024 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV024_DCVoltage | INV024 | Inverter 024 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_DailyEnergyYield | INV024 | Inverter 024 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV024_DeviceFault | INV024 | Inverter 024 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_ExternalFanAbnormal | INV024 | Inverter 024 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_FanFailure | INV024 | Inverter 024 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_Faulty | INV024 | Inverter 024 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_FaultyMonitoringUnit | INV024 | Inverter 024 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_FaultyPowerCollector | INV024 | Inverter 024 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_Frequency | INV024 | Inverter 024 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_GeneralFaultTrip | INV024 | Inverter 024 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_Grid | INV024 | Inverter 024 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GridConnectionDeratingInverterInternalCauses | INV024 | Inverter 024 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GridConnectionDeratingPowerRationing | INV024 | Inverter 024 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GridLoss | INV024 | Inverter 024 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GridOverfrequency | INV024 | Inverter 024 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GridOvervoltage | INV024 | Inverter 024 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GridTiedOffGridControllerAbnormal | INV024 | Inverter 024 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GridUnderfrequency | INV024 | Inverter 024 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GridUndervoltage | INV024 | Inverter 024 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GridVoltageImbalance | INV024 | Inverter 024 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_GroundFault | INV024 | Inverter 024 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_HighInputStringVoltageGround | INV024 | Inverter 024 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_HighStringInputVoltage | INV024 | Inverter 024 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_InverterEfficiency | INV024 | Inverter 024 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_InverterGridConnectionStatus | INV024 | Inverter 024 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_InverterOverTemperature | INV024 | Inverter 024 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_InverterRunningStopped | INV024 | Inverter 024 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_InverterStartupShutdownStatus | INV024 | Inverter 024 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_InverterTripHistoryAvailable | INV024 | Inverter 024 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_IslandingDetectionStatus | INV024 | Inverter 024 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_LicenseExpired | INV024 | Inverter 024 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_LockingStatus | INV024 | Inverter 024 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_LowInsulationResistance | INV024 | Inverter 024 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_NormalGridConnection | INV024 | Inverter 024 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_NormalShutdown | INV024 | Inverter 024 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_OffGridOutputOverload | INV024 | Inverter 024 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_OptimizerFault | INV024 | Inverter 024 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_OutputDCComponentOverhigh | INV024 | Inverter 024 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_OutputOvercurrent | INV024 | Inverter 024 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_PVStringLoss | INV024 | Inverter 024 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_PassiveIslanding | INV024 | Inverter 024 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_PeripheralPortShortCircuit | INV024 | Inverter 024 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_PhaseWireShortCircuitedPE | INV024 | Inverter 024 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_PowerCurtailmentStatus | INV024 | Inverter 024 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_PowerFactor | INV024 | Inverter 024 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_PowerLimitationActiveGridCommand | INV024 | Inverter 024 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_ReactivePower | INV024 | Inverter 024 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV024_RemoteOFFStatus | INV024 | Inverter 024 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_Shutdown | INV024 | Inverter 024 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_ShutdownPowerRationing | INV024 | Inverter 024 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_SpotCheck | INV024 | Inverter 024 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_Standby | INV024 | Inverter 024 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_StringCurrentBackfeed | INV024 | Inverter 024 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_StringReverseConnection | INV024 | Inverter 024 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_StringReversePolarity | INV024 | Inverter 024 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_TotalEnergyYield | INV024 | Inverter 024 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV024_TransientACOvervoltage | INV024 | Inverter 024 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_UnstableGridFrequency | INV024 | Inverter 024 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_UpgradeFailed | INV024 | Inverter 024 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV024_WarningActive | INV024 | Inverter 024 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_ACCurrent | INV025 | Inverter 025 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_ACOvervoltage | INV025 | Inverter 025 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_ACUndervoltage | INV025 | Inverter 025 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_ACVoltage | INV025 | Inverter 025 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_AFCISelfCheckFailure | INV025 | Inverter 025 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_AbnormalGrounding | INV025 | Inverter 025 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_AbnormalPVModuleConfiguration | INV025 | Inverter 025 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_AbnormalResidualCurrent | INV025 | Inverter 025 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_AbnormalStringPower | INV025 | Inverter 025 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_ActiveIslanding | INV025 | Inverter 025 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_ActivePower | INV025 | Inverter 025 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_ApparentPower | INV025 | Inverter 025 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV025_BuiltPIDOperationAbnormal | INV025 | Inverter 025 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_CabinetOvertemperature | INV025 | Inverter 025 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_CommunicationFailure | INV025 | Inverter 025 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_CommunicationStatus | INV025 | Inverter 025 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_DCArcFault | INV025 | Inverter 025 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_DCCurrent | INV025 | Inverter 025 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_DCInsulationFault | INV025 | Inverter 025 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_DCOvervoltage | INV025 | Inverter 025 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_DCPower | INV025 | Inverter 025 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV025_DCVoltage | INV025 | Inverter 025 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_DailyEnergyYield | INV025 | Inverter 025 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV025_DeviceFault | INV025 | Inverter 025 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_ExternalFanAbnormal | INV025 | Inverter 025 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_FanFailure | INV025 | Inverter 025 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_Faulty | INV025 | Inverter 025 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_FaultyMonitoringUnit | INV025 | Inverter 025 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_FaultyPowerCollector | INV025 | Inverter 025 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_Frequency | INV025 | Inverter 025 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_GeneralFaultTrip | INV025 | Inverter 025 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_Grid | INV025 | Inverter 025 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GridConnectionDeratingInverterInternalCauses | INV025 | Inverter 025 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GridConnectionDeratingPowerRationing | INV025 | Inverter 025 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GridLoss | INV025 | Inverter 025 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GridOverfrequency | INV025 | Inverter 025 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GridOvervoltage | INV025 | Inverter 025 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GridTiedOffGridControllerAbnormal | INV025 | Inverter 025 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GridUnderfrequency | INV025 | Inverter 025 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GridUndervoltage | INV025 | Inverter 025 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GridVoltageImbalance | INV025 | Inverter 025 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_GroundFault | INV025 | Inverter 025 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_HighInputStringVoltageGround | INV025 | Inverter 025 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_HighStringInputVoltage | INV025 | Inverter 025 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_InverterEfficiency | INV025 | Inverter 025 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_InverterGridConnectionStatus | INV025 | Inverter 025 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_InverterOverTemperature | INV025 | Inverter 025 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_InverterRunningStopped | INV025 | Inverter 025 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_InverterStartupShutdownStatus | INV025 | Inverter 025 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_InverterTripHistoryAvailable | INV025 | Inverter 025 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_IslandingDetectionStatus | INV025 | Inverter 025 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_LicenseExpired | INV025 | Inverter 025 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_LockingStatus | INV025 | Inverter 025 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_LowInsulationResistance | INV025 | Inverter 025 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_NormalGridConnection | INV025 | Inverter 025 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_NormalShutdown | INV025 | Inverter 025 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_OffGridOutputOverload | INV025 | Inverter 025 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_OptimizerFault | INV025 | Inverter 025 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_OutputDCComponentOverhigh | INV025 | Inverter 025 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_OutputOvercurrent | INV025 | Inverter 025 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_PVStringLoss | INV025 | Inverter 025 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_PassiveIslanding | INV025 | Inverter 025 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_PeripheralPortShortCircuit | INV025 | Inverter 025 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_PhaseWireShortCircuitedPE | INV025 | Inverter 025 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_PowerCurtailmentStatus | INV025 | Inverter 025 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_PowerFactor | INV025 | Inverter 025 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_PowerLimitationActiveGridCommand | INV025 | Inverter 025 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_ReactivePower | INV025 | Inverter 025 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV025_RemoteOFFStatus | INV025 | Inverter 025 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_Shutdown | INV025 | Inverter 025 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_ShutdownPowerRationing | INV025 | Inverter 025 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_SpotCheck | INV025 | Inverter 025 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_Standby | INV025 | Inverter 025 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_StringCurrentBackfeed | INV025 | Inverter 025 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_StringReverseConnection | INV025 | Inverter 025 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_StringReversePolarity | INV025 | Inverter 025 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_TotalEnergyYield | INV025 | Inverter 025 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV025_TransientACOvervoltage | INV025 | Inverter 025 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_UnstableGridFrequency | INV025 | Inverter 025 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_UpgradeFailed | INV025 | Inverter 025 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV025_WarningActive | INV025 | Inverter 025 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_ACCurrent | INV026 | Inverter 026 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_ACOvervoltage | INV026 | Inverter 026 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_ACUndervoltage | INV026 | Inverter 026 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_ACVoltage | INV026 | Inverter 026 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_AFCISelfCheckFailure | INV026 | Inverter 026 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_AbnormalGrounding | INV026 | Inverter 026 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_AbnormalPVModuleConfiguration | INV026 | Inverter 026 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_AbnormalResidualCurrent | INV026 | Inverter 026 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_AbnormalStringPower | INV026 | Inverter 026 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_ActiveIslanding | INV026 | Inverter 026 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_ActivePower | INV026 | Inverter 026 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_ApparentPower | INV026 | Inverter 026 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV026_BuiltPIDOperationAbnormal | INV026 | Inverter 026 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_CabinetOvertemperature | INV026 | Inverter 026 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_CommunicationFailure | INV026 | Inverter 026 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_CommunicationStatus | INV026 | Inverter 026 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_DCArcFault | INV026 | Inverter 026 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_DCCurrent | INV026 | Inverter 026 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_DCInsulationFault | INV026 | Inverter 026 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_DCOvervoltage | INV026 | Inverter 026 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_DCPower | INV026 | Inverter 026 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV026_DCVoltage | INV026 | Inverter 026 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_DailyEnergyYield | INV026 | Inverter 026 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV026_DeviceFault | INV026 | Inverter 026 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_ExternalFanAbnormal | INV026 | Inverter 026 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_FanFailure | INV026 | Inverter 026 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_Faulty | INV026 | Inverter 026 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_FaultyMonitoringUnit | INV026 | Inverter 026 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_FaultyPowerCollector | INV026 | Inverter 026 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_Frequency | INV026 | Inverter 026 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_GeneralFaultTrip | INV026 | Inverter 026 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_Grid | INV026 | Inverter 026 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GridConnectionDeratingInverterInternalCauses | INV026 | Inverter 026 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GridConnectionDeratingPowerRationing | INV026 | Inverter 026 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GridLoss | INV026 | Inverter 026 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GridOverfrequency | INV026 | Inverter 026 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GridOvervoltage | INV026 | Inverter 026 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GridTiedOffGridControllerAbnormal | INV026 | Inverter 026 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GridUnderfrequency | INV026 | Inverter 026 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GridUndervoltage | INV026 | Inverter 026 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GridVoltageImbalance | INV026 | Inverter 026 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_GroundFault | INV026 | Inverter 026 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_HighInputStringVoltageGround | INV026 | Inverter 026 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_HighStringInputVoltage | INV026 | Inverter 026 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_InverterEfficiency | INV026 | Inverter 026 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_InverterGridConnectionStatus | INV026 | Inverter 026 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_InverterOverTemperature | INV026 | Inverter 026 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_InverterRunningStopped | INV026 | Inverter 026 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_InverterStartupShutdownStatus | INV026 | Inverter 026 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_InverterTripHistoryAvailable | INV026 | Inverter 026 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_IslandingDetectionStatus | INV026 | Inverter 026 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_LicenseExpired | INV026 | Inverter 026 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_LockingStatus | INV026 | Inverter 026 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_LowInsulationResistance | INV026 | Inverter 026 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_NormalGridConnection | INV026 | Inverter 026 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_NormalShutdown | INV026 | Inverter 026 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_OffGridOutputOverload | INV026 | Inverter 026 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_OptimizerFault | INV026 | Inverter 026 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_OutputDCComponentOverhigh | INV026 | Inverter 026 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_OutputOvercurrent | INV026 | Inverter 026 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_PVStringLoss | INV026 | Inverter 026 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_PassiveIslanding | INV026 | Inverter 026 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_PeripheralPortShortCircuit | INV026 | Inverter 026 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_PhaseWireShortCircuitedPE | INV026 | Inverter 026 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_PowerCurtailmentStatus | INV026 | Inverter 026 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_PowerFactor | INV026 | Inverter 026 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_PowerLimitationActiveGridCommand | INV026 | Inverter 026 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_ReactivePower | INV026 | Inverter 026 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV026_RemoteOFFStatus | INV026 | Inverter 026 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_Shutdown | INV026 | Inverter 026 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_ShutdownPowerRationing | INV026 | Inverter 026 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_SpotCheck | INV026 | Inverter 026 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_Standby | INV026 | Inverter 026 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_StringCurrentBackfeed | INV026 | Inverter 026 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_StringReverseConnection | INV026 | Inverter 026 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_StringReversePolarity | INV026 | Inverter 026 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_TotalEnergyYield | INV026 | Inverter 026 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV026_TransientACOvervoltage | INV026 | Inverter 026 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_UnstableGridFrequency | INV026 | Inverter 026 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_UpgradeFailed | INV026 | Inverter 026 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV026_WarningActive | INV026 | Inverter 026 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_ACCurrent | INV027 | Inverter 027 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_ACOvervoltage | INV027 | Inverter 027 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_ACUndervoltage | INV027 | Inverter 027 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_ACVoltage | INV027 | Inverter 027 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_AFCISelfCheckFailure | INV027 | Inverter 027 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_AbnormalGrounding | INV027 | Inverter 027 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_AbnormalPVModuleConfiguration | INV027 | Inverter 027 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_AbnormalResidualCurrent | INV027 | Inverter 027 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_AbnormalStringPower | INV027 | Inverter 027 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_ActiveIslanding | INV027 | Inverter 027 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_ActivePower | INV027 | Inverter 027 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_ApparentPower | INV027 | Inverter 027 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV027_BuiltPIDOperationAbnormal | INV027 | Inverter 027 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_CabinetOvertemperature | INV027 | Inverter 027 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_CommunicationFailure | INV027 | Inverter 027 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_CommunicationStatus | INV027 | Inverter 027 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_DCArcFault | INV027 | Inverter 027 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_DCCurrent | INV027 | Inverter 027 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_DCInsulationFault | INV027 | Inverter 027 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_DCOvervoltage | INV027 | Inverter 027 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_DCPower | INV027 | Inverter 027 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV027_DCVoltage | INV027 | Inverter 027 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_DailyEnergyYield | INV027 | Inverter 027 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV027_DeviceFault | INV027 | Inverter 027 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_ExternalFanAbnormal | INV027 | Inverter 027 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_FanFailure | INV027 | Inverter 027 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_Faulty | INV027 | Inverter 027 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_FaultyMonitoringUnit | INV027 | Inverter 027 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_FaultyPowerCollector | INV027 | Inverter 027 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_Frequency | INV027 | Inverter 027 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_GeneralFaultTrip | INV027 | Inverter 027 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_Grid | INV027 | Inverter 027 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GridConnectionDeratingInverterInternalCauses | INV027 | Inverter 027 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GridConnectionDeratingPowerRationing | INV027 | Inverter 027 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GridLoss | INV027 | Inverter 027 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GridOverfrequency | INV027 | Inverter 027 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GridOvervoltage | INV027 | Inverter 027 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GridTiedOffGridControllerAbnormal | INV027 | Inverter 027 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GridUnderfrequency | INV027 | Inverter 027 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GridUndervoltage | INV027 | Inverter 027 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GridVoltageImbalance | INV027 | Inverter 027 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_GroundFault | INV027 | Inverter 027 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_HighInputStringVoltageGround | INV027 | Inverter 027 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_HighStringInputVoltage | INV027 | Inverter 027 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_InverterEfficiency | INV027 | Inverter 027 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_InverterGridConnectionStatus | INV027 | Inverter 027 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_InverterOverTemperature | INV027 | Inverter 027 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_InverterRunningStopped | INV027 | Inverter 027 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_InverterStartupShutdownStatus | INV027 | Inverter 027 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_InverterTripHistoryAvailable | INV027 | Inverter 027 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_IslandingDetectionStatus | INV027 | Inverter 027 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_LicenseExpired | INV027 | Inverter 027 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_LockingStatus | INV027 | Inverter 027 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_LowInsulationResistance | INV027 | Inverter 027 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_NormalGridConnection | INV027 | Inverter 027 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_NormalShutdown | INV027 | Inverter 027 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_OffGridOutputOverload | INV027 | Inverter 027 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_OptimizerFault | INV027 | Inverter 027 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_OutputDCComponentOverhigh | INV027 | Inverter 027 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_OutputOvercurrent | INV027 | Inverter 027 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_PVStringLoss | INV027 | Inverter 027 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_PassiveIslanding | INV027 | Inverter 027 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_PeripheralPortShortCircuit | INV027 | Inverter 027 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_PhaseWireShortCircuitedPE | INV027 | Inverter 027 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_PowerCurtailmentStatus | INV027 | Inverter 027 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_PowerFactor | INV027 | Inverter 027 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_PowerLimitationActiveGridCommand | INV027 | Inverter 027 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_ReactivePower | INV027 | Inverter 027 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV027_RemoteOFFStatus | INV027 | Inverter 027 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_Shutdown | INV027 | Inverter 027 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_ShutdownPowerRationing | INV027 | Inverter 027 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_SpotCheck | INV027 | Inverter 027 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_Standby | INV027 | Inverter 027 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_StringCurrentBackfeed | INV027 | Inverter 027 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_StringReverseConnection | INV027 | Inverter 027 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_StringReversePolarity | INV027 | Inverter 027 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_TotalEnergyYield | INV027 | Inverter 027 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV027_TransientACOvervoltage | INV027 | Inverter 027 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_UnstableGridFrequency | INV027 | Inverter 027 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_UpgradeFailed | INV027 | Inverter 027 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV027_WarningActive | INV027 | Inverter 027 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_ACCurrent | INV028 | Inverter 028 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_ACOvervoltage | INV028 | Inverter 028 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_ACUndervoltage | INV028 | Inverter 028 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_ACVoltage | INV028 | Inverter 028 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_AFCISelfCheckFailure | INV028 | Inverter 028 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_AbnormalGrounding | INV028 | Inverter 028 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_AbnormalPVModuleConfiguration | INV028 | Inverter 028 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_AbnormalResidualCurrent | INV028 | Inverter 028 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_AbnormalStringPower | INV028 | Inverter 028 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_ActiveIslanding | INV028 | Inverter 028 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_ActivePower | INV028 | Inverter 028 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_ApparentPower | INV028 | Inverter 028 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV028_BuiltPIDOperationAbnormal | INV028 | Inverter 028 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_CabinetOvertemperature | INV028 | Inverter 028 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_CommunicationFailure | INV028 | Inverter 028 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_CommunicationStatus | INV028 | Inverter 028 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_DCArcFault | INV028 | Inverter 028 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_DCCurrent | INV028 | Inverter 028 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_DCInsulationFault | INV028 | Inverter 028 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_DCOvervoltage | INV028 | Inverter 028 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_DCPower | INV028 | Inverter 028 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV028_DCVoltage | INV028 | Inverter 028 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_DailyEnergyYield | INV028 | Inverter 028 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV028_DeviceFault | INV028 | Inverter 028 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_ExternalFanAbnormal | INV028 | Inverter 028 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_FanFailure | INV028 | Inverter 028 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_Faulty | INV028 | Inverter 028 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_FaultyMonitoringUnit | INV028 | Inverter 028 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_FaultyPowerCollector | INV028 | Inverter 028 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_Frequency | INV028 | Inverter 028 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_GeneralFaultTrip | INV028 | Inverter 028 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_Grid | INV028 | Inverter 028 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GridConnectionDeratingInverterInternalCauses | INV028 | Inverter 028 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GridConnectionDeratingPowerRationing | INV028 | Inverter 028 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GridLoss | INV028 | Inverter 028 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GridOverfrequency | INV028 | Inverter 028 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GridOvervoltage | INV028 | Inverter 028 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GridTiedOffGridControllerAbnormal | INV028 | Inverter 028 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GridUnderfrequency | INV028 | Inverter 028 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GridUndervoltage | INV028 | Inverter 028 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GridVoltageImbalance | INV028 | Inverter 028 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_GroundFault | INV028 | Inverter 028 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_HighInputStringVoltageGround | INV028 | Inverter 028 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_HighStringInputVoltage | INV028 | Inverter 028 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_InverterEfficiency | INV028 | Inverter 028 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_InverterGridConnectionStatus | INV028 | Inverter 028 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_InverterOverTemperature | INV028 | Inverter 028 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_InverterRunningStopped | INV028 | Inverter 028 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_InverterStartupShutdownStatus | INV028 | Inverter 028 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_InverterTripHistoryAvailable | INV028 | Inverter 028 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_IslandingDetectionStatus | INV028 | Inverter 028 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_LicenseExpired | INV028 | Inverter 028 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_LockingStatus | INV028 | Inverter 028 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_LowInsulationResistance | INV028 | Inverter 028 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_NormalGridConnection | INV028 | Inverter 028 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_NormalShutdown | INV028 | Inverter 028 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_OffGridOutputOverload | INV028 | Inverter 028 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_OptimizerFault | INV028 | Inverter 028 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_OutputDCComponentOverhigh | INV028 | Inverter 028 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_OutputOvercurrent | INV028 | Inverter 028 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_PVStringLoss | INV028 | Inverter 028 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_PassiveIslanding | INV028 | Inverter 028 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_PeripheralPortShortCircuit | INV028 | Inverter 028 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_PhaseWireShortCircuitedPE | INV028 | Inverter 028 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_PowerCurtailmentStatus | INV028 | Inverter 028 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_PowerFactor | INV028 | Inverter 028 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_PowerLimitationActiveGridCommand | INV028 | Inverter 028 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_ReactivePower | INV028 | Inverter 028 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV028_RemoteOFFStatus | INV028 | Inverter 028 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_Shutdown | INV028 | Inverter 028 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_ShutdownPowerRationing | INV028 | Inverter 028 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_SpotCheck | INV028 | Inverter 028 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_Standby | INV028 | Inverter 028 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_StringCurrentBackfeed | INV028 | Inverter 028 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_StringReverseConnection | INV028 | Inverter 028 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_StringReversePolarity | INV028 | Inverter 028 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_TotalEnergyYield | INV028 | Inverter 028 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV028_TransientACOvervoltage | INV028 | Inverter 028 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_UnstableGridFrequency | INV028 | Inverter 028 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_UpgradeFailed | INV028 | Inverter 028 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV028_WarningActive | INV028 | Inverter 028 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_ACCurrent | INV029 | Inverter 029 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_ACOvervoltage | INV029 | Inverter 029 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_ACUndervoltage | INV029 | Inverter 029 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_ACVoltage | INV029 | Inverter 029 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_AFCISelfCheckFailure | INV029 | Inverter 029 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_AbnormalGrounding | INV029 | Inverter 029 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_AbnormalPVModuleConfiguration | INV029 | Inverter 029 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_AbnormalResidualCurrent | INV029 | Inverter 029 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_AbnormalStringPower | INV029 | Inverter 029 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_ActiveIslanding | INV029 | Inverter 029 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_ActivePower | INV029 | Inverter 029 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_ApparentPower | INV029 | Inverter 029 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV029_BuiltPIDOperationAbnormal | INV029 | Inverter 029 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_CabinetOvertemperature | INV029 | Inverter 029 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_CommunicationFailure | INV029 | Inverter 029 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_CommunicationStatus | INV029 | Inverter 029 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_DCArcFault | INV029 | Inverter 029 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_DCCurrent | INV029 | Inverter 029 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_DCInsulationFault | INV029 | Inverter 029 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_DCOvervoltage | INV029 | Inverter 029 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_DCPower | INV029 | Inverter 029 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV029_DCVoltage | INV029 | Inverter 029 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_DailyEnergyYield | INV029 | Inverter 029 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV029_DeviceFault | INV029 | Inverter 029 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_ExternalFanAbnormal | INV029 | Inverter 029 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_FanFailure | INV029 | Inverter 029 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_Faulty | INV029 | Inverter 029 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_FaultyMonitoringUnit | INV029 | Inverter 029 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_FaultyPowerCollector | INV029 | Inverter 029 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_Frequency | INV029 | Inverter 029 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_GeneralFaultTrip | INV029 | Inverter 029 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_Grid | INV029 | Inverter 029 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GridConnectionDeratingInverterInternalCauses | INV029 | Inverter 029 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GridConnectionDeratingPowerRationing | INV029 | Inverter 029 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GridLoss | INV029 | Inverter 029 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GridOverfrequency | INV029 | Inverter 029 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GridOvervoltage | INV029 | Inverter 029 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GridTiedOffGridControllerAbnormal | INV029 | Inverter 029 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GridUnderfrequency | INV029 | Inverter 029 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GridUndervoltage | INV029 | Inverter 029 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GridVoltageImbalance | INV029 | Inverter 029 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_GroundFault | INV029 | Inverter 029 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_HighInputStringVoltageGround | INV029 | Inverter 029 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_HighStringInputVoltage | INV029 | Inverter 029 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_InverterEfficiency | INV029 | Inverter 029 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_InverterGridConnectionStatus | INV029 | Inverter 029 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_InverterOverTemperature | INV029 | Inverter 029 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_InverterRunningStopped | INV029 | Inverter 029 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_InverterStartupShutdownStatus | INV029 | Inverter 029 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_InverterTripHistoryAvailable | INV029 | Inverter 029 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_IslandingDetectionStatus | INV029 | Inverter 029 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_LicenseExpired | INV029 | Inverter 029 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_LockingStatus | INV029 | Inverter 029 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_LowInsulationResistance | INV029 | Inverter 029 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_NormalGridConnection | INV029 | Inverter 029 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_NormalShutdown | INV029 | Inverter 029 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_OffGridOutputOverload | INV029 | Inverter 029 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_OptimizerFault | INV029 | Inverter 029 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_OutputDCComponentOverhigh | INV029 | Inverter 029 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_OutputOvercurrent | INV029 | Inverter 029 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_PVStringLoss | INV029 | Inverter 029 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_PassiveIslanding | INV029 | Inverter 029 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_PeripheralPortShortCircuit | INV029 | Inverter 029 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_PhaseWireShortCircuitedPE | INV029 | Inverter 029 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_PowerCurtailmentStatus | INV029 | Inverter 029 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_PowerFactor | INV029 | Inverter 029 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_PowerLimitationActiveGridCommand | INV029 | Inverter 029 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_ReactivePower | INV029 | Inverter 029 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV029_RemoteOFFStatus | INV029 | Inverter 029 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_Shutdown | INV029 | Inverter 029 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_ShutdownPowerRationing | INV029 | Inverter 029 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_SpotCheck | INV029 | Inverter 029 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_Standby | INV029 | Inverter 029 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_StringCurrentBackfeed | INV029 | Inverter 029 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_StringReverseConnection | INV029 | Inverter 029 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_StringReversePolarity | INV029 | Inverter 029 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_TotalEnergyYield | INV029 | Inverter 029 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV029_TransientACOvervoltage | INV029 | Inverter 029 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_UnstableGridFrequency | INV029 | Inverter 029 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_UpgradeFailed | INV029 | Inverter 029 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV029_WarningActive | INV029 | Inverter 029 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_ACCurrent | INV030 | Inverter 030 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_ACOvervoltage | INV030 | Inverter 030 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_ACUndervoltage | INV030 | Inverter 030 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_ACVoltage | INV030 | Inverter 030 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_AFCISelfCheckFailure | INV030 | Inverter 030 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_AbnormalGrounding | INV030 | Inverter 030 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_AbnormalPVModuleConfiguration | INV030 | Inverter 030 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_AbnormalResidualCurrent | INV030 | Inverter 030 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_AbnormalStringPower | INV030 | Inverter 030 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_ActiveIslanding | INV030 | Inverter 030 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_ActivePower | INV030 | Inverter 030 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_ApparentPower | INV030 | Inverter 030 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV030_BuiltPIDOperationAbnormal | INV030 | Inverter 030 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_CabinetOvertemperature | INV030 | Inverter 030 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_CommunicationFailure | INV030 | Inverter 030 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_CommunicationStatus | INV030 | Inverter 030 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_DCArcFault | INV030 | Inverter 030 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_DCCurrent | INV030 | Inverter 030 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_DCInsulationFault | INV030 | Inverter 030 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_DCOvervoltage | INV030 | Inverter 030 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_DCPower | INV030 | Inverter 030 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV030_DCVoltage | INV030 | Inverter 030 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_DailyEnergyYield | INV030 | Inverter 030 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV030_DeviceFault | INV030 | Inverter 030 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_ExternalFanAbnormal | INV030 | Inverter 030 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_FanFailure | INV030 | Inverter 030 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_Faulty | INV030 | Inverter 030 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_FaultyMonitoringUnit | INV030 | Inverter 030 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_FaultyPowerCollector | INV030 | Inverter 030 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_Frequency | INV030 | Inverter 030 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_GeneralFaultTrip | INV030 | Inverter 030 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_Grid | INV030 | Inverter 030 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GridConnectionDeratingInverterInternalCauses | INV030 | Inverter 030 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GridConnectionDeratingPowerRationing | INV030 | Inverter 030 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GridLoss | INV030 | Inverter 030 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GridOverfrequency | INV030 | Inverter 030 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GridOvervoltage | INV030 | Inverter 030 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GridTiedOffGridControllerAbnormal | INV030 | Inverter 030 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GridUnderfrequency | INV030 | Inverter 030 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GridUndervoltage | INV030 | Inverter 030 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GridVoltageImbalance | INV030 | Inverter 030 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_GroundFault | INV030 | Inverter 030 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_HighInputStringVoltageGround | INV030 | Inverter 030 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_HighStringInputVoltage | INV030 | Inverter 030 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_InverterEfficiency | INV030 | Inverter 030 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_InverterGridConnectionStatus | INV030 | Inverter 030 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_InverterOverTemperature | INV030 | Inverter 030 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_InverterRunningStopped | INV030 | Inverter 030 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_InverterStartupShutdownStatus | INV030 | Inverter 030 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_InverterTripHistoryAvailable | INV030 | Inverter 030 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_IslandingDetectionStatus | INV030 | Inverter 030 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_LicenseExpired | INV030 | Inverter 030 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_LockingStatus | INV030 | Inverter 030 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_LowInsulationResistance | INV030 | Inverter 030 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_NormalGridConnection | INV030 | Inverter 030 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_NormalShutdown | INV030 | Inverter 030 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_OffGridOutputOverload | INV030 | Inverter 030 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_OptimizerFault | INV030 | Inverter 030 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_OutputDCComponentOverhigh | INV030 | Inverter 030 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_OutputOvercurrent | INV030 | Inverter 030 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_PVStringLoss | INV030 | Inverter 030 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_PassiveIslanding | INV030 | Inverter 030 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_PeripheralPortShortCircuit | INV030 | Inverter 030 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_PhaseWireShortCircuitedPE | INV030 | Inverter 030 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_PowerCurtailmentStatus | INV030 | Inverter 030 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_PowerFactor | INV030 | Inverter 030 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_PowerLimitationActiveGridCommand | INV030 | Inverter 030 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_ReactivePower | INV030 | Inverter 030 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV030_RemoteOFFStatus | INV030 | Inverter 030 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_Shutdown | INV030 | Inverter 030 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_ShutdownPowerRationing | INV030 | Inverter 030 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_SpotCheck | INV030 | Inverter 030 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_Standby | INV030 | Inverter 030 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_StringCurrentBackfeed | INV030 | Inverter 030 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_StringReverseConnection | INV030 | Inverter 030 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_StringReversePolarity | INV030 | Inverter 030 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_TotalEnergyYield | INV030 | Inverter 030 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV030_TransientACOvervoltage | INV030 | Inverter 030 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_UnstableGridFrequency | INV030 | Inverter 030 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_UpgradeFailed | INV030 | Inverter 030 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV030_WarningActive | INV030 | Inverter 030 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_ACCurrent | INV031 | Inverter 031 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_ACOvervoltage | INV031 | Inverter 031 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_ACUndervoltage | INV031 | Inverter 031 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_ACVoltage | INV031 | Inverter 031 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_AFCISelfCheckFailure | INV031 | Inverter 031 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_AbnormalGrounding | INV031 | Inverter 031 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_AbnormalPVModuleConfiguration | INV031 | Inverter 031 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_AbnormalResidualCurrent | INV031 | Inverter 031 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_AbnormalStringPower | INV031 | Inverter 031 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_ActiveIslanding | INV031 | Inverter 031 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_ActivePower | INV031 | Inverter 031 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_ApparentPower | INV031 | Inverter 031 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV031_BuiltPIDOperationAbnormal | INV031 | Inverter 031 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_CabinetOvertemperature | INV031 | Inverter 031 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_CommunicationFailure | INV031 | Inverter 031 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_CommunicationStatus | INV031 | Inverter 031 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_DCArcFault | INV031 | Inverter 031 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_DCCurrent | INV031 | Inverter 031 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_DCInsulationFault | INV031 | Inverter 031 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_DCOvervoltage | INV031 | Inverter 031 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_DCPower | INV031 | Inverter 031 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV031_DCVoltage | INV031 | Inverter 031 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_DailyEnergyYield | INV031 | Inverter 031 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV031_DeviceFault | INV031 | Inverter 031 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_ExternalFanAbnormal | INV031 | Inverter 031 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_FanFailure | INV031 | Inverter 031 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_Faulty | INV031 | Inverter 031 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_FaultyMonitoringUnit | INV031 | Inverter 031 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_FaultyPowerCollector | INV031 | Inverter 031 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_Frequency | INV031 | Inverter 031 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_GeneralFaultTrip | INV031 | Inverter 031 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_Grid | INV031 | Inverter 031 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GridConnectionDeratingInverterInternalCauses | INV031 | Inverter 031 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GridConnectionDeratingPowerRationing | INV031 | Inverter 031 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GridLoss | INV031 | Inverter 031 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GridOverfrequency | INV031 | Inverter 031 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GridOvervoltage | INV031 | Inverter 031 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GridTiedOffGridControllerAbnormal | INV031 | Inverter 031 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GridUnderfrequency | INV031 | Inverter 031 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GridUndervoltage | INV031 | Inverter 031 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GridVoltageImbalance | INV031 | Inverter 031 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_GroundFault | INV031 | Inverter 031 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_HighInputStringVoltageGround | INV031 | Inverter 031 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_HighStringInputVoltage | INV031 | Inverter 031 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_InverterEfficiency | INV031 | Inverter 031 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_InverterGridConnectionStatus | INV031 | Inverter 031 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_InverterOverTemperature | INV031 | Inverter 031 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_InverterRunningStopped | INV031 | Inverter 031 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_InverterStartupShutdownStatus | INV031 | Inverter 031 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_InverterTripHistoryAvailable | INV031 | Inverter 031 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_IslandingDetectionStatus | INV031 | Inverter 031 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_LicenseExpired | INV031 | Inverter 031 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_LockingStatus | INV031 | Inverter 031 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_LowInsulationResistance | INV031 | Inverter 031 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_NormalGridConnection | INV031 | Inverter 031 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_NormalShutdown | INV031 | Inverter 031 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_OffGridOutputOverload | INV031 | Inverter 031 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_OptimizerFault | INV031 | Inverter 031 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_OutputDCComponentOverhigh | INV031 | Inverter 031 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_OutputOvercurrent | INV031 | Inverter 031 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_PVStringLoss | INV031 | Inverter 031 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_PassiveIslanding | INV031 | Inverter 031 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_PeripheralPortShortCircuit | INV031 | Inverter 031 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_PhaseWireShortCircuitedPE | INV031 | Inverter 031 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_PowerCurtailmentStatus | INV031 | Inverter 031 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_PowerFactor | INV031 | Inverter 031 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_PowerLimitationActiveGridCommand | INV031 | Inverter 031 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_ReactivePower | INV031 | Inverter 031 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV031_RemoteOFFStatus | INV031 | Inverter 031 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_Shutdown | INV031 | Inverter 031 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_ShutdownPowerRationing | INV031 | Inverter 031 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_SpotCheck | INV031 | Inverter 031 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_Standby | INV031 | Inverter 031 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_StringCurrentBackfeed | INV031 | Inverter 031 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_StringReverseConnection | INV031 | Inverter 031 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_StringReversePolarity | INV031 | Inverter 031 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_TotalEnergyYield | INV031 | Inverter 031 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV031_TransientACOvervoltage | INV031 | Inverter 031 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_UnstableGridFrequency | INV031 | Inverter 031 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_UpgradeFailed | INV031 | Inverter 031 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV031_WarningActive | INV031 | Inverter 031 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_ACCurrent | INV032 | Inverter 032 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_ACOvervoltage | INV032 | Inverter 032 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_ACUndervoltage | INV032 | Inverter 032 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_ACVoltage | INV032 | Inverter 032 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_AFCISelfCheckFailure | INV032 | Inverter 032 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_AbnormalGrounding | INV032 | Inverter 032 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_AbnormalPVModuleConfiguration | INV032 | Inverter 032 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_AbnormalResidualCurrent | INV032 | Inverter 032 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_AbnormalStringPower | INV032 | Inverter 032 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_ActiveIslanding | INV032 | Inverter 032 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_ActivePower | INV032 | Inverter 032 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_ApparentPower | INV032 | Inverter 032 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV032_BuiltPIDOperationAbnormal | INV032 | Inverter 032 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_CabinetOvertemperature | INV032 | Inverter 032 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_CommunicationFailure | INV032 | Inverter 032 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_CommunicationStatus | INV032 | Inverter 032 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_DCArcFault | INV032 | Inverter 032 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_DCCurrent | INV032 | Inverter 032 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_DCInsulationFault | INV032 | Inverter 032 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_DCOvervoltage | INV032 | Inverter 032 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_DCPower | INV032 | Inverter 032 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV032_DCVoltage | INV032 | Inverter 032 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_DailyEnergyYield | INV032 | Inverter 032 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV032_DeviceFault | INV032 | Inverter 032 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_ExternalFanAbnormal | INV032 | Inverter 032 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_FanFailure | INV032 | Inverter 032 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_Faulty | INV032 | Inverter 032 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_FaultyMonitoringUnit | INV032 | Inverter 032 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_FaultyPowerCollector | INV032 | Inverter 032 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_Frequency | INV032 | Inverter 032 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_GeneralFaultTrip | INV032 | Inverter 032 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_Grid | INV032 | Inverter 032 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GridConnectionDeratingInverterInternalCauses | INV032 | Inverter 032 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GridConnectionDeratingPowerRationing | INV032 | Inverter 032 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GridLoss | INV032 | Inverter 032 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GridOverfrequency | INV032 | Inverter 032 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GridOvervoltage | INV032 | Inverter 032 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GridTiedOffGridControllerAbnormal | INV032 | Inverter 032 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GridUnderfrequency | INV032 | Inverter 032 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GridUndervoltage | INV032 | Inverter 032 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GridVoltageImbalance | INV032 | Inverter 032 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_GroundFault | INV032 | Inverter 032 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_HighInputStringVoltageGround | INV032 | Inverter 032 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_HighStringInputVoltage | INV032 | Inverter 032 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_InverterEfficiency | INV032 | Inverter 032 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_InverterGridConnectionStatus | INV032 | Inverter 032 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_InverterOverTemperature | INV032 | Inverter 032 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_InverterRunningStopped | INV032 | Inverter 032 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_InverterStartupShutdownStatus | INV032 | Inverter 032 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_InverterTripHistoryAvailable | INV032 | Inverter 032 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_IslandingDetectionStatus | INV032 | Inverter 032 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_LicenseExpired | INV032 | Inverter 032 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_LockingStatus | INV032 | Inverter 032 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_LowInsulationResistance | INV032 | Inverter 032 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_NormalGridConnection | INV032 | Inverter 032 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_NormalShutdown | INV032 | Inverter 032 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_OffGridOutputOverload | INV032 | Inverter 032 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_OptimizerFault | INV032 | Inverter 032 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_OutputDCComponentOverhigh | INV032 | Inverter 032 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_OutputOvercurrent | INV032 | Inverter 032 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_PVStringLoss | INV032 | Inverter 032 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_PassiveIslanding | INV032 | Inverter 032 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_PeripheralPortShortCircuit | INV032 | Inverter 032 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_PhaseWireShortCircuitedPE | INV032 | Inverter 032 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_PowerCurtailmentStatus | INV032 | Inverter 032 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_PowerFactor | INV032 | Inverter 032 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_PowerLimitationActiveGridCommand | INV032 | Inverter 032 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_ReactivePower | INV032 | Inverter 032 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV032_RemoteOFFStatus | INV032 | Inverter 032 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_Shutdown | INV032 | Inverter 032 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_ShutdownPowerRationing | INV032 | Inverter 032 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_SpotCheck | INV032 | Inverter 032 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_Standby | INV032 | Inverter 032 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_StringCurrentBackfeed | INV032 | Inverter 032 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_StringReverseConnection | INV032 | Inverter 032 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_StringReversePolarity | INV032 | Inverter 032 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_TotalEnergyYield | INV032 | Inverter 032 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV032_TransientACOvervoltage | INV032 | Inverter 032 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_UnstableGridFrequency | INV032 | Inverter 032 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_UpgradeFailed | INV032 | Inverter 032 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV032_WarningActive | INV032 | Inverter 032 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_ACCurrent | INV033 | Inverter 033 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_ACOvervoltage | INV033 | Inverter 033 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_ACUndervoltage | INV033 | Inverter 033 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_ACVoltage | INV033 | Inverter 033 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_AFCISelfCheckFailure | INV033 | Inverter 033 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_AbnormalGrounding | INV033 | Inverter 033 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_AbnormalPVModuleConfiguration | INV033 | Inverter 033 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_AbnormalResidualCurrent | INV033 | Inverter 033 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_AbnormalStringPower | INV033 | Inverter 033 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_ActiveIslanding | INV033 | Inverter 033 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_ActivePower | INV033 | Inverter 033 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_ApparentPower | INV033 | Inverter 033 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV033_BuiltPIDOperationAbnormal | INV033 | Inverter 033 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_CabinetOvertemperature | INV033 | Inverter 033 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_CommunicationFailure | INV033 | Inverter 033 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_CommunicationStatus | INV033 | Inverter 033 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_DCArcFault | INV033 | Inverter 033 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_DCCurrent | INV033 | Inverter 033 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_DCInsulationFault | INV033 | Inverter 033 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_DCOvervoltage | INV033 | Inverter 033 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_DCPower | INV033 | Inverter 033 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV033_DCVoltage | INV033 | Inverter 033 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_DailyEnergyYield | INV033 | Inverter 033 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV033_DeviceFault | INV033 | Inverter 033 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_ExternalFanAbnormal | INV033 | Inverter 033 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_FanFailure | INV033 | Inverter 033 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_Faulty | INV033 | Inverter 033 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_FaultyMonitoringUnit | INV033 | Inverter 033 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_FaultyPowerCollector | INV033 | Inverter 033 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_Frequency | INV033 | Inverter 033 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_GeneralFaultTrip | INV033 | Inverter 033 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_Grid | INV033 | Inverter 033 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GridConnectionDeratingInverterInternalCauses | INV033 | Inverter 033 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GridConnectionDeratingPowerRationing | INV033 | Inverter 033 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GridLoss | INV033 | Inverter 033 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GridOverfrequency | INV033 | Inverter 033 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GridOvervoltage | INV033 | Inverter 033 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GridTiedOffGridControllerAbnormal | INV033 | Inverter 033 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GridUnderfrequency | INV033 | Inverter 033 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GridUndervoltage | INV033 | Inverter 033 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GridVoltageImbalance | INV033 | Inverter 033 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_GroundFault | INV033 | Inverter 033 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_HighInputStringVoltageGround | INV033 | Inverter 033 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_HighStringInputVoltage | INV033 | Inverter 033 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_InverterEfficiency | INV033 | Inverter 033 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_InverterGridConnectionStatus | INV033 | Inverter 033 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_InverterOverTemperature | INV033 | Inverter 033 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_InverterRunningStopped | INV033 | Inverter 033 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_InverterStartupShutdownStatus | INV033 | Inverter 033 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_InverterTripHistoryAvailable | INV033 | Inverter 033 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_IslandingDetectionStatus | INV033 | Inverter 033 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_LicenseExpired | INV033 | Inverter 033 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_LockingStatus | INV033 | Inverter 033 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_LowInsulationResistance | INV033 | Inverter 033 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_NormalGridConnection | INV033 | Inverter 033 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_NormalShutdown | INV033 | Inverter 033 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_OffGridOutputOverload | INV033 | Inverter 033 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_OptimizerFault | INV033 | Inverter 033 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_OutputDCComponentOverhigh | INV033 | Inverter 033 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_OutputOvercurrent | INV033 | Inverter 033 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_PVStringLoss | INV033 | Inverter 033 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_PassiveIslanding | INV033 | Inverter 033 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_PeripheralPortShortCircuit | INV033 | Inverter 033 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_PhaseWireShortCircuitedPE | INV033 | Inverter 033 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_PowerCurtailmentStatus | INV033 | Inverter 033 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_PowerFactor | INV033 | Inverter 033 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_PowerLimitationActiveGridCommand | INV033 | Inverter 033 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_ReactivePower | INV033 | Inverter 033 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV033_RemoteOFFStatus | INV033 | Inverter 033 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_Shutdown | INV033 | Inverter 033 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_ShutdownPowerRationing | INV033 | Inverter 033 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_SpotCheck | INV033 | Inverter 033 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_Standby | INV033 | Inverter 033 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_StringCurrentBackfeed | INV033 | Inverter 033 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_StringReverseConnection | INV033 | Inverter 033 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_StringReversePolarity | INV033 | Inverter 033 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_TotalEnergyYield | INV033 | Inverter 033 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV033_TransientACOvervoltage | INV033 | Inverter 033 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_UnstableGridFrequency | INV033 | Inverter 033 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_UpgradeFailed | INV033 | Inverter 033 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV033_WarningActive | INV033 | Inverter 033 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_ACCurrent | INV034 | Inverter 034 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_ACOvervoltage | INV034 | Inverter 034 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_ACUndervoltage | INV034 | Inverter 034 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_ACVoltage | INV034 | Inverter 034 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_AFCISelfCheckFailure | INV034 | Inverter 034 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_AbnormalGrounding | INV034 | Inverter 034 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_AbnormalPVModuleConfiguration | INV034 | Inverter 034 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_AbnormalResidualCurrent | INV034 | Inverter 034 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_AbnormalStringPower | INV034 | Inverter 034 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_ActiveIslanding | INV034 | Inverter 034 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_ActivePower | INV034 | Inverter 034 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_ApparentPower | INV034 | Inverter 034 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV034_BuiltPIDOperationAbnormal | INV034 | Inverter 034 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_CabinetOvertemperature | INV034 | Inverter 034 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_CommunicationFailure | INV034 | Inverter 034 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_CommunicationStatus | INV034 | Inverter 034 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_DCArcFault | INV034 | Inverter 034 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_DCCurrent | INV034 | Inverter 034 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_DCInsulationFault | INV034 | Inverter 034 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_DCOvervoltage | INV034 | Inverter 034 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_DCPower | INV034 | Inverter 034 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV034_DCVoltage | INV034 | Inverter 034 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_DailyEnergyYield | INV034 | Inverter 034 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV034_DeviceFault | INV034 | Inverter 034 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_ExternalFanAbnormal | INV034 | Inverter 034 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_FanFailure | INV034 | Inverter 034 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_Faulty | INV034 | Inverter 034 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_FaultyMonitoringUnit | INV034 | Inverter 034 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_FaultyPowerCollector | INV034 | Inverter 034 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_Frequency | INV034 | Inverter 034 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_GeneralFaultTrip | INV034 | Inverter 034 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_Grid | INV034 | Inverter 034 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GridConnectionDeratingInverterInternalCauses | INV034 | Inverter 034 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GridConnectionDeratingPowerRationing | INV034 | Inverter 034 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GridLoss | INV034 | Inverter 034 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GridOverfrequency | INV034 | Inverter 034 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GridOvervoltage | INV034 | Inverter 034 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GridTiedOffGridControllerAbnormal | INV034 | Inverter 034 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GridUnderfrequency | INV034 | Inverter 034 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GridUndervoltage | INV034 | Inverter 034 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GridVoltageImbalance | INV034 | Inverter 034 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_GroundFault | INV034 | Inverter 034 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_HighInputStringVoltageGround | INV034 | Inverter 034 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_HighStringInputVoltage | INV034 | Inverter 034 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_InverterEfficiency | INV034 | Inverter 034 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_InverterGridConnectionStatus | INV034 | Inverter 034 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_InverterOverTemperature | INV034 | Inverter 034 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_InverterRunningStopped | INV034 | Inverter 034 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_InverterStartupShutdownStatus | INV034 | Inverter 034 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_InverterTripHistoryAvailable | INV034 | Inverter 034 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_IslandingDetectionStatus | INV034 | Inverter 034 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_LicenseExpired | INV034 | Inverter 034 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_LockingStatus | INV034 | Inverter 034 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_LowInsulationResistance | INV034 | Inverter 034 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_NormalGridConnection | INV034 | Inverter 034 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_NormalShutdown | INV034 | Inverter 034 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_OffGridOutputOverload | INV034 | Inverter 034 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_OptimizerFault | INV034 | Inverter 034 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_OutputDCComponentOverhigh | INV034 | Inverter 034 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_OutputOvercurrent | INV034 | Inverter 034 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_PVStringLoss | INV034 | Inverter 034 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_PassiveIslanding | INV034 | Inverter 034 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_PeripheralPortShortCircuit | INV034 | Inverter 034 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_PhaseWireShortCircuitedPE | INV034 | Inverter 034 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_PowerCurtailmentStatus | INV034 | Inverter 034 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_PowerFactor | INV034 | Inverter 034 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_PowerLimitationActiveGridCommand | INV034 | Inverter 034 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_ReactivePower | INV034 | Inverter 034 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV034_RemoteOFFStatus | INV034 | Inverter 034 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_Shutdown | INV034 | Inverter 034 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_ShutdownPowerRationing | INV034 | Inverter 034 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_SpotCheck | INV034 | Inverter 034 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_Standby | INV034 | Inverter 034 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_StringCurrentBackfeed | INV034 | Inverter 034 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_StringReverseConnection | INV034 | Inverter 034 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_StringReversePolarity | INV034 | Inverter 034 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_TotalEnergyYield | INV034 | Inverter 034 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV034_TransientACOvervoltage | INV034 | Inverter 034 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_UnstableGridFrequency | INV034 | Inverter 034 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_UpgradeFailed | INV034 | Inverter 034 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV034_WarningActive | INV034 | Inverter 034 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_ACCurrent | INV035 | Inverter 035 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_ACOvervoltage | INV035 | Inverter 035 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_ACUndervoltage | INV035 | Inverter 035 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_ACVoltage | INV035 | Inverter 035 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_AFCISelfCheckFailure | INV035 | Inverter 035 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_AbnormalGrounding | INV035 | Inverter 035 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_AbnormalPVModuleConfiguration | INV035 | Inverter 035 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_AbnormalResidualCurrent | INV035 | Inverter 035 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_AbnormalStringPower | INV035 | Inverter 035 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_ActiveIslanding | INV035 | Inverter 035 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_ActivePower | INV035 | Inverter 035 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_ApparentPower | INV035 | Inverter 035 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV035_BuiltPIDOperationAbnormal | INV035 | Inverter 035 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_CabinetOvertemperature | INV035 | Inverter 035 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_CommunicationFailure | INV035 | Inverter 035 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_CommunicationStatus | INV035 | Inverter 035 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_DCArcFault | INV035 | Inverter 035 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_DCCurrent | INV035 | Inverter 035 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_DCInsulationFault | INV035 | Inverter 035 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_DCOvervoltage | INV035 | Inverter 035 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_DCPower | INV035 | Inverter 035 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV035_DCVoltage | INV035 | Inverter 035 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_DailyEnergyYield | INV035 | Inverter 035 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV035_DeviceFault | INV035 | Inverter 035 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_ExternalFanAbnormal | INV035 | Inverter 035 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_FanFailure | INV035 | Inverter 035 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_Faulty | INV035 | Inverter 035 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_FaultyMonitoringUnit | INV035 | Inverter 035 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_FaultyPowerCollector | INV035 | Inverter 035 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_Frequency | INV035 | Inverter 035 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_GeneralFaultTrip | INV035 | Inverter 035 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_Grid | INV035 | Inverter 035 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GridConnectionDeratingInverterInternalCauses | INV035 | Inverter 035 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GridConnectionDeratingPowerRationing | INV035 | Inverter 035 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GridLoss | INV035 | Inverter 035 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GridOverfrequency | INV035 | Inverter 035 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GridOvervoltage | INV035 | Inverter 035 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GridTiedOffGridControllerAbnormal | INV035 | Inverter 035 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GridUnderfrequency | INV035 | Inverter 035 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GridUndervoltage | INV035 | Inverter 035 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GridVoltageImbalance | INV035 | Inverter 035 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_GroundFault | INV035 | Inverter 035 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_HighInputStringVoltageGround | INV035 | Inverter 035 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_HighStringInputVoltage | INV035 | Inverter 035 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_InverterEfficiency | INV035 | Inverter 035 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_InverterGridConnectionStatus | INV035 | Inverter 035 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_InverterOverTemperature | INV035 | Inverter 035 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_InverterRunningStopped | INV035 | Inverter 035 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_InverterStartupShutdownStatus | INV035 | Inverter 035 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_InverterTripHistoryAvailable | INV035 | Inverter 035 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_IslandingDetectionStatus | INV035 | Inverter 035 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_LicenseExpired | INV035 | Inverter 035 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_LockingStatus | INV035 | Inverter 035 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_LowInsulationResistance | INV035 | Inverter 035 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_NormalGridConnection | INV035 | Inverter 035 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_NormalShutdown | INV035 | Inverter 035 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_OffGridOutputOverload | INV035 | Inverter 035 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_OptimizerFault | INV035 | Inverter 035 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_OutputDCComponentOverhigh | INV035 | Inverter 035 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_OutputOvercurrent | INV035 | Inverter 035 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_PVStringLoss | INV035 | Inverter 035 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_PassiveIslanding | INV035 | Inverter 035 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_PeripheralPortShortCircuit | INV035 | Inverter 035 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_PhaseWireShortCircuitedPE | INV035 | Inverter 035 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_PowerCurtailmentStatus | INV035 | Inverter 035 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_PowerFactor | INV035 | Inverter 035 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_PowerLimitationActiveGridCommand | INV035 | Inverter 035 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_ReactivePower | INV035 | Inverter 035 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV035_RemoteOFFStatus | INV035 | Inverter 035 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_Shutdown | INV035 | Inverter 035 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_ShutdownPowerRationing | INV035 | Inverter 035 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_SpotCheck | INV035 | Inverter 035 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_Standby | INV035 | Inverter 035 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_StringCurrentBackfeed | INV035 | Inverter 035 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_StringReverseConnection | INV035 | Inverter 035 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_StringReversePolarity | INV035 | Inverter 035 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_TotalEnergyYield | INV035 | Inverter 035 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV035_TransientACOvervoltage | INV035 | Inverter 035 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_UnstableGridFrequency | INV035 | Inverter 035 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_UpgradeFailed | INV035 | Inverter 035 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV035_WarningActive | INV035 | Inverter 035 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_ACCurrent | INV036 | Inverter 036 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_ACOvervoltage | INV036 | Inverter 036 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_ACUndervoltage | INV036 | Inverter 036 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_ACVoltage | INV036 | Inverter 036 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_AFCISelfCheckFailure | INV036 | Inverter 036 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_AbnormalGrounding | INV036 | Inverter 036 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_AbnormalPVModuleConfiguration | INV036 | Inverter 036 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_AbnormalResidualCurrent | INV036 | Inverter 036 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_AbnormalStringPower | INV036 | Inverter 036 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_ActiveIslanding | INV036 | Inverter 036 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_ActivePower | INV036 | Inverter 036 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_ApparentPower | INV036 | Inverter 036 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV036_BuiltPIDOperationAbnormal | INV036 | Inverter 036 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_CabinetOvertemperature | INV036 | Inverter 036 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_CommunicationFailure | INV036 | Inverter 036 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_CommunicationStatus | INV036 | Inverter 036 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_DCArcFault | INV036 | Inverter 036 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_DCCurrent | INV036 | Inverter 036 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_DCInsulationFault | INV036 | Inverter 036 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_DCOvervoltage | INV036 | Inverter 036 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_DCPower | INV036 | Inverter 036 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV036_DCVoltage | INV036 | Inverter 036 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_DailyEnergyYield | INV036 | Inverter 036 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV036_DeviceFault | INV036 | Inverter 036 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_ExternalFanAbnormal | INV036 | Inverter 036 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_FanFailure | INV036 | Inverter 036 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_Faulty | INV036 | Inverter 036 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_FaultyMonitoringUnit | INV036 | Inverter 036 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_FaultyPowerCollector | INV036 | Inverter 036 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_Frequency | INV036 | Inverter 036 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_GeneralFaultTrip | INV036 | Inverter 036 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_Grid | INV036 | Inverter 036 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GridConnectionDeratingInverterInternalCauses | INV036 | Inverter 036 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GridConnectionDeratingPowerRationing | INV036 | Inverter 036 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GridLoss | INV036 | Inverter 036 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GridOverfrequency | INV036 | Inverter 036 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GridOvervoltage | INV036 | Inverter 036 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GridTiedOffGridControllerAbnormal | INV036 | Inverter 036 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GridUnderfrequency | INV036 | Inverter 036 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GridUndervoltage | INV036 | Inverter 036 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GridVoltageImbalance | INV036 | Inverter 036 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_GroundFault | INV036 | Inverter 036 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_HighInputStringVoltageGround | INV036 | Inverter 036 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_HighStringInputVoltage | INV036 | Inverter 036 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_InverterEfficiency | INV036 | Inverter 036 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_InverterGridConnectionStatus | INV036 | Inverter 036 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_InverterOverTemperature | INV036 | Inverter 036 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_InverterRunningStopped | INV036 | Inverter 036 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_InverterStartupShutdownStatus | INV036 | Inverter 036 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_InverterTripHistoryAvailable | INV036 | Inverter 036 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_IslandingDetectionStatus | INV036 | Inverter 036 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_LicenseExpired | INV036 | Inverter 036 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_LockingStatus | INV036 | Inverter 036 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_LowInsulationResistance | INV036 | Inverter 036 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_NormalGridConnection | INV036 | Inverter 036 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_NormalShutdown | INV036 | Inverter 036 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_OffGridOutputOverload | INV036 | Inverter 036 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_OptimizerFault | INV036 | Inverter 036 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_OutputDCComponentOverhigh | INV036 | Inverter 036 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_OutputOvercurrent | INV036 | Inverter 036 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_PVStringLoss | INV036 | Inverter 036 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_PassiveIslanding | INV036 | Inverter 036 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_PeripheralPortShortCircuit | INV036 | Inverter 036 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_PhaseWireShortCircuitedPE | INV036 | Inverter 036 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_PowerCurtailmentStatus | INV036 | Inverter 036 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_PowerFactor | INV036 | Inverter 036 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_PowerLimitationActiveGridCommand | INV036 | Inverter 036 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_ReactivePower | INV036 | Inverter 036 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV036_RemoteOFFStatus | INV036 | Inverter 036 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_Shutdown | INV036 | Inverter 036 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_ShutdownPowerRationing | INV036 | Inverter 036 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_SpotCheck | INV036 | Inverter 036 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_Standby | INV036 | Inverter 036 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_StringCurrentBackfeed | INV036 | Inverter 036 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_StringReverseConnection | INV036 | Inverter 036 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_StringReversePolarity | INV036 | Inverter 036 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_TotalEnergyYield | INV036 | Inverter 036 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV036_TransientACOvervoltage | INV036 | Inverter 036 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_UnstableGridFrequency | INV036 | Inverter 036 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_UpgradeFailed | INV036 | Inverter 036 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV036_WarningActive | INV036 | Inverter 036 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_ACCurrent | INV037 | Inverter 037 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_ACOvervoltage | INV037 | Inverter 037 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_ACUndervoltage | INV037 | Inverter 037 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_ACVoltage | INV037 | Inverter 037 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_AFCISelfCheckFailure | INV037 | Inverter 037 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_AbnormalGrounding | INV037 | Inverter 037 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_AbnormalPVModuleConfiguration | INV037 | Inverter 037 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_AbnormalResidualCurrent | INV037 | Inverter 037 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_AbnormalStringPower | INV037 | Inverter 037 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_ActiveIslanding | INV037 | Inverter 037 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_ActivePower | INV037 | Inverter 037 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_ApparentPower | INV037 | Inverter 037 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV037_BuiltPIDOperationAbnormal | INV037 | Inverter 037 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_CabinetOvertemperature | INV037 | Inverter 037 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_CommunicationFailure | INV037 | Inverter 037 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_CommunicationStatus | INV037 | Inverter 037 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_DCArcFault | INV037 | Inverter 037 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_DCCurrent | INV037 | Inverter 037 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_DCInsulationFault | INV037 | Inverter 037 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_DCOvervoltage | INV037 | Inverter 037 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_DCPower | INV037 | Inverter 037 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV037_DCVoltage | INV037 | Inverter 037 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_DailyEnergyYield | INV037 | Inverter 037 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV037_DeviceFault | INV037 | Inverter 037 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_ExternalFanAbnormal | INV037 | Inverter 037 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_FanFailure | INV037 | Inverter 037 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_Faulty | INV037 | Inverter 037 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_FaultyMonitoringUnit | INV037 | Inverter 037 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_FaultyPowerCollector | INV037 | Inverter 037 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_Frequency | INV037 | Inverter 037 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_GeneralFaultTrip | INV037 | Inverter 037 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_Grid | INV037 | Inverter 037 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GridConnectionDeratingInverterInternalCauses | INV037 | Inverter 037 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GridConnectionDeratingPowerRationing | INV037 | Inverter 037 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GridLoss | INV037 | Inverter 037 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GridOverfrequency | INV037 | Inverter 037 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GridOvervoltage | INV037 | Inverter 037 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GridTiedOffGridControllerAbnormal | INV037 | Inverter 037 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GridUnderfrequency | INV037 | Inverter 037 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GridUndervoltage | INV037 | Inverter 037 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GridVoltageImbalance | INV037 | Inverter 037 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_GroundFault | INV037 | Inverter 037 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_HighInputStringVoltageGround | INV037 | Inverter 037 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_HighStringInputVoltage | INV037 | Inverter 037 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_InverterEfficiency | INV037 | Inverter 037 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_InverterGridConnectionStatus | INV037 | Inverter 037 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_InverterOverTemperature | INV037 | Inverter 037 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_InverterRunningStopped | INV037 | Inverter 037 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_InverterStartupShutdownStatus | INV037 | Inverter 037 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_InverterTripHistoryAvailable | INV037 | Inverter 037 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_IslandingDetectionStatus | INV037 | Inverter 037 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_LicenseExpired | INV037 | Inverter 037 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_LockingStatus | INV037 | Inverter 037 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_LowInsulationResistance | INV037 | Inverter 037 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_NormalGridConnection | INV037 | Inverter 037 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_NormalShutdown | INV037 | Inverter 037 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_OffGridOutputOverload | INV037 | Inverter 037 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_OptimizerFault | INV037 | Inverter 037 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_OutputDCComponentOverhigh | INV037 | Inverter 037 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_OutputOvercurrent | INV037 | Inverter 037 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_PVStringLoss | INV037 | Inverter 037 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_PassiveIslanding | INV037 | Inverter 037 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_PeripheralPortShortCircuit | INV037 | Inverter 037 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_PhaseWireShortCircuitedPE | INV037 | Inverter 037 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_PowerCurtailmentStatus | INV037 | Inverter 037 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_PowerFactor | INV037 | Inverter 037 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_PowerLimitationActiveGridCommand | INV037 | Inverter 037 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_ReactivePower | INV037 | Inverter 037 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV037_RemoteOFFStatus | INV037 | Inverter 037 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_Shutdown | INV037 | Inverter 037 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_ShutdownPowerRationing | INV037 | Inverter 037 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_SpotCheck | INV037 | Inverter 037 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_Standby | INV037 | Inverter 037 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_StringCurrentBackfeed | INV037 | Inverter 037 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_StringReverseConnection | INV037 | Inverter 037 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_StringReversePolarity | INV037 | Inverter 037 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_TotalEnergyYield | INV037 | Inverter 037 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV037_TransientACOvervoltage | INV037 | Inverter 037 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_UnstableGridFrequency | INV037 | Inverter 037 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_UpgradeFailed | INV037 | Inverter 037 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV037_WarningActive | INV037 | Inverter 037 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_ACCurrent | INV038 | Inverter 038 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_ACOvervoltage | INV038 | Inverter 038 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_ACUndervoltage | INV038 | Inverter 038 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_ACVoltage | INV038 | Inverter 038 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_AFCISelfCheckFailure | INV038 | Inverter 038 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_AbnormalGrounding | INV038 | Inverter 038 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_AbnormalPVModuleConfiguration | INV038 | Inverter 038 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_AbnormalResidualCurrent | INV038 | Inverter 038 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_AbnormalStringPower | INV038 | Inverter 038 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_ActiveIslanding | INV038 | Inverter 038 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_ActivePower | INV038 | Inverter 038 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_ApparentPower | INV038 | Inverter 038 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV038_BuiltPIDOperationAbnormal | INV038 | Inverter 038 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_CabinetOvertemperature | INV038 | Inverter 038 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_CommunicationFailure | INV038 | Inverter 038 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_CommunicationStatus | INV038 | Inverter 038 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_DCArcFault | INV038 | Inverter 038 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_DCCurrent | INV038 | Inverter 038 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_DCInsulationFault | INV038 | Inverter 038 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_DCOvervoltage | INV038 | Inverter 038 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_DCPower | INV038 | Inverter 038 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV038_DCVoltage | INV038 | Inverter 038 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_DailyEnergyYield | INV038 | Inverter 038 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV038_DeviceFault | INV038 | Inverter 038 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_ExternalFanAbnormal | INV038 | Inverter 038 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_FanFailure | INV038 | Inverter 038 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_Faulty | INV038 | Inverter 038 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_FaultyMonitoringUnit | INV038 | Inverter 038 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_FaultyPowerCollector | INV038 | Inverter 038 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_Frequency | INV038 | Inverter 038 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_GeneralFaultTrip | INV038 | Inverter 038 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_Grid | INV038 | Inverter 038 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GridConnectionDeratingInverterInternalCauses | INV038 | Inverter 038 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GridConnectionDeratingPowerRationing | INV038 | Inverter 038 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GridLoss | INV038 | Inverter 038 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GridOverfrequency | INV038 | Inverter 038 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GridOvervoltage | INV038 | Inverter 038 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GridTiedOffGridControllerAbnormal | INV038 | Inverter 038 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GridUnderfrequency | INV038 | Inverter 038 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GridUndervoltage | INV038 | Inverter 038 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GridVoltageImbalance | INV038 | Inverter 038 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_GroundFault | INV038 | Inverter 038 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_HighInputStringVoltageGround | INV038 | Inverter 038 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_HighStringInputVoltage | INV038 | Inverter 038 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_InverterEfficiency | INV038 | Inverter 038 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_InverterGridConnectionStatus | INV038 | Inverter 038 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_InverterOverTemperature | INV038 | Inverter 038 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_InverterRunningStopped | INV038 | Inverter 038 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_InverterStartupShutdownStatus | INV038 | Inverter 038 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_InverterTripHistoryAvailable | INV038 | Inverter 038 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_IslandingDetectionStatus | INV038 | Inverter 038 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_LicenseExpired | INV038 | Inverter 038 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_LockingStatus | INV038 | Inverter 038 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_LowInsulationResistance | INV038 | Inverter 038 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_NormalGridConnection | INV038 | Inverter 038 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_NormalShutdown | INV038 | Inverter 038 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_OffGridOutputOverload | INV038 | Inverter 038 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_OptimizerFault | INV038 | Inverter 038 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_OutputDCComponentOverhigh | INV038 | Inverter 038 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_OutputOvercurrent | INV038 | Inverter 038 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_PVStringLoss | INV038 | Inverter 038 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_PassiveIslanding | INV038 | Inverter 038 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_PeripheralPortShortCircuit | INV038 | Inverter 038 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_PhaseWireShortCircuitedPE | INV038 | Inverter 038 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_PowerCurtailmentStatus | INV038 | Inverter 038 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_PowerFactor | INV038 | Inverter 038 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_PowerLimitationActiveGridCommand | INV038 | Inverter 038 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_ReactivePower | INV038 | Inverter 038 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV038_RemoteOFFStatus | INV038 | Inverter 038 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_Shutdown | INV038 | Inverter 038 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_ShutdownPowerRationing | INV038 | Inverter 038 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_SpotCheck | INV038 | Inverter 038 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_Standby | INV038 | Inverter 038 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_StringCurrentBackfeed | INV038 | Inverter 038 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_StringReverseConnection | INV038 | Inverter 038 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_StringReversePolarity | INV038 | Inverter 038 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_TotalEnergyYield | INV038 | Inverter 038 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV038_TransientACOvervoltage | INV038 | Inverter 038 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_UnstableGridFrequency | INV038 | Inverter 038 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_UpgradeFailed | INV038 | Inverter 038 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV038_WarningActive | INV038 | Inverter 038 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_ACCurrent | INV039 | Inverter 039 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_ACOvervoltage | INV039 | Inverter 039 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_ACUndervoltage | INV039 | Inverter 039 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_ACVoltage | INV039 | Inverter 039 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_AFCISelfCheckFailure | INV039 | Inverter 039 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_AbnormalGrounding | INV039 | Inverter 039 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_AbnormalPVModuleConfiguration | INV039 | Inverter 039 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_AbnormalResidualCurrent | INV039 | Inverter 039 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_AbnormalStringPower | INV039 | Inverter 039 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_ActiveIslanding | INV039 | Inverter 039 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_ActivePower | INV039 | Inverter 039 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_ApparentPower | INV039 | Inverter 039 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV039_BuiltPIDOperationAbnormal | INV039 | Inverter 039 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_CabinetOvertemperature | INV039 | Inverter 039 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_CommunicationFailure | INV039 | Inverter 039 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_CommunicationStatus | INV039 | Inverter 039 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_DCArcFault | INV039 | Inverter 039 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_DCCurrent | INV039 | Inverter 039 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_DCInsulationFault | INV039 | Inverter 039 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_DCOvervoltage | INV039 | Inverter 039 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_DCPower | INV039 | Inverter 039 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV039_DCVoltage | INV039 | Inverter 039 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_DailyEnergyYield | INV039 | Inverter 039 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV039_DeviceFault | INV039 | Inverter 039 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_ExternalFanAbnormal | INV039 | Inverter 039 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_FanFailure | INV039 | Inverter 039 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_Faulty | INV039 | Inverter 039 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_FaultyMonitoringUnit | INV039 | Inverter 039 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_FaultyPowerCollector | INV039 | Inverter 039 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_Frequency | INV039 | Inverter 039 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_GeneralFaultTrip | INV039 | Inverter 039 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_Grid | INV039 | Inverter 039 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GridConnectionDeratingInverterInternalCauses | INV039 | Inverter 039 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GridConnectionDeratingPowerRationing | INV039 | Inverter 039 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GridLoss | INV039 | Inverter 039 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GridOverfrequency | INV039 | Inverter 039 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GridOvervoltage | INV039 | Inverter 039 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GridTiedOffGridControllerAbnormal | INV039 | Inverter 039 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GridUnderfrequency | INV039 | Inverter 039 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GridUndervoltage | INV039 | Inverter 039 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GridVoltageImbalance | INV039 | Inverter 039 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_GroundFault | INV039 | Inverter 039 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_HighInputStringVoltageGround | INV039 | Inverter 039 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_HighStringInputVoltage | INV039 | Inverter 039 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_InverterEfficiency | INV039 | Inverter 039 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_InverterGridConnectionStatus | INV039 | Inverter 039 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_InverterOverTemperature | INV039 | Inverter 039 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_InverterRunningStopped | INV039 | Inverter 039 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_InverterStartupShutdownStatus | INV039 | Inverter 039 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_InverterTripHistoryAvailable | INV039 | Inverter 039 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_IslandingDetectionStatus | INV039 | Inverter 039 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_LicenseExpired | INV039 | Inverter 039 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_LockingStatus | INV039 | Inverter 039 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_LowInsulationResistance | INV039 | Inverter 039 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_NormalGridConnection | INV039 | Inverter 039 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_NormalShutdown | INV039 | Inverter 039 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_OffGridOutputOverload | INV039 | Inverter 039 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_OptimizerFault | INV039 | Inverter 039 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_OutputDCComponentOverhigh | INV039 | Inverter 039 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_OutputOvercurrent | INV039 | Inverter 039 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_PVStringLoss | INV039 | Inverter 039 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_PassiveIslanding | INV039 | Inverter 039 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_PeripheralPortShortCircuit | INV039 | Inverter 039 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_PhaseWireShortCircuitedPE | INV039 | Inverter 039 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_PowerCurtailmentStatus | INV039 | Inverter 039 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_PowerFactor | INV039 | Inverter 039 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_PowerLimitationActiveGridCommand | INV039 | Inverter 039 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_ReactivePower | INV039 | Inverter 039 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV039_RemoteOFFStatus | INV039 | Inverter 039 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_Shutdown | INV039 | Inverter 039 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_ShutdownPowerRationing | INV039 | Inverter 039 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_SpotCheck | INV039 | Inverter 039 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_Standby | INV039 | Inverter 039 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_StringCurrentBackfeed | INV039 | Inverter 039 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_StringReverseConnection | INV039 | Inverter 039 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_StringReversePolarity | INV039 | Inverter 039 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_TotalEnergyYield | INV039 | Inverter 039 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV039_TransientACOvervoltage | INV039 | Inverter 039 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_UnstableGridFrequency | INV039 | Inverter 039 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_UpgradeFailed | INV039 | Inverter 039 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV039_WarningActive | INV039 | Inverter 039 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_ACCurrent | INV040 | Inverter 040 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_ACOvervoltage | INV040 | Inverter 040 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_ACUndervoltage | INV040 | Inverter 040 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_ACVoltage | INV040 | Inverter 040 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_AFCISelfCheckFailure | INV040 | Inverter 040 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_AbnormalGrounding | INV040 | Inverter 040 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_AbnormalPVModuleConfiguration | INV040 | Inverter 040 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_AbnormalResidualCurrent | INV040 | Inverter 040 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_AbnormalStringPower | INV040 | Inverter 040 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_ActiveIslanding | INV040 | Inverter 040 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_ActivePower | INV040 | Inverter 040 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_ApparentPower | INV040 | Inverter 040 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV040_BuiltPIDOperationAbnormal | INV040 | Inverter 040 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_CabinetOvertemperature | INV040 | Inverter 040 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_CommunicationFailure | INV040 | Inverter 040 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_CommunicationStatus | INV040 | Inverter 040 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_DCArcFault | INV040 | Inverter 040 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_DCCurrent | INV040 | Inverter 040 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_DCInsulationFault | INV040 | Inverter 040 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_DCOvervoltage | INV040 | Inverter 040 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_DCPower | INV040 | Inverter 040 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV040_DCVoltage | INV040 | Inverter 040 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_DailyEnergyYield | INV040 | Inverter 040 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV040_DeviceFault | INV040 | Inverter 040 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_ExternalFanAbnormal | INV040 | Inverter 040 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_FanFailure | INV040 | Inverter 040 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_Faulty | INV040 | Inverter 040 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_FaultyMonitoringUnit | INV040 | Inverter 040 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_FaultyPowerCollector | INV040 | Inverter 040 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_Frequency | INV040 | Inverter 040 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_GeneralFaultTrip | INV040 | Inverter 040 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_Grid | INV040 | Inverter 040 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GridConnectionDeratingInverterInternalCauses | INV040 | Inverter 040 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GridConnectionDeratingPowerRationing | INV040 | Inverter 040 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GridLoss | INV040 | Inverter 040 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GridOverfrequency | INV040 | Inverter 040 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GridOvervoltage | INV040 | Inverter 040 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GridTiedOffGridControllerAbnormal | INV040 | Inverter 040 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GridUnderfrequency | INV040 | Inverter 040 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GridUndervoltage | INV040 | Inverter 040 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GridVoltageImbalance | INV040 | Inverter 040 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_GroundFault | INV040 | Inverter 040 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_HighInputStringVoltageGround | INV040 | Inverter 040 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_HighStringInputVoltage | INV040 | Inverter 040 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_InverterEfficiency | INV040 | Inverter 040 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_InverterGridConnectionStatus | INV040 | Inverter 040 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_InverterOverTemperature | INV040 | Inverter 040 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_InverterRunningStopped | INV040 | Inverter 040 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_InverterStartupShutdownStatus | INV040 | Inverter 040 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_InverterTripHistoryAvailable | INV040 | Inverter 040 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_IslandingDetectionStatus | INV040 | Inverter 040 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_LicenseExpired | INV040 | Inverter 040 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_LockingStatus | INV040 | Inverter 040 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_LowInsulationResistance | INV040 | Inverter 040 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_NormalGridConnection | INV040 | Inverter 040 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_NormalShutdown | INV040 | Inverter 040 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_OffGridOutputOverload | INV040 | Inverter 040 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_OptimizerFault | INV040 | Inverter 040 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_OutputDCComponentOverhigh | INV040 | Inverter 040 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_OutputOvercurrent | INV040 | Inverter 040 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_PVStringLoss | INV040 | Inverter 040 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_PassiveIslanding | INV040 | Inverter 040 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_PeripheralPortShortCircuit | INV040 | Inverter 040 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_PhaseWireShortCircuitedPE | INV040 | Inverter 040 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_PowerCurtailmentStatus | INV040 | Inverter 040 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_PowerFactor | INV040 | Inverter 040 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_PowerLimitationActiveGridCommand | INV040 | Inverter 040 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_ReactivePower | INV040 | Inverter 040 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV040_RemoteOFFStatus | INV040 | Inverter 040 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_Shutdown | INV040 | Inverter 040 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_ShutdownPowerRationing | INV040 | Inverter 040 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_SpotCheck | INV040 | Inverter 040 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_Standby | INV040 | Inverter 040 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_StringCurrentBackfeed | INV040 | Inverter 040 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_StringReverseConnection | INV040 | Inverter 040 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_StringReversePolarity | INV040 | Inverter 040 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_TotalEnergyYield | INV040 | Inverter 040 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV040_TransientACOvervoltage | INV040 | Inverter 040 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_UnstableGridFrequency | INV040 | Inverter 040 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_UpgradeFailed | INV040 | Inverter 040 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV040_WarningActive | INV040 | Inverter 040 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_ACCurrent | INV041 | Inverter 041 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_ACOvervoltage | INV041 | Inverter 041 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_ACUndervoltage | INV041 | Inverter 041 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_ACVoltage | INV041 | Inverter 041 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_AFCISelfCheckFailure | INV041 | Inverter 041 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_AbnormalGrounding | INV041 | Inverter 041 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_AbnormalPVModuleConfiguration | INV041 | Inverter 041 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_AbnormalResidualCurrent | INV041 | Inverter 041 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_AbnormalStringPower | INV041 | Inverter 041 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_ActiveIslanding | INV041 | Inverter 041 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_ActivePower | INV041 | Inverter 041 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_ApparentPower | INV041 | Inverter 041 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV041_BuiltPIDOperationAbnormal | INV041 | Inverter 041 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_CabinetOvertemperature | INV041 | Inverter 041 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_CommunicationFailure | INV041 | Inverter 041 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_CommunicationStatus | INV041 | Inverter 041 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_DCArcFault | INV041 | Inverter 041 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_DCCurrent | INV041 | Inverter 041 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_DCInsulationFault | INV041 | Inverter 041 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_DCOvervoltage | INV041 | Inverter 041 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_DCPower | INV041 | Inverter 041 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV041_DCVoltage | INV041 | Inverter 041 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_DailyEnergyYield | INV041 | Inverter 041 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV041_DeviceFault | INV041 | Inverter 041 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_ExternalFanAbnormal | INV041 | Inverter 041 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_FanFailure | INV041 | Inverter 041 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_Faulty | INV041 | Inverter 041 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_FaultyMonitoringUnit | INV041 | Inverter 041 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_FaultyPowerCollector | INV041 | Inverter 041 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_Frequency | INV041 | Inverter 041 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_GeneralFaultTrip | INV041 | Inverter 041 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_Grid | INV041 | Inverter 041 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GridConnectionDeratingInverterInternalCauses | INV041 | Inverter 041 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GridConnectionDeratingPowerRationing | INV041 | Inverter 041 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GridLoss | INV041 | Inverter 041 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GridOverfrequency | INV041 | Inverter 041 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GridOvervoltage | INV041 | Inverter 041 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GridTiedOffGridControllerAbnormal | INV041 | Inverter 041 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GridUnderfrequency | INV041 | Inverter 041 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GridUndervoltage | INV041 | Inverter 041 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GridVoltageImbalance | INV041 | Inverter 041 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_GroundFault | INV041 | Inverter 041 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_HighInputStringVoltageGround | INV041 | Inverter 041 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_HighStringInputVoltage | INV041 | Inverter 041 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_InverterEfficiency | INV041 | Inverter 041 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_InverterGridConnectionStatus | INV041 | Inverter 041 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_InverterOverTemperature | INV041 | Inverter 041 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_InverterRunningStopped | INV041 | Inverter 041 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_InverterStartupShutdownStatus | INV041 | Inverter 041 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_InverterTripHistoryAvailable | INV041 | Inverter 041 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_IslandingDetectionStatus | INV041 | Inverter 041 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_LicenseExpired | INV041 | Inverter 041 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_LockingStatus | INV041 | Inverter 041 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_LowInsulationResistance | INV041 | Inverter 041 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_NormalGridConnection | INV041 | Inverter 041 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_NormalShutdown | INV041 | Inverter 041 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_OffGridOutputOverload | INV041 | Inverter 041 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_OptimizerFault | INV041 | Inverter 041 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_OutputDCComponentOverhigh | INV041 | Inverter 041 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_OutputOvercurrent | INV041 | Inverter 041 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_PVStringLoss | INV041 | Inverter 041 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_PassiveIslanding | INV041 | Inverter 041 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_PeripheralPortShortCircuit | INV041 | Inverter 041 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_PhaseWireShortCircuitedPE | INV041 | Inverter 041 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_PowerCurtailmentStatus | INV041 | Inverter 041 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_PowerFactor | INV041 | Inverter 041 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_PowerLimitationActiveGridCommand | INV041 | Inverter 041 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_ReactivePower | INV041 | Inverter 041 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV041_RemoteOFFStatus | INV041 | Inverter 041 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_Shutdown | INV041 | Inverter 041 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_ShutdownPowerRationing | INV041 | Inverter 041 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_SpotCheck | INV041 | Inverter 041 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_Standby | INV041 | Inverter 041 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_StringCurrentBackfeed | INV041 | Inverter 041 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_StringReverseConnection | INV041 | Inverter 041 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_StringReversePolarity | INV041 | Inverter 041 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_TotalEnergyYield | INV041 | Inverter 041 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV041_TransientACOvervoltage | INV041 | Inverter 041 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_UnstableGridFrequency | INV041 | Inverter 041 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_UpgradeFailed | INV041 | Inverter 041 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV041_WarningActive | INV041 | Inverter 041 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_ACCurrent | INV042 | Inverter 042 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_ACOvervoltage | INV042 | Inverter 042 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_ACUndervoltage | INV042 | Inverter 042 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_ACVoltage | INV042 | Inverter 042 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_AFCISelfCheckFailure | INV042 | Inverter 042 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_AbnormalGrounding | INV042 | Inverter 042 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_AbnormalPVModuleConfiguration | INV042 | Inverter 042 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_AbnormalResidualCurrent | INV042 | Inverter 042 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_AbnormalStringPower | INV042 | Inverter 042 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_ActiveIslanding | INV042 | Inverter 042 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_ActivePower | INV042 | Inverter 042 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_ApparentPower | INV042 | Inverter 042 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV042_BuiltPIDOperationAbnormal | INV042 | Inverter 042 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_CabinetOvertemperature | INV042 | Inverter 042 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_CommunicationFailure | INV042 | Inverter 042 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_CommunicationStatus | INV042 | Inverter 042 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_DCArcFault | INV042 | Inverter 042 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_DCCurrent | INV042 | Inverter 042 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_DCInsulationFault | INV042 | Inverter 042 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_DCOvervoltage | INV042 | Inverter 042 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_DCPower | INV042 | Inverter 042 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV042_DCVoltage | INV042 | Inverter 042 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_DailyEnergyYield | INV042 | Inverter 042 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV042_DeviceFault | INV042 | Inverter 042 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_ExternalFanAbnormal | INV042 | Inverter 042 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_FanFailure | INV042 | Inverter 042 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_Faulty | INV042 | Inverter 042 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_FaultyMonitoringUnit | INV042 | Inverter 042 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_FaultyPowerCollector | INV042 | Inverter 042 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_Frequency | INV042 | Inverter 042 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_GeneralFaultTrip | INV042 | Inverter 042 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_Grid | INV042 | Inverter 042 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GridConnectionDeratingInverterInternalCauses | INV042 | Inverter 042 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GridConnectionDeratingPowerRationing | INV042 | Inverter 042 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GridLoss | INV042 | Inverter 042 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GridOverfrequency | INV042 | Inverter 042 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GridOvervoltage | INV042 | Inverter 042 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GridTiedOffGridControllerAbnormal | INV042 | Inverter 042 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GridUnderfrequency | INV042 | Inverter 042 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GridUndervoltage | INV042 | Inverter 042 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GridVoltageImbalance | INV042 | Inverter 042 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_GroundFault | INV042 | Inverter 042 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_HighInputStringVoltageGround | INV042 | Inverter 042 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_HighStringInputVoltage | INV042 | Inverter 042 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_InverterEfficiency | INV042 | Inverter 042 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_InverterGridConnectionStatus | INV042 | Inverter 042 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_InverterOverTemperature | INV042 | Inverter 042 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_InverterRunningStopped | INV042 | Inverter 042 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_InverterStartupShutdownStatus | INV042 | Inverter 042 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_InverterTripHistoryAvailable | INV042 | Inverter 042 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_IslandingDetectionStatus | INV042 | Inverter 042 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_LicenseExpired | INV042 | Inverter 042 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_LockingStatus | INV042 | Inverter 042 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_LowInsulationResistance | INV042 | Inverter 042 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_NormalGridConnection | INV042 | Inverter 042 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_NormalShutdown | INV042 | Inverter 042 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_OffGridOutputOverload | INV042 | Inverter 042 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_OptimizerFault | INV042 | Inverter 042 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_OutputDCComponentOverhigh | INV042 | Inverter 042 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_OutputOvercurrent | INV042 | Inverter 042 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_PVStringLoss | INV042 | Inverter 042 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_PassiveIslanding | INV042 | Inverter 042 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_PeripheralPortShortCircuit | INV042 | Inverter 042 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_PhaseWireShortCircuitedPE | INV042 | Inverter 042 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_PowerCurtailmentStatus | INV042 | Inverter 042 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_PowerFactor | INV042 | Inverter 042 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_PowerLimitationActiveGridCommand | INV042 | Inverter 042 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_ReactivePower | INV042 | Inverter 042 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV042_RemoteOFFStatus | INV042 | Inverter 042 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_Shutdown | INV042 | Inverter 042 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_ShutdownPowerRationing | INV042 | Inverter 042 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_SpotCheck | INV042 | Inverter 042 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_Standby | INV042 | Inverter 042 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_StringCurrentBackfeed | INV042 | Inverter 042 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_StringReverseConnection | INV042 | Inverter 042 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_StringReversePolarity | INV042 | Inverter 042 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_TotalEnergyYield | INV042 | Inverter 042 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV042_TransientACOvervoltage | INV042 | Inverter 042 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_UnstableGridFrequency | INV042 | Inverter 042 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_UpgradeFailed | INV042 | Inverter 042 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV042_WarningActive | INV042 | Inverter 042 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_ACCurrent | INV043 | Inverter 043 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_ACOvervoltage | INV043 | Inverter 043 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_ACUndervoltage | INV043 | Inverter 043 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_ACVoltage | INV043 | Inverter 043 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_AFCISelfCheckFailure | INV043 | Inverter 043 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_AbnormalGrounding | INV043 | Inverter 043 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_AbnormalPVModuleConfiguration | INV043 | Inverter 043 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_AbnormalResidualCurrent | INV043 | Inverter 043 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_AbnormalStringPower | INV043 | Inverter 043 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_ActiveIslanding | INV043 | Inverter 043 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_ActivePower | INV043 | Inverter 043 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_ApparentPower | INV043 | Inverter 043 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV043_BuiltPIDOperationAbnormal | INV043 | Inverter 043 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_CabinetOvertemperature | INV043 | Inverter 043 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_CommunicationFailure | INV043 | Inverter 043 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_CommunicationStatus | INV043 | Inverter 043 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_DCArcFault | INV043 | Inverter 043 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_DCCurrent | INV043 | Inverter 043 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_DCInsulationFault | INV043 | Inverter 043 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_DCOvervoltage | INV043 | Inverter 043 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_DCPower | INV043 | Inverter 043 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV043_DCVoltage | INV043 | Inverter 043 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_DailyEnergyYield | INV043 | Inverter 043 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV043_DeviceFault | INV043 | Inverter 043 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_ExternalFanAbnormal | INV043 | Inverter 043 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_FanFailure | INV043 | Inverter 043 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_Faulty | INV043 | Inverter 043 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_FaultyMonitoringUnit | INV043 | Inverter 043 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_FaultyPowerCollector | INV043 | Inverter 043 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_Frequency | INV043 | Inverter 043 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_GeneralFaultTrip | INV043 | Inverter 043 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_Grid | INV043 | Inverter 043 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GridConnectionDeratingInverterInternalCauses | INV043 | Inverter 043 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GridConnectionDeratingPowerRationing | INV043 | Inverter 043 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GridLoss | INV043 | Inverter 043 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GridOverfrequency | INV043 | Inverter 043 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GridOvervoltage | INV043 | Inverter 043 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GridTiedOffGridControllerAbnormal | INV043 | Inverter 043 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GridUnderfrequency | INV043 | Inverter 043 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GridUndervoltage | INV043 | Inverter 043 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GridVoltageImbalance | INV043 | Inverter 043 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_GroundFault | INV043 | Inverter 043 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_HighInputStringVoltageGround | INV043 | Inverter 043 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_HighStringInputVoltage | INV043 | Inverter 043 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_InverterEfficiency | INV043 | Inverter 043 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_InverterGridConnectionStatus | INV043 | Inverter 043 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_InverterOverTemperature | INV043 | Inverter 043 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_InverterRunningStopped | INV043 | Inverter 043 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_InverterStartupShutdownStatus | INV043 | Inverter 043 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_InverterTripHistoryAvailable | INV043 | Inverter 043 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_IslandingDetectionStatus | INV043 | Inverter 043 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_LicenseExpired | INV043 | Inverter 043 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_LockingStatus | INV043 | Inverter 043 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_LowInsulationResistance | INV043 | Inverter 043 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_NormalGridConnection | INV043 | Inverter 043 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_NormalShutdown | INV043 | Inverter 043 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_OffGridOutputOverload | INV043 | Inverter 043 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_OptimizerFault | INV043 | Inverter 043 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_OutputDCComponentOverhigh | INV043 | Inverter 043 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_OutputOvercurrent | INV043 | Inverter 043 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_PVStringLoss | INV043 | Inverter 043 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_PassiveIslanding | INV043 | Inverter 043 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_PeripheralPortShortCircuit | INV043 | Inverter 043 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_PhaseWireShortCircuitedPE | INV043 | Inverter 043 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_PowerCurtailmentStatus | INV043 | Inverter 043 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_PowerFactor | INV043 | Inverter 043 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_PowerLimitationActiveGridCommand | INV043 | Inverter 043 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_ReactivePower | INV043 | Inverter 043 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV043_RemoteOFFStatus | INV043 | Inverter 043 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_Shutdown | INV043 | Inverter 043 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_ShutdownPowerRationing | INV043 | Inverter 043 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_SpotCheck | INV043 | Inverter 043 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_Standby | INV043 | Inverter 043 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_StringCurrentBackfeed | INV043 | Inverter 043 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_StringReverseConnection | INV043 | Inverter 043 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_StringReversePolarity | INV043 | Inverter 043 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_TotalEnergyYield | INV043 | Inverter 043 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV043_TransientACOvervoltage | INV043 | Inverter 043 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_UnstableGridFrequency | INV043 | Inverter 043 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_UpgradeFailed | INV043 | Inverter 043 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV043_WarningActive | INV043 | Inverter 043 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_ACCurrent | INV044 | Inverter 044 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_ACOvervoltage | INV044 | Inverter 044 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_ACUndervoltage | INV044 | Inverter 044 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_ACVoltage | INV044 | Inverter 044 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_AFCISelfCheckFailure | INV044 | Inverter 044 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_AbnormalGrounding | INV044 | Inverter 044 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_AbnormalPVModuleConfiguration | INV044 | Inverter 044 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_AbnormalResidualCurrent | INV044 | Inverter 044 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_AbnormalStringPower | INV044 | Inverter 044 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_ActiveIslanding | INV044 | Inverter 044 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_ActivePower | INV044 | Inverter 044 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_ApparentPower | INV044 | Inverter 044 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV044_BuiltPIDOperationAbnormal | INV044 | Inverter 044 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_CabinetOvertemperature | INV044 | Inverter 044 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_CommunicationFailure | INV044 | Inverter 044 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_CommunicationStatus | INV044 | Inverter 044 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_DCArcFault | INV044 | Inverter 044 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_DCCurrent | INV044 | Inverter 044 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_DCInsulationFault | INV044 | Inverter 044 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_DCOvervoltage | INV044 | Inverter 044 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_DCPower | INV044 | Inverter 044 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV044_DCVoltage | INV044 | Inverter 044 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_DailyEnergyYield | INV044 | Inverter 044 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV044_DeviceFault | INV044 | Inverter 044 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_ExternalFanAbnormal | INV044 | Inverter 044 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_FanFailure | INV044 | Inverter 044 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_Faulty | INV044 | Inverter 044 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_FaultyMonitoringUnit | INV044 | Inverter 044 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_FaultyPowerCollector | INV044 | Inverter 044 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_Frequency | INV044 | Inverter 044 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_GeneralFaultTrip | INV044 | Inverter 044 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_Grid | INV044 | Inverter 044 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GridConnectionDeratingInverterInternalCauses | INV044 | Inverter 044 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GridConnectionDeratingPowerRationing | INV044 | Inverter 044 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GridLoss | INV044 | Inverter 044 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GridOverfrequency | INV044 | Inverter 044 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GridOvervoltage | INV044 | Inverter 044 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GridTiedOffGridControllerAbnormal | INV044 | Inverter 044 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GridUnderfrequency | INV044 | Inverter 044 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GridUndervoltage | INV044 | Inverter 044 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GridVoltageImbalance | INV044 | Inverter 044 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_GroundFault | INV044 | Inverter 044 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_HighInputStringVoltageGround | INV044 | Inverter 044 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_HighStringInputVoltage | INV044 | Inverter 044 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_InverterEfficiency | INV044 | Inverter 044 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_InverterGridConnectionStatus | INV044 | Inverter 044 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_InverterOverTemperature | INV044 | Inverter 044 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_InverterRunningStopped | INV044 | Inverter 044 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_InverterStartupShutdownStatus | INV044 | Inverter 044 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_InverterTripHistoryAvailable | INV044 | Inverter 044 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_IslandingDetectionStatus | INV044 | Inverter 044 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_LicenseExpired | INV044 | Inverter 044 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_LockingStatus | INV044 | Inverter 044 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_LowInsulationResistance | INV044 | Inverter 044 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_NormalGridConnection | INV044 | Inverter 044 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_NormalShutdown | INV044 | Inverter 044 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_OffGridOutputOverload | INV044 | Inverter 044 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_OptimizerFault | INV044 | Inverter 044 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_OutputDCComponentOverhigh | INV044 | Inverter 044 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_OutputOvercurrent | INV044 | Inverter 044 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_PVStringLoss | INV044 | Inverter 044 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_PassiveIslanding | INV044 | Inverter 044 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_PeripheralPortShortCircuit | INV044 | Inverter 044 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_PhaseWireShortCircuitedPE | INV044 | Inverter 044 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_PowerCurtailmentStatus | INV044 | Inverter 044 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_PowerFactor | INV044 | Inverter 044 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_PowerLimitationActiveGridCommand | INV044 | Inverter 044 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_ReactivePower | INV044 | Inverter 044 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV044_RemoteOFFStatus | INV044 | Inverter 044 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_Shutdown | INV044 | Inverter 044 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_ShutdownPowerRationing | INV044 | Inverter 044 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_SpotCheck | INV044 | Inverter 044 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_Standby | INV044 | Inverter 044 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_StringCurrentBackfeed | INV044 | Inverter 044 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_StringReverseConnection | INV044 | Inverter 044 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_StringReversePolarity | INV044 | Inverter 044 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_TotalEnergyYield | INV044 | Inverter 044 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV044_TransientACOvervoltage | INV044 | Inverter 044 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_UnstableGridFrequency | INV044 | Inverter 044 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_UpgradeFailed | INV044 | Inverter 044 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV044_WarningActive | INV044 | Inverter 044 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_ACCurrent | INV045 | Inverter 045 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_ACOvervoltage | INV045 | Inverter 045 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_ACUndervoltage | INV045 | Inverter 045 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_ACVoltage | INV045 | Inverter 045 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_AFCISelfCheckFailure | INV045 | Inverter 045 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_AbnormalGrounding | INV045 | Inverter 045 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_AbnormalPVModuleConfiguration | INV045 | Inverter 045 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_AbnormalResidualCurrent | INV045 | Inverter 045 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_AbnormalStringPower | INV045 | Inverter 045 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_ActiveIslanding | INV045 | Inverter 045 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_ActivePower | INV045 | Inverter 045 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_ApparentPower | INV045 | Inverter 045 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV045_BuiltPIDOperationAbnormal | INV045 | Inverter 045 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_CabinetOvertemperature | INV045 | Inverter 045 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_CommunicationFailure | INV045 | Inverter 045 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_CommunicationStatus | INV045 | Inverter 045 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_DCArcFault | INV045 | Inverter 045 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_DCCurrent | INV045 | Inverter 045 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_DCInsulationFault | INV045 | Inverter 045 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_DCOvervoltage | INV045 | Inverter 045 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_DCPower | INV045 | Inverter 045 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV045_DCVoltage | INV045 | Inverter 045 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_DailyEnergyYield | INV045 | Inverter 045 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV045_DeviceFault | INV045 | Inverter 045 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_ExternalFanAbnormal | INV045 | Inverter 045 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_FanFailure | INV045 | Inverter 045 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_Faulty | INV045 | Inverter 045 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_FaultyMonitoringUnit | INV045 | Inverter 045 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_FaultyPowerCollector | INV045 | Inverter 045 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_Frequency | INV045 | Inverter 045 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_GeneralFaultTrip | INV045 | Inverter 045 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_Grid | INV045 | Inverter 045 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GridConnectionDeratingInverterInternalCauses | INV045 | Inverter 045 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GridConnectionDeratingPowerRationing | INV045 | Inverter 045 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GridLoss | INV045 | Inverter 045 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GridOverfrequency | INV045 | Inverter 045 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GridOvervoltage | INV045 | Inverter 045 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GridTiedOffGridControllerAbnormal | INV045 | Inverter 045 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GridUnderfrequency | INV045 | Inverter 045 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GridUndervoltage | INV045 | Inverter 045 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GridVoltageImbalance | INV045 | Inverter 045 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_GroundFault | INV045 | Inverter 045 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_HighInputStringVoltageGround | INV045 | Inverter 045 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_HighStringInputVoltage | INV045 | Inverter 045 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_InverterEfficiency | INV045 | Inverter 045 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_InverterGridConnectionStatus | INV045 | Inverter 045 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_InverterOverTemperature | INV045 | Inverter 045 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_InverterRunningStopped | INV045 | Inverter 045 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_InverterStartupShutdownStatus | INV045 | Inverter 045 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_InverterTripHistoryAvailable | INV045 | Inverter 045 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_IslandingDetectionStatus | INV045 | Inverter 045 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_LicenseExpired | INV045 | Inverter 045 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_LockingStatus | INV045 | Inverter 045 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_LowInsulationResistance | INV045 | Inverter 045 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_NormalGridConnection | INV045 | Inverter 045 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_NormalShutdown | INV045 | Inverter 045 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_OffGridOutputOverload | INV045 | Inverter 045 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_OptimizerFault | INV045 | Inverter 045 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_OutputDCComponentOverhigh | INV045 | Inverter 045 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_OutputOvercurrent | INV045 | Inverter 045 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_PVStringLoss | INV045 | Inverter 045 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_PassiveIslanding | INV045 | Inverter 045 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_PeripheralPortShortCircuit | INV045 | Inverter 045 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_PhaseWireShortCircuitedPE | INV045 | Inverter 045 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_PowerCurtailmentStatus | INV045 | Inverter 045 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_PowerFactor | INV045 | Inverter 045 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_PowerLimitationActiveGridCommand | INV045 | Inverter 045 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_ReactivePower | INV045 | Inverter 045 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV045_RemoteOFFStatus | INV045 | Inverter 045 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_Shutdown | INV045 | Inverter 045 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_ShutdownPowerRationing | INV045 | Inverter 045 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_SpotCheck | INV045 | Inverter 045 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_Standby | INV045 | Inverter 045 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_StringCurrentBackfeed | INV045 | Inverter 045 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_StringReverseConnection | INV045 | Inverter 045 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_StringReversePolarity | INV045 | Inverter 045 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_TotalEnergyYield | INV045 | Inverter 045 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV045_TransientACOvervoltage | INV045 | Inverter 045 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_UnstableGridFrequency | INV045 | Inverter 045 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_UpgradeFailed | INV045 | Inverter 045 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV045_WarningActive | INV045 | Inverter 045 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_ACCurrent | INV046 | Inverter 046 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_ACOvervoltage | INV046 | Inverter 046 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_ACUndervoltage | INV046 | Inverter 046 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_ACVoltage | INV046 | Inverter 046 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_AFCISelfCheckFailure | INV046 | Inverter 046 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_AbnormalGrounding | INV046 | Inverter 046 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_AbnormalPVModuleConfiguration | INV046 | Inverter 046 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_AbnormalResidualCurrent | INV046 | Inverter 046 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_AbnormalStringPower | INV046 | Inverter 046 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_ActiveIslanding | INV046 | Inverter 046 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_ActivePower | INV046 | Inverter 046 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_ApparentPower | INV046 | Inverter 046 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV046_BuiltPIDOperationAbnormal | INV046 | Inverter 046 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_CabinetOvertemperature | INV046 | Inverter 046 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_CommunicationFailure | INV046 | Inverter 046 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_CommunicationStatus | INV046 | Inverter 046 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_DCArcFault | INV046 | Inverter 046 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_DCCurrent | INV046 | Inverter 046 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_DCInsulationFault | INV046 | Inverter 046 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_DCOvervoltage | INV046 | Inverter 046 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_DCPower | INV046 | Inverter 046 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV046_DCVoltage | INV046 | Inverter 046 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_DailyEnergyYield | INV046 | Inverter 046 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV046_DeviceFault | INV046 | Inverter 046 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_ExternalFanAbnormal | INV046 | Inverter 046 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_FanFailure | INV046 | Inverter 046 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_Faulty | INV046 | Inverter 046 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_FaultyMonitoringUnit | INV046 | Inverter 046 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_FaultyPowerCollector | INV046 | Inverter 046 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_Frequency | INV046 | Inverter 046 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_GeneralFaultTrip | INV046 | Inverter 046 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_Grid | INV046 | Inverter 046 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GridConnectionDeratingInverterInternalCauses | INV046 | Inverter 046 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GridConnectionDeratingPowerRationing | INV046 | Inverter 046 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GridLoss | INV046 | Inverter 046 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GridOverfrequency | INV046 | Inverter 046 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GridOvervoltage | INV046 | Inverter 046 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GridTiedOffGridControllerAbnormal | INV046 | Inverter 046 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GridUnderfrequency | INV046 | Inverter 046 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GridUndervoltage | INV046 | Inverter 046 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GridVoltageImbalance | INV046 | Inverter 046 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_GroundFault | INV046 | Inverter 046 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_HighInputStringVoltageGround | INV046 | Inverter 046 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_HighStringInputVoltage | INV046 | Inverter 046 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_InverterEfficiency | INV046 | Inverter 046 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_InverterGridConnectionStatus | INV046 | Inverter 046 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_InverterOverTemperature | INV046 | Inverter 046 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_InverterRunningStopped | INV046 | Inverter 046 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_InverterStartupShutdownStatus | INV046 | Inverter 046 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_InverterTripHistoryAvailable | INV046 | Inverter 046 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_IslandingDetectionStatus | INV046 | Inverter 046 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_LicenseExpired | INV046 | Inverter 046 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_LockingStatus | INV046 | Inverter 046 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_LowInsulationResistance | INV046 | Inverter 046 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_NormalGridConnection | INV046 | Inverter 046 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_NormalShutdown | INV046 | Inverter 046 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_OffGridOutputOverload | INV046 | Inverter 046 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_OptimizerFault | INV046 | Inverter 046 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_OutputDCComponentOverhigh | INV046 | Inverter 046 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_OutputOvercurrent | INV046 | Inverter 046 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_PVStringLoss | INV046 | Inverter 046 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_PassiveIslanding | INV046 | Inverter 046 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_PeripheralPortShortCircuit | INV046 | Inverter 046 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_PhaseWireShortCircuitedPE | INV046 | Inverter 046 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_PowerCurtailmentStatus | INV046 | Inverter 046 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_PowerFactor | INV046 | Inverter 046 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_PowerLimitationActiveGridCommand | INV046 | Inverter 046 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_ReactivePower | INV046 | Inverter 046 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV046_RemoteOFFStatus | INV046 | Inverter 046 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_Shutdown | INV046 | Inverter 046 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_ShutdownPowerRationing | INV046 | Inverter 046 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_SpotCheck | INV046 | Inverter 046 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_Standby | INV046 | Inverter 046 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_StringCurrentBackfeed | INV046 | Inverter 046 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_StringReverseConnection | INV046 | Inverter 046 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_StringReversePolarity | INV046 | Inverter 046 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_TotalEnergyYield | INV046 | Inverter 046 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV046_TransientACOvervoltage | INV046 | Inverter 046 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_UnstableGridFrequency | INV046 | Inverter 046 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_UpgradeFailed | INV046 | Inverter 046 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV046_WarningActive | INV046 | Inverter 046 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_ACCurrent | INV047 | Inverter 047 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_ACOvervoltage | INV047 | Inverter 047 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_ACUndervoltage | INV047 | Inverter 047 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_ACVoltage | INV047 | Inverter 047 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_AFCISelfCheckFailure | INV047 | Inverter 047 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_AbnormalGrounding | INV047 | Inverter 047 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_AbnormalPVModuleConfiguration | INV047 | Inverter 047 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_AbnormalResidualCurrent | INV047 | Inverter 047 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_AbnormalStringPower | INV047 | Inverter 047 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_ActiveIslanding | INV047 | Inverter 047 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_ActivePower | INV047 | Inverter 047 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_ApparentPower | INV047 | Inverter 047 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV047_BuiltPIDOperationAbnormal | INV047 | Inverter 047 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_CabinetOvertemperature | INV047 | Inverter 047 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_CommunicationFailure | INV047 | Inverter 047 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_CommunicationStatus | INV047 | Inverter 047 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_DCArcFault | INV047 | Inverter 047 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_DCCurrent | INV047 | Inverter 047 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_DCInsulationFault | INV047 | Inverter 047 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_DCOvervoltage | INV047 | Inverter 047 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_DCPower | INV047 | Inverter 047 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV047_DCVoltage | INV047 | Inverter 047 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_DailyEnergyYield | INV047 | Inverter 047 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV047_DeviceFault | INV047 | Inverter 047 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_ExternalFanAbnormal | INV047 | Inverter 047 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_FanFailure | INV047 | Inverter 047 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_Faulty | INV047 | Inverter 047 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_FaultyMonitoringUnit | INV047 | Inverter 047 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_FaultyPowerCollector | INV047 | Inverter 047 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_Frequency | INV047 | Inverter 047 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_GeneralFaultTrip | INV047 | Inverter 047 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_Grid | INV047 | Inverter 047 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GridConnectionDeratingInverterInternalCauses | INV047 | Inverter 047 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GridConnectionDeratingPowerRationing | INV047 | Inverter 047 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GridLoss | INV047 | Inverter 047 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GridOverfrequency | INV047 | Inverter 047 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GridOvervoltage | INV047 | Inverter 047 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GridTiedOffGridControllerAbnormal | INV047 | Inverter 047 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GridUnderfrequency | INV047 | Inverter 047 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GridUndervoltage | INV047 | Inverter 047 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GridVoltageImbalance | INV047 | Inverter 047 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_GroundFault | INV047 | Inverter 047 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_HighInputStringVoltageGround | INV047 | Inverter 047 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_HighStringInputVoltage | INV047 | Inverter 047 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_InverterEfficiency | INV047 | Inverter 047 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_InverterGridConnectionStatus | INV047 | Inverter 047 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_InverterOverTemperature | INV047 | Inverter 047 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_InverterRunningStopped | INV047 | Inverter 047 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_InverterStartupShutdownStatus | INV047 | Inverter 047 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_InverterTripHistoryAvailable | INV047 | Inverter 047 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_IslandingDetectionStatus | INV047 | Inverter 047 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_LicenseExpired | INV047 | Inverter 047 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_LockingStatus | INV047 | Inverter 047 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_LowInsulationResistance | INV047 | Inverter 047 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_NormalGridConnection | INV047 | Inverter 047 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_NormalShutdown | INV047 | Inverter 047 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_OffGridOutputOverload | INV047 | Inverter 047 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_OptimizerFault | INV047 | Inverter 047 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_OutputDCComponentOverhigh | INV047 | Inverter 047 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_OutputOvercurrent | INV047 | Inverter 047 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_PVStringLoss | INV047 | Inverter 047 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_PassiveIslanding | INV047 | Inverter 047 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_PeripheralPortShortCircuit | INV047 | Inverter 047 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_PhaseWireShortCircuitedPE | INV047 | Inverter 047 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_PowerCurtailmentStatus | INV047 | Inverter 047 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_PowerFactor | INV047 | Inverter 047 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_PowerLimitationActiveGridCommand | INV047 | Inverter 047 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_ReactivePower | INV047 | Inverter 047 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV047_RemoteOFFStatus | INV047 | Inverter 047 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_Shutdown | INV047 | Inverter 047 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_ShutdownPowerRationing | INV047 | Inverter 047 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_SpotCheck | INV047 | Inverter 047 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_Standby | INV047 | Inverter 047 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_StringCurrentBackfeed | INV047 | Inverter 047 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_StringReverseConnection | INV047 | Inverter 047 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_StringReversePolarity | INV047 | Inverter 047 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_TotalEnergyYield | INV047 | Inverter 047 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV047_TransientACOvervoltage | INV047 | Inverter 047 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_UnstableGridFrequency | INV047 | Inverter 047 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_UpgradeFailed | INV047 | Inverter 047 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV047_WarningActive | INV047 | Inverter 047 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_ACCurrent | INV048 | Inverter 048 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_ACOvervoltage | INV048 | Inverter 048 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_ACUndervoltage | INV048 | Inverter 048 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_ACVoltage | INV048 | Inverter 048 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_AFCISelfCheckFailure | INV048 | Inverter 048 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_AbnormalGrounding | INV048 | Inverter 048 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_AbnormalPVModuleConfiguration | INV048 | Inverter 048 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_AbnormalResidualCurrent | INV048 | Inverter 048 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_AbnormalStringPower | INV048 | Inverter 048 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_ActiveIslanding | INV048 | Inverter 048 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_ActivePower | INV048 | Inverter 048 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_ApparentPower | INV048 | Inverter 048 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV048_BuiltPIDOperationAbnormal | INV048 | Inverter 048 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_CabinetOvertemperature | INV048 | Inverter 048 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_CommunicationFailure | INV048 | Inverter 048 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_CommunicationStatus | INV048 | Inverter 048 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_DCArcFault | INV048 | Inverter 048 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_DCCurrent | INV048 | Inverter 048 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_DCInsulationFault | INV048 | Inverter 048 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_DCOvervoltage | INV048 | Inverter 048 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_DCPower | INV048 | Inverter 048 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV048_DCVoltage | INV048 | Inverter 048 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_DailyEnergyYield | INV048 | Inverter 048 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV048_DeviceFault | INV048 | Inverter 048 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_ExternalFanAbnormal | INV048 | Inverter 048 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_FanFailure | INV048 | Inverter 048 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_Faulty | INV048 | Inverter 048 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_FaultyMonitoringUnit | INV048 | Inverter 048 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_FaultyPowerCollector | INV048 | Inverter 048 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_Frequency | INV048 | Inverter 048 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_GeneralFaultTrip | INV048 | Inverter 048 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_Grid | INV048 | Inverter 048 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GridConnectionDeratingInverterInternalCauses | INV048 | Inverter 048 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GridConnectionDeratingPowerRationing | INV048 | Inverter 048 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GridLoss | INV048 | Inverter 048 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GridOverfrequency | INV048 | Inverter 048 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GridOvervoltage | INV048 | Inverter 048 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GridTiedOffGridControllerAbnormal | INV048 | Inverter 048 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GridUnderfrequency | INV048 | Inverter 048 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GridUndervoltage | INV048 | Inverter 048 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GridVoltageImbalance | INV048 | Inverter 048 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_GroundFault | INV048 | Inverter 048 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_HighInputStringVoltageGround | INV048 | Inverter 048 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_HighStringInputVoltage | INV048 | Inverter 048 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_InverterEfficiency | INV048 | Inverter 048 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_InverterGridConnectionStatus | INV048 | Inverter 048 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_InverterOverTemperature | INV048 | Inverter 048 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_InverterRunningStopped | INV048 | Inverter 048 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_InverterStartupShutdownStatus | INV048 | Inverter 048 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_InverterTripHistoryAvailable | INV048 | Inverter 048 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_IslandingDetectionStatus | INV048 | Inverter 048 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_LicenseExpired | INV048 | Inverter 048 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_LockingStatus | INV048 | Inverter 048 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_LowInsulationResistance | INV048 | Inverter 048 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_NormalGridConnection | INV048 | Inverter 048 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_NormalShutdown | INV048 | Inverter 048 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_OffGridOutputOverload | INV048 | Inverter 048 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_OptimizerFault | INV048 | Inverter 048 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_OutputDCComponentOverhigh | INV048 | Inverter 048 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_OutputOvercurrent | INV048 | Inverter 048 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_PVStringLoss | INV048 | Inverter 048 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_PassiveIslanding | INV048 | Inverter 048 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_PeripheralPortShortCircuit | INV048 | Inverter 048 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_PhaseWireShortCircuitedPE | INV048 | Inverter 048 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_PowerCurtailmentStatus | INV048 | Inverter 048 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_PowerFactor | INV048 | Inverter 048 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_PowerLimitationActiveGridCommand | INV048 | Inverter 048 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_ReactivePower | INV048 | Inverter 048 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV048_RemoteOFFStatus | INV048 | Inverter 048 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_Shutdown | INV048 | Inverter 048 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_ShutdownPowerRationing | INV048 | Inverter 048 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_SpotCheck | INV048 | Inverter 048 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_Standby | INV048 | Inverter 048 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_StringCurrentBackfeed | INV048 | Inverter 048 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_StringReverseConnection | INV048 | Inverter 048 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_StringReversePolarity | INV048 | Inverter 048 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_TotalEnergyYield | INV048 | Inverter 048 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV048_TransientACOvervoltage | INV048 | Inverter 048 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_UnstableGridFrequency | INV048 | Inverter 048 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_UpgradeFailed | INV048 | Inverter 048 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV048_WarningActive | INV048 | Inverter 048 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_ACCurrent | INV049 | Inverter 049 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_ACOvervoltage | INV049 | Inverter 049 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_ACUndervoltage | INV049 | Inverter 049 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_ACVoltage | INV049 | Inverter 049 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_AFCISelfCheckFailure | INV049 | Inverter 049 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_AbnormalGrounding | INV049 | Inverter 049 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_AbnormalPVModuleConfiguration | INV049 | Inverter 049 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_AbnormalResidualCurrent | INV049 | Inverter 049 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_AbnormalStringPower | INV049 | Inverter 049 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_ActiveIslanding | INV049 | Inverter 049 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_ActivePower | INV049 | Inverter 049 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_ApparentPower | INV049 | Inverter 049 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV049_BuiltPIDOperationAbnormal | INV049 | Inverter 049 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_CabinetOvertemperature | INV049 | Inverter 049 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_CommunicationFailure | INV049 | Inverter 049 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_CommunicationStatus | INV049 | Inverter 049 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_DCArcFault | INV049 | Inverter 049 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_DCCurrent | INV049 | Inverter 049 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_DCInsulationFault | INV049 | Inverter 049 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_DCOvervoltage | INV049 | Inverter 049 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_DCPower | INV049 | Inverter 049 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV049_DCVoltage | INV049 | Inverter 049 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_DailyEnergyYield | INV049 | Inverter 049 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV049_DeviceFault | INV049 | Inverter 049 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_ExternalFanAbnormal | INV049 | Inverter 049 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_FanFailure | INV049 | Inverter 049 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_Faulty | INV049 | Inverter 049 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_FaultyMonitoringUnit | INV049 | Inverter 049 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_FaultyPowerCollector | INV049 | Inverter 049 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_Frequency | INV049 | Inverter 049 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_GeneralFaultTrip | INV049 | Inverter 049 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_Grid | INV049 | Inverter 049 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GridConnectionDeratingInverterInternalCauses | INV049 | Inverter 049 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GridConnectionDeratingPowerRationing | INV049 | Inverter 049 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GridLoss | INV049 | Inverter 049 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GridOverfrequency | INV049 | Inverter 049 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GridOvervoltage | INV049 | Inverter 049 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GridTiedOffGridControllerAbnormal | INV049 | Inverter 049 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GridUnderfrequency | INV049 | Inverter 049 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GridUndervoltage | INV049 | Inverter 049 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GridVoltageImbalance | INV049 | Inverter 049 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_GroundFault | INV049 | Inverter 049 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_HighInputStringVoltageGround | INV049 | Inverter 049 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_HighStringInputVoltage | INV049 | Inverter 049 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_InverterEfficiency | INV049 | Inverter 049 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_InverterGridConnectionStatus | INV049 | Inverter 049 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_InverterOverTemperature | INV049 | Inverter 049 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_InverterRunningStopped | INV049 | Inverter 049 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_InverterStartupShutdownStatus | INV049 | Inverter 049 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_InverterTripHistoryAvailable | INV049 | Inverter 049 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_IslandingDetectionStatus | INV049 | Inverter 049 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_LicenseExpired | INV049 | Inverter 049 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_LockingStatus | INV049 | Inverter 049 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_LowInsulationResistance | INV049 | Inverter 049 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_NormalGridConnection | INV049 | Inverter 049 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_NormalShutdown | INV049 | Inverter 049 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_OffGridOutputOverload | INV049 | Inverter 049 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_OptimizerFault | INV049 | Inverter 049 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_OutputDCComponentOverhigh | INV049 | Inverter 049 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_OutputOvercurrent | INV049 | Inverter 049 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_PVStringLoss | INV049 | Inverter 049 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_PassiveIslanding | INV049 | Inverter 049 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_PeripheralPortShortCircuit | INV049 | Inverter 049 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_PhaseWireShortCircuitedPE | INV049 | Inverter 049 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_PowerCurtailmentStatus | INV049 | Inverter 049 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_PowerFactor | INV049 | Inverter 049 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_PowerLimitationActiveGridCommand | INV049 | Inverter 049 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_ReactivePower | INV049 | Inverter 049 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV049_RemoteOFFStatus | INV049 | Inverter 049 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_Shutdown | INV049 | Inverter 049 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_ShutdownPowerRationing | INV049 | Inverter 049 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_SpotCheck | INV049 | Inverter 049 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_Standby | INV049 | Inverter 049 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_StringCurrentBackfeed | INV049 | Inverter 049 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_StringReverseConnection | INV049 | Inverter 049 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_StringReversePolarity | INV049 | Inverter 049 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_TotalEnergyYield | INV049 | Inverter 049 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV049_TransientACOvervoltage | INV049 | Inverter 049 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_UnstableGridFrequency | INV049 | Inverter 049 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_UpgradeFailed | INV049 | Inverter 049 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV049_WarningActive | INV049 | Inverter 049 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_ACCurrent | INV050 | Inverter 050 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_ACOvervoltage | INV050 | Inverter 050 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_ACUndervoltage | INV050 | Inverter 050 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_ACVoltage | INV050 | Inverter 050 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_AFCISelfCheckFailure | INV050 | Inverter 050 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_AbnormalGrounding | INV050 | Inverter 050 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_AbnormalPVModuleConfiguration | INV050 | Inverter 050 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_AbnormalResidualCurrent | INV050 | Inverter 050 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_AbnormalStringPower | INV050 | Inverter 050 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_ActiveIslanding | INV050 | Inverter 050 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_ActivePower | INV050 | Inverter 050 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_ApparentPower | INV050 | Inverter 050 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV050_BuiltPIDOperationAbnormal | INV050 | Inverter 050 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_CabinetOvertemperature | INV050 | Inverter 050 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_CommunicationFailure | INV050 | Inverter 050 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_CommunicationStatus | INV050 | Inverter 050 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_DCArcFault | INV050 | Inverter 050 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_DCCurrent | INV050 | Inverter 050 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_DCInsulationFault | INV050 | Inverter 050 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_DCOvervoltage | INV050 | Inverter 050 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_DCPower | INV050 | Inverter 050 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV050_DCVoltage | INV050 | Inverter 050 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_DailyEnergyYield | INV050 | Inverter 050 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV050_DeviceFault | INV050 | Inverter 050 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_ExternalFanAbnormal | INV050 | Inverter 050 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_FanFailure | INV050 | Inverter 050 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_Faulty | INV050 | Inverter 050 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_FaultyMonitoringUnit | INV050 | Inverter 050 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_FaultyPowerCollector | INV050 | Inverter 050 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_Frequency | INV050 | Inverter 050 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_GeneralFaultTrip | INV050 | Inverter 050 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_Grid | INV050 | Inverter 050 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GridConnectionDeratingInverterInternalCauses | INV050 | Inverter 050 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GridConnectionDeratingPowerRationing | INV050 | Inverter 050 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GridLoss | INV050 | Inverter 050 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GridOverfrequency | INV050 | Inverter 050 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GridOvervoltage | INV050 | Inverter 050 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GridTiedOffGridControllerAbnormal | INV050 | Inverter 050 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GridUnderfrequency | INV050 | Inverter 050 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GridUndervoltage | INV050 | Inverter 050 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GridVoltageImbalance | INV050 | Inverter 050 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_GroundFault | INV050 | Inverter 050 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_HighInputStringVoltageGround | INV050 | Inverter 050 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_HighStringInputVoltage | INV050 | Inverter 050 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_InverterEfficiency | INV050 | Inverter 050 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_InverterGridConnectionStatus | INV050 | Inverter 050 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_InverterOverTemperature | INV050 | Inverter 050 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_InverterRunningStopped | INV050 | Inverter 050 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_InverterStartupShutdownStatus | INV050 | Inverter 050 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_InverterTripHistoryAvailable | INV050 | Inverter 050 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_IslandingDetectionStatus | INV050 | Inverter 050 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_LicenseExpired | INV050 | Inverter 050 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_LockingStatus | INV050 | Inverter 050 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_LowInsulationResistance | INV050 | Inverter 050 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_NormalGridConnection | INV050 | Inverter 050 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_NormalShutdown | INV050 | Inverter 050 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_OffGridOutputOverload | INV050 | Inverter 050 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_OptimizerFault | INV050 | Inverter 050 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_OutputDCComponentOverhigh | INV050 | Inverter 050 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_OutputOvercurrent | INV050 | Inverter 050 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_PVStringLoss | INV050 | Inverter 050 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_PassiveIslanding | INV050 | Inverter 050 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_PeripheralPortShortCircuit | INV050 | Inverter 050 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_PhaseWireShortCircuitedPE | INV050 | Inverter 050 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_PowerCurtailmentStatus | INV050 | Inverter 050 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_PowerFactor | INV050 | Inverter 050 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_PowerLimitationActiveGridCommand | INV050 | Inverter 050 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_ReactivePower | INV050 | Inverter 050 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV050_RemoteOFFStatus | INV050 | Inverter 050 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_Shutdown | INV050 | Inverter 050 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_ShutdownPowerRationing | INV050 | Inverter 050 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_SpotCheck | INV050 | Inverter 050 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_Standby | INV050 | Inverter 050 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_StringCurrentBackfeed | INV050 | Inverter 050 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_StringReverseConnection | INV050 | Inverter 050 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_StringReversePolarity | INV050 | Inverter 050 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_TotalEnergyYield | INV050 | Inverter 050 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV050_TransientACOvervoltage | INV050 | Inverter 050 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_UnstableGridFrequency | INV050 | Inverter 050 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_UpgradeFailed | INV050 | Inverter 050 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV050_WarningActive | INV050 | Inverter 050 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_ACCurrent | INV051 | Inverter 051 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_ACOvervoltage | INV051 | Inverter 051 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_ACUndervoltage | INV051 | Inverter 051 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_ACVoltage | INV051 | Inverter 051 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_AFCISelfCheckFailure | INV051 | Inverter 051 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_AbnormalGrounding | INV051 | Inverter 051 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_AbnormalPVModuleConfiguration | INV051 | Inverter 051 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_AbnormalResidualCurrent | INV051 | Inverter 051 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_AbnormalStringPower | INV051 | Inverter 051 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_ActiveIslanding | INV051 | Inverter 051 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_ActivePower | INV051 | Inverter 051 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_ApparentPower | INV051 | Inverter 051 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV051_BuiltPIDOperationAbnormal | INV051 | Inverter 051 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_CabinetOvertemperature | INV051 | Inverter 051 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_CommunicationFailure | INV051 | Inverter 051 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_CommunicationStatus | INV051 | Inverter 051 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_DCArcFault | INV051 | Inverter 051 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_DCCurrent | INV051 | Inverter 051 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_DCInsulationFault | INV051 | Inverter 051 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_DCOvervoltage | INV051 | Inverter 051 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_DCPower | INV051 | Inverter 051 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV051_DCVoltage | INV051 | Inverter 051 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_DailyEnergyYield | INV051 | Inverter 051 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV051_DeviceFault | INV051 | Inverter 051 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_ExternalFanAbnormal | INV051 | Inverter 051 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_FanFailure | INV051 | Inverter 051 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_Faulty | INV051 | Inverter 051 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_FaultyMonitoringUnit | INV051 | Inverter 051 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_FaultyPowerCollector | INV051 | Inverter 051 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_Frequency | INV051 | Inverter 051 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_GeneralFaultTrip | INV051 | Inverter 051 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_Grid | INV051 | Inverter 051 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GridConnectionDeratingInverterInternalCauses | INV051 | Inverter 051 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GridConnectionDeratingPowerRationing | INV051 | Inverter 051 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GridLoss | INV051 | Inverter 051 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GridOverfrequency | INV051 | Inverter 051 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GridOvervoltage | INV051 | Inverter 051 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GridTiedOffGridControllerAbnormal | INV051 | Inverter 051 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GridUnderfrequency | INV051 | Inverter 051 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GridUndervoltage | INV051 | Inverter 051 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GridVoltageImbalance | INV051 | Inverter 051 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_GroundFault | INV051 | Inverter 051 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_HighInputStringVoltageGround | INV051 | Inverter 051 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_HighStringInputVoltage | INV051 | Inverter 051 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_InverterEfficiency | INV051 | Inverter 051 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_InverterGridConnectionStatus | INV051 | Inverter 051 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_InverterOverTemperature | INV051 | Inverter 051 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_InverterRunningStopped | INV051 | Inverter 051 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_InverterStartupShutdownStatus | INV051 | Inverter 051 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_InverterTripHistoryAvailable | INV051 | Inverter 051 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_IslandingDetectionStatus | INV051 | Inverter 051 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_LicenseExpired | INV051 | Inverter 051 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_LockingStatus | INV051 | Inverter 051 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_LowInsulationResistance | INV051 | Inverter 051 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_NormalGridConnection | INV051 | Inverter 051 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_NormalShutdown | INV051 | Inverter 051 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_OffGridOutputOverload | INV051 | Inverter 051 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_OptimizerFault | INV051 | Inverter 051 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_OutputDCComponentOverhigh | INV051 | Inverter 051 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_OutputOvercurrent | INV051 | Inverter 051 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_PVStringLoss | INV051 | Inverter 051 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_PassiveIslanding | INV051 | Inverter 051 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_PeripheralPortShortCircuit | INV051 | Inverter 051 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_PhaseWireShortCircuitedPE | INV051 | Inverter 051 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_PowerCurtailmentStatus | INV051 | Inverter 051 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_PowerFactor | INV051 | Inverter 051 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_PowerLimitationActiveGridCommand | INV051 | Inverter 051 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_ReactivePower | INV051 | Inverter 051 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV051_RemoteOFFStatus | INV051 | Inverter 051 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_Shutdown | INV051 | Inverter 051 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_ShutdownPowerRationing | INV051 | Inverter 051 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_SpotCheck | INV051 | Inverter 051 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_Standby | INV051 | Inverter 051 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_StringCurrentBackfeed | INV051 | Inverter 051 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_StringReverseConnection | INV051 | Inverter 051 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_StringReversePolarity | INV051 | Inverter 051 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_TotalEnergyYield | INV051 | Inverter 051 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV051_TransientACOvervoltage | INV051 | Inverter 051 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_UnstableGridFrequency | INV051 | Inverter 051 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_UpgradeFailed | INV051 | Inverter 051 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV051_WarningActive | INV051 | Inverter 051 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_ACCurrent | INV052 | Inverter 052 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_ACOvervoltage | INV052 | Inverter 052 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_ACUndervoltage | INV052 | Inverter 052 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_ACVoltage | INV052 | Inverter 052 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_AFCISelfCheckFailure | INV052 | Inverter 052 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_AbnormalGrounding | INV052 | Inverter 052 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_AbnormalPVModuleConfiguration | INV052 | Inverter 052 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_AbnormalResidualCurrent | INV052 | Inverter 052 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_AbnormalStringPower | INV052 | Inverter 052 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_ActiveIslanding | INV052 | Inverter 052 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_ActivePower | INV052 | Inverter 052 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_ApparentPower | INV052 | Inverter 052 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV052_BuiltPIDOperationAbnormal | INV052 | Inverter 052 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_CabinetOvertemperature | INV052 | Inverter 052 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_CommunicationFailure | INV052 | Inverter 052 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_CommunicationStatus | INV052 | Inverter 052 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_DCArcFault | INV052 | Inverter 052 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_DCCurrent | INV052 | Inverter 052 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_DCInsulationFault | INV052 | Inverter 052 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_DCOvervoltage | INV052 | Inverter 052 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_DCPower | INV052 | Inverter 052 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV052_DCVoltage | INV052 | Inverter 052 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_DailyEnergyYield | INV052 | Inverter 052 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV052_DeviceFault | INV052 | Inverter 052 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_ExternalFanAbnormal | INV052 | Inverter 052 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_FanFailure | INV052 | Inverter 052 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_Faulty | INV052 | Inverter 052 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_FaultyMonitoringUnit | INV052 | Inverter 052 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_FaultyPowerCollector | INV052 | Inverter 052 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_Frequency | INV052 | Inverter 052 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_GeneralFaultTrip | INV052 | Inverter 052 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_Grid | INV052 | Inverter 052 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GridConnectionDeratingInverterInternalCauses | INV052 | Inverter 052 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GridConnectionDeratingPowerRationing | INV052 | Inverter 052 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GridLoss | INV052 | Inverter 052 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GridOverfrequency | INV052 | Inverter 052 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GridOvervoltage | INV052 | Inverter 052 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GridTiedOffGridControllerAbnormal | INV052 | Inverter 052 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GridUnderfrequency | INV052 | Inverter 052 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GridUndervoltage | INV052 | Inverter 052 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GridVoltageImbalance | INV052 | Inverter 052 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_GroundFault | INV052 | Inverter 052 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_HighInputStringVoltageGround | INV052 | Inverter 052 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_HighStringInputVoltage | INV052 | Inverter 052 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_InverterEfficiency | INV052 | Inverter 052 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_InverterGridConnectionStatus | INV052 | Inverter 052 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_InverterOverTemperature | INV052 | Inverter 052 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_InverterRunningStopped | INV052 | Inverter 052 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_InverterStartupShutdownStatus | INV052 | Inverter 052 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_InverterTripHistoryAvailable | INV052 | Inverter 052 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_IslandingDetectionStatus | INV052 | Inverter 052 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_LicenseExpired | INV052 | Inverter 052 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_LockingStatus | INV052 | Inverter 052 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_LowInsulationResistance | INV052 | Inverter 052 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_NormalGridConnection | INV052 | Inverter 052 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_NormalShutdown | INV052 | Inverter 052 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_OffGridOutputOverload | INV052 | Inverter 052 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_OptimizerFault | INV052 | Inverter 052 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_OutputDCComponentOverhigh | INV052 | Inverter 052 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_OutputOvercurrent | INV052 | Inverter 052 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_PVStringLoss | INV052 | Inverter 052 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_PassiveIslanding | INV052 | Inverter 052 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_PeripheralPortShortCircuit | INV052 | Inverter 052 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_PhaseWireShortCircuitedPE | INV052 | Inverter 052 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_PowerCurtailmentStatus | INV052 | Inverter 052 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_PowerFactor | INV052 | Inverter 052 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_PowerLimitationActiveGridCommand | INV052 | Inverter 052 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_ReactivePower | INV052 | Inverter 052 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV052_RemoteOFFStatus | INV052 | Inverter 052 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_Shutdown | INV052 | Inverter 052 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_ShutdownPowerRationing | INV052 | Inverter 052 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_SpotCheck | INV052 | Inverter 052 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_Standby | INV052 | Inverter 052 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_StringCurrentBackfeed | INV052 | Inverter 052 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_StringReverseConnection | INV052 | Inverter 052 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_StringReversePolarity | INV052 | Inverter 052 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_TotalEnergyYield | INV052 | Inverter 052 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV052_TransientACOvervoltage | INV052 | Inverter 052 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_UnstableGridFrequency | INV052 | Inverter 052 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_UpgradeFailed | INV052 | Inverter 052 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV052_WarningActive | INV052 | Inverter 052 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_ACCurrent | INV053 | Inverter 053 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_ACOvervoltage | INV053 | Inverter 053 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_ACUndervoltage | INV053 | Inverter 053 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_ACVoltage | INV053 | Inverter 053 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_AFCISelfCheckFailure | INV053 | Inverter 053 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_AbnormalGrounding | INV053 | Inverter 053 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_AbnormalPVModuleConfiguration | INV053 | Inverter 053 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_AbnormalResidualCurrent | INV053 | Inverter 053 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_AbnormalStringPower | INV053 | Inverter 053 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_ActiveIslanding | INV053 | Inverter 053 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_ActivePower | INV053 | Inverter 053 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_ApparentPower | INV053 | Inverter 053 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV053_BuiltPIDOperationAbnormal | INV053 | Inverter 053 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_CabinetOvertemperature | INV053 | Inverter 053 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_CommunicationFailure | INV053 | Inverter 053 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_CommunicationStatus | INV053 | Inverter 053 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_DCArcFault | INV053 | Inverter 053 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_DCCurrent | INV053 | Inverter 053 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_DCInsulationFault | INV053 | Inverter 053 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_DCOvervoltage | INV053 | Inverter 053 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_DCPower | INV053 | Inverter 053 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV053_DCVoltage | INV053 | Inverter 053 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_DailyEnergyYield | INV053 | Inverter 053 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV053_DeviceFault | INV053 | Inverter 053 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_ExternalFanAbnormal | INV053 | Inverter 053 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_FanFailure | INV053 | Inverter 053 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_Faulty | INV053 | Inverter 053 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_FaultyMonitoringUnit | INV053 | Inverter 053 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_FaultyPowerCollector | INV053 | Inverter 053 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_Frequency | INV053 | Inverter 053 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_GeneralFaultTrip | INV053 | Inverter 053 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_Grid | INV053 | Inverter 053 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GridConnectionDeratingInverterInternalCauses | INV053 | Inverter 053 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GridConnectionDeratingPowerRationing | INV053 | Inverter 053 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GridLoss | INV053 | Inverter 053 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GridOverfrequency | INV053 | Inverter 053 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GridOvervoltage | INV053 | Inverter 053 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GridTiedOffGridControllerAbnormal | INV053 | Inverter 053 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GridUnderfrequency | INV053 | Inverter 053 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GridUndervoltage | INV053 | Inverter 053 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GridVoltageImbalance | INV053 | Inverter 053 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_GroundFault | INV053 | Inverter 053 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_HighInputStringVoltageGround | INV053 | Inverter 053 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_HighStringInputVoltage | INV053 | Inverter 053 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_InverterEfficiency | INV053 | Inverter 053 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_InverterGridConnectionStatus | INV053 | Inverter 053 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_InverterOverTemperature | INV053 | Inverter 053 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_InverterRunningStopped | INV053 | Inverter 053 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_InverterStartupShutdownStatus | INV053 | Inverter 053 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_InverterTripHistoryAvailable | INV053 | Inverter 053 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_IslandingDetectionStatus | INV053 | Inverter 053 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_LicenseExpired | INV053 | Inverter 053 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_LockingStatus | INV053 | Inverter 053 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_LowInsulationResistance | INV053 | Inverter 053 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_NormalGridConnection | INV053 | Inverter 053 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_NormalShutdown | INV053 | Inverter 053 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_OffGridOutputOverload | INV053 | Inverter 053 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_OptimizerFault | INV053 | Inverter 053 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_OutputDCComponentOverhigh | INV053 | Inverter 053 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_OutputOvercurrent | INV053 | Inverter 053 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_PVStringLoss | INV053 | Inverter 053 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_PassiveIslanding | INV053 | Inverter 053 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_PeripheralPortShortCircuit | INV053 | Inverter 053 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_PhaseWireShortCircuitedPE | INV053 | Inverter 053 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_PowerCurtailmentStatus | INV053 | Inverter 053 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_PowerFactor | INV053 | Inverter 053 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_PowerLimitationActiveGridCommand | INV053 | Inverter 053 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_ReactivePower | INV053 | Inverter 053 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV053_RemoteOFFStatus | INV053 | Inverter 053 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_Shutdown | INV053 | Inverter 053 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_ShutdownPowerRationing | INV053 | Inverter 053 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_SpotCheck | INV053 | Inverter 053 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_Standby | INV053 | Inverter 053 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_StringCurrentBackfeed | INV053 | Inverter 053 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_StringReverseConnection | INV053 | Inverter 053 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_StringReversePolarity | INV053 | Inverter 053 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_TotalEnergyYield | INV053 | Inverter 053 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV053_TransientACOvervoltage | INV053 | Inverter 053 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_UnstableGridFrequency | INV053 | Inverter 053 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_UpgradeFailed | INV053 | Inverter 053 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV053_WarningActive | INV053 | Inverter 053 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_ACCurrent | INV054 | Inverter 054 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_ACOvervoltage | INV054 | Inverter 054 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_ACUndervoltage | INV054 | Inverter 054 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_ACVoltage | INV054 | Inverter 054 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_AFCISelfCheckFailure | INV054 | Inverter 054 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_AbnormalGrounding | INV054 | Inverter 054 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_AbnormalPVModuleConfiguration | INV054 | Inverter 054 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_AbnormalResidualCurrent | INV054 | Inverter 054 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_AbnormalStringPower | INV054 | Inverter 054 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_ActiveIslanding | INV054 | Inverter 054 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_ActivePower | INV054 | Inverter 054 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_ApparentPower | INV054 | Inverter 054 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV054_BuiltPIDOperationAbnormal | INV054 | Inverter 054 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_CabinetOvertemperature | INV054 | Inverter 054 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_CommunicationFailure | INV054 | Inverter 054 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_CommunicationStatus | INV054 | Inverter 054 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_DCArcFault | INV054 | Inverter 054 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_DCCurrent | INV054 | Inverter 054 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_DCInsulationFault | INV054 | Inverter 054 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_DCOvervoltage | INV054 | Inverter 054 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_DCPower | INV054 | Inverter 054 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV054_DCVoltage | INV054 | Inverter 054 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_DailyEnergyYield | INV054 | Inverter 054 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV054_DeviceFault | INV054 | Inverter 054 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_ExternalFanAbnormal | INV054 | Inverter 054 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_FanFailure | INV054 | Inverter 054 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_Faulty | INV054 | Inverter 054 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_FaultyMonitoringUnit | INV054 | Inverter 054 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_FaultyPowerCollector | INV054 | Inverter 054 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_Frequency | INV054 | Inverter 054 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_GeneralFaultTrip | INV054 | Inverter 054 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_Grid | INV054 | Inverter 054 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GridConnectionDeratingInverterInternalCauses | INV054 | Inverter 054 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GridConnectionDeratingPowerRationing | INV054 | Inverter 054 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GridLoss | INV054 | Inverter 054 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GridOverfrequency | INV054 | Inverter 054 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GridOvervoltage | INV054 | Inverter 054 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GridTiedOffGridControllerAbnormal | INV054 | Inverter 054 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GridUnderfrequency | INV054 | Inverter 054 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GridUndervoltage | INV054 | Inverter 054 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GridVoltageImbalance | INV054 | Inverter 054 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_GroundFault | INV054 | Inverter 054 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_HighInputStringVoltageGround | INV054 | Inverter 054 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_HighStringInputVoltage | INV054 | Inverter 054 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_InverterEfficiency | INV054 | Inverter 054 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_InverterGridConnectionStatus | INV054 | Inverter 054 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_InverterOverTemperature | INV054 | Inverter 054 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_InverterRunningStopped | INV054 | Inverter 054 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_InverterStartupShutdownStatus | INV054 | Inverter 054 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_InverterTripHistoryAvailable | INV054 | Inverter 054 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_IslandingDetectionStatus | INV054 | Inverter 054 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_LicenseExpired | INV054 | Inverter 054 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_LockingStatus | INV054 | Inverter 054 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_LowInsulationResistance | INV054 | Inverter 054 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_NormalGridConnection | INV054 | Inverter 054 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_NormalShutdown | INV054 | Inverter 054 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_OffGridOutputOverload | INV054 | Inverter 054 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_OptimizerFault | INV054 | Inverter 054 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_OutputDCComponentOverhigh | INV054 | Inverter 054 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_OutputOvercurrent | INV054 | Inverter 054 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_PVStringLoss | INV054 | Inverter 054 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_PassiveIslanding | INV054 | Inverter 054 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_PeripheralPortShortCircuit | INV054 | Inverter 054 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_PhaseWireShortCircuitedPE | INV054 | Inverter 054 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_PowerCurtailmentStatus | INV054 | Inverter 054 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_PowerFactor | INV054 | Inverter 054 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_PowerLimitationActiveGridCommand | INV054 | Inverter 054 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_ReactivePower | INV054 | Inverter 054 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV054_RemoteOFFStatus | INV054 | Inverter 054 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_Shutdown | INV054 | Inverter 054 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_ShutdownPowerRationing | INV054 | Inverter 054 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_SpotCheck | INV054 | Inverter 054 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_Standby | INV054 | Inverter 054 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_StringCurrentBackfeed | INV054 | Inverter 054 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_StringReverseConnection | INV054 | Inverter 054 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_StringReversePolarity | INV054 | Inverter 054 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_TotalEnergyYield | INV054 | Inverter 054 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV054_TransientACOvervoltage | INV054 | Inverter 054 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_UnstableGridFrequency | INV054 | Inverter 054 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_UpgradeFailed | INV054 | Inverter 054 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV054_WarningActive | INV054 | Inverter 054 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_ACCurrent | INV055 | Inverter 055 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_ACOvervoltage | INV055 | Inverter 055 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_ACUndervoltage | INV055 | Inverter 055 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_ACVoltage | INV055 | Inverter 055 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_AFCISelfCheckFailure | INV055 | Inverter 055 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_AbnormalGrounding | INV055 | Inverter 055 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_AbnormalPVModuleConfiguration | INV055 | Inverter 055 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_AbnormalResidualCurrent | INV055 | Inverter 055 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_AbnormalStringPower | INV055 | Inverter 055 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_ActiveIslanding | INV055 | Inverter 055 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_ActivePower | INV055 | Inverter 055 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_ApparentPower | INV055 | Inverter 055 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV055_BuiltPIDOperationAbnormal | INV055 | Inverter 055 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_CabinetOvertemperature | INV055 | Inverter 055 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_CommunicationFailure | INV055 | Inverter 055 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_CommunicationStatus | INV055 | Inverter 055 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_DCArcFault | INV055 | Inverter 055 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_DCCurrent | INV055 | Inverter 055 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_DCInsulationFault | INV055 | Inverter 055 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_DCOvervoltage | INV055 | Inverter 055 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_DCPower | INV055 | Inverter 055 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV055_DCVoltage | INV055 | Inverter 055 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_DailyEnergyYield | INV055 | Inverter 055 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV055_DeviceFault | INV055 | Inverter 055 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_ExternalFanAbnormal | INV055 | Inverter 055 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_FanFailure | INV055 | Inverter 055 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_Faulty | INV055 | Inverter 055 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_FaultyMonitoringUnit | INV055 | Inverter 055 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_FaultyPowerCollector | INV055 | Inverter 055 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_Frequency | INV055 | Inverter 055 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_GeneralFaultTrip | INV055 | Inverter 055 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_Grid | INV055 | Inverter 055 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GridConnectionDeratingInverterInternalCauses | INV055 | Inverter 055 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GridConnectionDeratingPowerRationing | INV055 | Inverter 055 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GridLoss | INV055 | Inverter 055 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GridOverfrequency | INV055 | Inverter 055 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GridOvervoltage | INV055 | Inverter 055 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GridTiedOffGridControllerAbnormal | INV055 | Inverter 055 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GridUnderfrequency | INV055 | Inverter 055 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GridUndervoltage | INV055 | Inverter 055 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GridVoltageImbalance | INV055 | Inverter 055 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_GroundFault | INV055 | Inverter 055 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_HighInputStringVoltageGround | INV055 | Inverter 055 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_HighStringInputVoltage | INV055 | Inverter 055 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_InverterEfficiency | INV055 | Inverter 055 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_InverterGridConnectionStatus | INV055 | Inverter 055 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_InverterOverTemperature | INV055 | Inverter 055 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_InverterRunningStopped | INV055 | Inverter 055 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_InverterStartupShutdownStatus | INV055 | Inverter 055 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_InverterTripHistoryAvailable | INV055 | Inverter 055 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_IslandingDetectionStatus | INV055 | Inverter 055 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_LicenseExpired | INV055 | Inverter 055 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_LockingStatus | INV055 | Inverter 055 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_LowInsulationResistance | INV055 | Inverter 055 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_NormalGridConnection | INV055 | Inverter 055 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_NormalShutdown | INV055 | Inverter 055 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_OffGridOutputOverload | INV055 | Inverter 055 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_OptimizerFault | INV055 | Inverter 055 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_OutputDCComponentOverhigh | INV055 | Inverter 055 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_OutputOvercurrent | INV055 | Inverter 055 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_PVStringLoss | INV055 | Inverter 055 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_PassiveIslanding | INV055 | Inverter 055 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_PeripheralPortShortCircuit | INV055 | Inverter 055 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_PhaseWireShortCircuitedPE | INV055 | Inverter 055 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_PowerCurtailmentStatus | INV055 | Inverter 055 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_PowerFactor | INV055 | Inverter 055 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_PowerLimitationActiveGridCommand | INV055 | Inverter 055 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_ReactivePower | INV055 | Inverter 055 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV055_RemoteOFFStatus | INV055 | Inverter 055 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_Shutdown | INV055 | Inverter 055 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_ShutdownPowerRationing | INV055 | Inverter 055 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_SpotCheck | INV055 | Inverter 055 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_Standby | INV055 | Inverter 055 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_StringCurrentBackfeed | INV055 | Inverter 055 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_StringReverseConnection | INV055 | Inverter 055 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_StringReversePolarity | INV055 | Inverter 055 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_TotalEnergyYield | INV055 | Inverter 055 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV055_TransientACOvervoltage | INV055 | Inverter 055 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_UnstableGridFrequency | INV055 | Inverter 055 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_UpgradeFailed | INV055 | Inverter 055 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV055_WarningActive | INV055 | Inverter 055 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_ACCurrent | INV056 | Inverter 056 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_ACOvervoltage | INV056 | Inverter 056 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_ACUndervoltage | INV056 | Inverter 056 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_ACVoltage | INV056 | Inverter 056 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_AFCISelfCheckFailure | INV056 | Inverter 056 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_AbnormalGrounding | INV056 | Inverter 056 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_AbnormalPVModuleConfiguration | INV056 | Inverter 056 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_AbnormalResidualCurrent | INV056 | Inverter 056 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_AbnormalStringPower | INV056 | Inverter 056 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_ActiveIslanding | INV056 | Inverter 056 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_ActivePower | INV056 | Inverter 056 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_ApparentPower | INV056 | Inverter 056 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV056_BuiltPIDOperationAbnormal | INV056 | Inverter 056 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_CabinetOvertemperature | INV056 | Inverter 056 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_CommunicationFailure | INV056 | Inverter 056 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_CommunicationStatus | INV056 | Inverter 056 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_DCArcFault | INV056 | Inverter 056 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_DCCurrent | INV056 | Inverter 056 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_DCInsulationFault | INV056 | Inverter 056 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_DCOvervoltage | INV056 | Inverter 056 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_DCPower | INV056 | Inverter 056 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV056_DCVoltage | INV056 | Inverter 056 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_DailyEnergyYield | INV056 | Inverter 056 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV056_DeviceFault | INV056 | Inverter 056 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_ExternalFanAbnormal | INV056 | Inverter 056 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_FanFailure | INV056 | Inverter 056 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_Faulty | INV056 | Inverter 056 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_FaultyMonitoringUnit | INV056 | Inverter 056 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_FaultyPowerCollector | INV056 | Inverter 056 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_Frequency | INV056 | Inverter 056 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_GeneralFaultTrip | INV056 | Inverter 056 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_Grid | INV056 | Inverter 056 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GridConnectionDeratingInverterInternalCauses | INV056 | Inverter 056 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GridConnectionDeratingPowerRationing | INV056 | Inverter 056 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GridLoss | INV056 | Inverter 056 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GridOverfrequency | INV056 | Inverter 056 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GridOvervoltage | INV056 | Inverter 056 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GridTiedOffGridControllerAbnormal | INV056 | Inverter 056 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GridUnderfrequency | INV056 | Inverter 056 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GridUndervoltage | INV056 | Inverter 056 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GridVoltageImbalance | INV056 | Inverter 056 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_GroundFault | INV056 | Inverter 056 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_HighInputStringVoltageGround | INV056 | Inverter 056 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_HighStringInputVoltage | INV056 | Inverter 056 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_InverterEfficiency | INV056 | Inverter 056 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_InverterGridConnectionStatus | INV056 | Inverter 056 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_InverterOverTemperature | INV056 | Inverter 056 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_InverterRunningStopped | INV056 | Inverter 056 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_InverterStartupShutdownStatus | INV056 | Inverter 056 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_InverterTripHistoryAvailable | INV056 | Inverter 056 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_IslandingDetectionStatus | INV056 | Inverter 056 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_LicenseExpired | INV056 | Inverter 056 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_LockingStatus | INV056 | Inverter 056 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_LowInsulationResistance | INV056 | Inverter 056 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_NormalGridConnection | INV056 | Inverter 056 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_NormalShutdown | INV056 | Inverter 056 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_OffGridOutputOverload | INV056 | Inverter 056 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_OptimizerFault | INV056 | Inverter 056 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_OutputDCComponentOverhigh | INV056 | Inverter 056 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_OutputOvercurrent | INV056 | Inverter 056 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_PVStringLoss | INV056 | Inverter 056 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_PassiveIslanding | INV056 | Inverter 056 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_PeripheralPortShortCircuit | INV056 | Inverter 056 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_PhaseWireShortCircuitedPE | INV056 | Inverter 056 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_PowerCurtailmentStatus | INV056 | Inverter 056 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_PowerFactor | INV056 | Inverter 056 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_PowerLimitationActiveGridCommand | INV056 | Inverter 056 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_ReactivePower | INV056 | Inverter 056 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV056_RemoteOFFStatus | INV056 | Inverter 056 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_Shutdown | INV056 | Inverter 056 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_ShutdownPowerRationing | INV056 | Inverter 056 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_SpotCheck | INV056 | Inverter 056 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_Standby | INV056 | Inverter 056 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_StringCurrentBackfeed | INV056 | Inverter 056 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_StringReverseConnection | INV056 | Inverter 056 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_StringReversePolarity | INV056 | Inverter 056 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_TotalEnergyYield | INV056 | Inverter 056 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV056_TransientACOvervoltage | INV056 | Inverter 056 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_UnstableGridFrequency | INV056 | Inverter 056 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_UpgradeFailed | INV056 | Inverter 056 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV056_WarningActive | INV056 | Inverter 056 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_ACCurrent | INV057 | Inverter 057 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_ACOvervoltage | INV057 | Inverter 057 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_ACUndervoltage | INV057 | Inverter 057 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_ACVoltage | INV057 | Inverter 057 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_AFCISelfCheckFailure | INV057 | Inverter 057 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_AbnormalGrounding | INV057 | Inverter 057 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_AbnormalPVModuleConfiguration | INV057 | Inverter 057 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_AbnormalResidualCurrent | INV057 | Inverter 057 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_AbnormalStringPower | INV057 | Inverter 057 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_ActiveIslanding | INV057 | Inverter 057 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_ActivePower | INV057 | Inverter 057 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_ApparentPower | INV057 | Inverter 057 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV057_BuiltPIDOperationAbnormal | INV057 | Inverter 057 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_CabinetOvertemperature | INV057 | Inverter 057 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_CommunicationFailure | INV057 | Inverter 057 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_CommunicationStatus | INV057 | Inverter 057 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_DCArcFault | INV057 | Inverter 057 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_DCCurrent | INV057 | Inverter 057 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_DCInsulationFault | INV057 | Inverter 057 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_DCOvervoltage | INV057 | Inverter 057 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_DCPower | INV057 | Inverter 057 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV057_DCVoltage | INV057 | Inverter 057 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_DailyEnergyYield | INV057 | Inverter 057 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV057_DeviceFault | INV057 | Inverter 057 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_ExternalFanAbnormal | INV057 | Inverter 057 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_FanFailure | INV057 | Inverter 057 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_Faulty | INV057 | Inverter 057 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_FaultyMonitoringUnit | INV057 | Inverter 057 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_FaultyPowerCollector | INV057 | Inverter 057 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_Frequency | INV057 | Inverter 057 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_GeneralFaultTrip | INV057 | Inverter 057 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_Grid | INV057 | Inverter 057 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GridConnectionDeratingInverterInternalCauses | INV057 | Inverter 057 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GridConnectionDeratingPowerRationing | INV057 | Inverter 057 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GridLoss | INV057 | Inverter 057 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GridOverfrequency | INV057 | Inverter 057 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GridOvervoltage | INV057 | Inverter 057 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GridTiedOffGridControllerAbnormal | INV057 | Inverter 057 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GridUnderfrequency | INV057 | Inverter 057 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GridUndervoltage | INV057 | Inverter 057 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GridVoltageImbalance | INV057 | Inverter 057 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_GroundFault | INV057 | Inverter 057 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_HighInputStringVoltageGround | INV057 | Inverter 057 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_HighStringInputVoltage | INV057 | Inverter 057 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_InverterEfficiency | INV057 | Inverter 057 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_InverterGridConnectionStatus | INV057 | Inverter 057 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_InverterOverTemperature | INV057 | Inverter 057 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_InverterRunningStopped | INV057 | Inverter 057 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_InverterStartupShutdownStatus | INV057 | Inverter 057 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_InverterTripHistoryAvailable | INV057 | Inverter 057 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_IslandingDetectionStatus | INV057 | Inverter 057 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_LicenseExpired | INV057 | Inverter 057 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_LockingStatus | INV057 | Inverter 057 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_LowInsulationResistance | INV057 | Inverter 057 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_NormalGridConnection | INV057 | Inverter 057 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_NormalShutdown | INV057 | Inverter 057 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_OffGridOutputOverload | INV057 | Inverter 057 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_OptimizerFault | INV057 | Inverter 057 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_OutputDCComponentOverhigh | INV057 | Inverter 057 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_OutputOvercurrent | INV057 | Inverter 057 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_PVStringLoss | INV057 | Inverter 057 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_PassiveIslanding | INV057 | Inverter 057 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_PeripheralPortShortCircuit | INV057 | Inverter 057 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_PhaseWireShortCircuitedPE | INV057 | Inverter 057 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_PowerCurtailmentStatus | INV057 | Inverter 057 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_PowerFactor | INV057 | Inverter 057 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_PowerLimitationActiveGridCommand | INV057 | Inverter 057 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_ReactivePower | INV057 | Inverter 057 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV057_RemoteOFFStatus | INV057 | Inverter 057 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_Shutdown | INV057 | Inverter 057 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_ShutdownPowerRationing | INV057 | Inverter 057 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_SpotCheck | INV057 | Inverter 057 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_Standby | INV057 | Inverter 057 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_StringCurrentBackfeed | INV057 | Inverter 057 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_StringReverseConnection | INV057 | Inverter 057 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_StringReversePolarity | INV057 | Inverter 057 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_TotalEnergyYield | INV057 | Inverter 057 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV057_TransientACOvervoltage | INV057 | Inverter 057 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_UnstableGridFrequency | INV057 | Inverter 057 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_UpgradeFailed | INV057 | Inverter 057 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV057_WarningActive | INV057 | Inverter 057 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_ACCurrent | INV058 | Inverter 058 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_ACOvervoltage | INV058 | Inverter 058 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_ACUndervoltage | INV058 | Inverter 058 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_ACVoltage | INV058 | Inverter 058 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_AFCISelfCheckFailure | INV058 | Inverter 058 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_AbnormalGrounding | INV058 | Inverter 058 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_AbnormalPVModuleConfiguration | INV058 | Inverter 058 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_AbnormalResidualCurrent | INV058 | Inverter 058 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_AbnormalStringPower | INV058 | Inverter 058 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_ActiveIslanding | INV058 | Inverter 058 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_ActivePower | INV058 | Inverter 058 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_ApparentPower | INV058 | Inverter 058 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV058_BuiltPIDOperationAbnormal | INV058 | Inverter 058 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_CabinetOvertemperature | INV058 | Inverter 058 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_CommunicationFailure | INV058 | Inverter 058 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_CommunicationStatus | INV058 | Inverter 058 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_DCArcFault | INV058 | Inverter 058 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_DCCurrent | INV058 | Inverter 058 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_DCInsulationFault | INV058 | Inverter 058 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_DCOvervoltage | INV058 | Inverter 058 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_DCPower | INV058 | Inverter 058 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV058_DCVoltage | INV058 | Inverter 058 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_DailyEnergyYield | INV058 | Inverter 058 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV058_DeviceFault | INV058 | Inverter 058 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_ExternalFanAbnormal | INV058 | Inverter 058 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_FanFailure | INV058 | Inverter 058 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_Faulty | INV058 | Inverter 058 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_FaultyMonitoringUnit | INV058 | Inverter 058 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_FaultyPowerCollector | INV058 | Inverter 058 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_Frequency | INV058 | Inverter 058 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_GeneralFaultTrip | INV058 | Inverter 058 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_Grid | INV058 | Inverter 058 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GridConnectionDeratingInverterInternalCauses | INV058 | Inverter 058 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GridConnectionDeratingPowerRationing | INV058 | Inverter 058 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GridLoss | INV058 | Inverter 058 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GridOverfrequency | INV058 | Inverter 058 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GridOvervoltage | INV058 | Inverter 058 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GridTiedOffGridControllerAbnormal | INV058 | Inverter 058 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GridUnderfrequency | INV058 | Inverter 058 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GridUndervoltage | INV058 | Inverter 058 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GridVoltageImbalance | INV058 | Inverter 058 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_GroundFault | INV058 | Inverter 058 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_HighInputStringVoltageGround | INV058 | Inverter 058 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_HighStringInputVoltage | INV058 | Inverter 058 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_InverterEfficiency | INV058 | Inverter 058 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_InverterGridConnectionStatus | INV058 | Inverter 058 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_InverterOverTemperature | INV058 | Inverter 058 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_InverterRunningStopped | INV058 | Inverter 058 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_InverterStartupShutdownStatus | INV058 | Inverter 058 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_InverterTripHistoryAvailable | INV058 | Inverter 058 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_IslandingDetectionStatus | INV058 | Inverter 058 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_LicenseExpired | INV058 | Inverter 058 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_LockingStatus | INV058 | Inverter 058 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_LowInsulationResistance | INV058 | Inverter 058 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_NormalGridConnection | INV058 | Inverter 058 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_NormalShutdown | INV058 | Inverter 058 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_OffGridOutputOverload | INV058 | Inverter 058 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_OptimizerFault | INV058 | Inverter 058 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_OutputDCComponentOverhigh | INV058 | Inverter 058 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_OutputOvercurrent | INV058 | Inverter 058 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_PVStringLoss | INV058 | Inverter 058 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_PassiveIslanding | INV058 | Inverter 058 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_PeripheralPortShortCircuit | INV058 | Inverter 058 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_PhaseWireShortCircuitedPE | INV058 | Inverter 058 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_PowerCurtailmentStatus | INV058 | Inverter 058 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_PowerFactor | INV058 | Inverter 058 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_PowerLimitationActiveGridCommand | INV058 | Inverter 058 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_ReactivePower | INV058 | Inverter 058 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV058_RemoteOFFStatus | INV058 | Inverter 058 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_Shutdown | INV058 | Inverter 058 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_ShutdownPowerRationing | INV058 | Inverter 058 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_SpotCheck | INV058 | Inverter 058 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_Standby | INV058 | Inverter 058 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_StringCurrentBackfeed | INV058 | Inverter 058 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_StringReverseConnection | INV058 | Inverter 058 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_StringReversePolarity | INV058 | Inverter 058 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_TotalEnergyYield | INV058 | Inverter 058 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV058_TransientACOvervoltage | INV058 | Inverter 058 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_UnstableGridFrequency | INV058 | Inverter 058 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_UpgradeFailed | INV058 | Inverter 058 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV058_WarningActive | INV058 | Inverter 058 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_ACCurrent | INV059 | Inverter 059 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_ACOvervoltage | INV059 | Inverter 059 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_ACUndervoltage | INV059 | Inverter 059 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_ACVoltage | INV059 | Inverter 059 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_AFCISelfCheckFailure | INV059 | Inverter 059 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_AbnormalGrounding | INV059 | Inverter 059 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_AbnormalPVModuleConfiguration | INV059 | Inverter 059 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_AbnormalResidualCurrent | INV059 | Inverter 059 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_AbnormalStringPower | INV059 | Inverter 059 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_ActiveIslanding | INV059 | Inverter 059 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_ActivePower | INV059 | Inverter 059 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_ApparentPower | INV059 | Inverter 059 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV059_BuiltPIDOperationAbnormal | INV059 | Inverter 059 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_CabinetOvertemperature | INV059 | Inverter 059 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_CommunicationFailure | INV059 | Inverter 059 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_CommunicationStatus | INV059 | Inverter 059 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_DCArcFault | INV059 | Inverter 059 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_DCCurrent | INV059 | Inverter 059 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_DCInsulationFault | INV059 | Inverter 059 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_DCOvervoltage | INV059 | Inverter 059 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_DCPower | INV059 | Inverter 059 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV059_DCVoltage | INV059 | Inverter 059 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_DailyEnergyYield | INV059 | Inverter 059 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV059_DeviceFault | INV059 | Inverter 059 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_ExternalFanAbnormal | INV059 | Inverter 059 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_FanFailure | INV059 | Inverter 059 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_Faulty | INV059 | Inverter 059 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_FaultyMonitoringUnit | INV059 | Inverter 059 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_FaultyPowerCollector | INV059 | Inverter 059 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_Frequency | INV059 | Inverter 059 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_GeneralFaultTrip | INV059 | Inverter 059 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_Grid | INV059 | Inverter 059 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GridConnectionDeratingInverterInternalCauses | INV059 | Inverter 059 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GridConnectionDeratingPowerRationing | INV059 | Inverter 059 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GridLoss | INV059 | Inverter 059 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GridOverfrequency | INV059 | Inverter 059 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GridOvervoltage | INV059 | Inverter 059 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GridTiedOffGridControllerAbnormal | INV059 | Inverter 059 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GridUnderfrequency | INV059 | Inverter 059 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GridUndervoltage | INV059 | Inverter 059 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GridVoltageImbalance | INV059 | Inverter 059 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_GroundFault | INV059 | Inverter 059 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_HighInputStringVoltageGround | INV059 | Inverter 059 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_HighStringInputVoltage | INV059 | Inverter 059 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_InverterEfficiency | INV059 | Inverter 059 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_InverterGridConnectionStatus | INV059 | Inverter 059 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_InverterOverTemperature | INV059 | Inverter 059 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_InverterRunningStopped | INV059 | Inverter 059 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_InverterStartupShutdownStatus | INV059 | Inverter 059 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_InverterTripHistoryAvailable | INV059 | Inverter 059 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_IslandingDetectionStatus | INV059 | Inverter 059 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_LicenseExpired | INV059 | Inverter 059 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_LockingStatus | INV059 | Inverter 059 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_LowInsulationResistance | INV059 | Inverter 059 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_NormalGridConnection | INV059 | Inverter 059 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_NormalShutdown | INV059 | Inverter 059 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_OffGridOutputOverload | INV059 | Inverter 059 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_OptimizerFault | INV059 | Inverter 059 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_OutputDCComponentOverhigh | INV059 | Inverter 059 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_OutputOvercurrent | INV059 | Inverter 059 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_PVStringLoss | INV059 | Inverter 059 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_PassiveIslanding | INV059 | Inverter 059 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_PeripheralPortShortCircuit | INV059 | Inverter 059 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_PhaseWireShortCircuitedPE | INV059 | Inverter 059 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_PowerCurtailmentStatus | INV059 | Inverter 059 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_PowerFactor | INV059 | Inverter 059 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_PowerLimitationActiveGridCommand | INV059 | Inverter 059 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_ReactivePower | INV059 | Inverter 059 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV059_RemoteOFFStatus | INV059 | Inverter 059 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_Shutdown | INV059 | Inverter 059 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_ShutdownPowerRationing | INV059 | Inverter 059 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_SpotCheck | INV059 | Inverter 059 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_Standby | INV059 | Inverter 059 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_StringCurrentBackfeed | INV059 | Inverter 059 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_StringReverseConnection | INV059 | Inverter 059 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_StringReversePolarity | INV059 | Inverter 059 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_TotalEnergyYield | INV059 | Inverter 059 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV059_TransientACOvervoltage | INV059 | Inverter 059 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_UnstableGridFrequency | INV059 | Inverter 059 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_UpgradeFailed | INV059 | Inverter 059 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV059_WarningActive | INV059 | Inverter 059 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_ACCurrent | INV060 | Inverter 060 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_ACOvervoltage | INV060 | Inverter 060 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_ACUndervoltage | INV060 | Inverter 060 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_ACVoltage | INV060 | Inverter 060 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_AFCISelfCheckFailure | INV060 | Inverter 060 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_AbnormalGrounding | INV060 | Inverter 060 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_AbnormalPVModuleConfiguration | INV060 | Inverter 060 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_AbnormalResidualCurrent | INV060 | Inverter 060 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_AbnormalStringPower | INV060 | Inverter 060 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_ActiveIslanding | INV060 | Inverter 060 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_ActivePower | INV060 | Inverter 060 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_ApparentPower | INV060 | Inverter 060 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV060_BuiltPIDOperationAbnormal | INV060 | Inverter 060 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_CabinetOvertemperature | INV060 | Inverter 060 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_CommunicationFailure | INV060 | Inverter 060 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_CommunicationStatus | INV060 | Inverter 060 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_DCArcFault | INV060 | Inverter 060 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_DCCurrent | INV060 | Inverter 060 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_DCInsulationFault | INV060 | Inverter 060 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_DCOvervoltage | INV060 | Inverter 060 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_DCPower | INV060 | Inverter 060 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV060_DCVoltage | INV060 | Inverter 060 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_DailyEnergyYield | INV060 | Inverter 060 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV060_DeviceFault | INV060 | Inverter 060 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_ExternalFanAbnormal | INV060 | Inverter 060 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_FanFailure | INV060 | Inverter 060 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_Faulty | INV060 | Inverter 060 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_FaultyMonitoringUnit | INV060 | Inverter 060 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_FaultyPowerCollector | INV060 | Inverter 060 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_Frequency | INV060 | Inverter 060 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_GeneralFaultTrip | INV060 | Inverter 060 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_Grid | INV060 | Inverter 060 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GridConnectionDeratingInverterInternalCauses | INV060 | Inverter 060 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GridConnectionDeratingPowerRationing | INV060 | Inverter 060 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GridLoss | INV060 | Inverter 060 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GridOverfrequency | INV060 | Inverter 060 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GridOvervoltage | INV060 | Inverter 060 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GridTiedOffGridControllerAbnormal | INV060 | Inverter 060 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GridUnderfrequency | INV060 | Inverter 060 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GridUndervoltage | INV060 | Inverter 060 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GridVoltageImbalance | INV060 | Inverter 060 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_GroundFault | INV060 | Inverter 060 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_HighInputStringVoltageGround | INV060 | Inverter 060 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_HighStringInputVoltage | INV060 | Inverter 060 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_InverterEfficiency | INV060 | Inverter 060 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_InverterGridConnectionStatus | INV060 | Inverter 060 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_InverterOverTemperature | INV060 | Inverter 060 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_InverterRunningStopped | INV060 | Inverter 060 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_InverterStartupShutdownStatus | INV060 | Inverter 060 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_InverterTripHistoryAvailable | INV060 | Inverter 060 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_IslandingDetectionStatus | INV060 | Inverter 060 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_LicenseExpired | INV060 | Inverter 060 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_LockingStatus | INV060 | Inverter 060 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_LowInsulationResistance | INV060 | Inverter 060 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_NormalGridConnection | INV060 | Inverter 060 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_NormalShutdown | INV060 | Inverter 060 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_OffGridOutputOverload | INV060 | Inverter 060 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_OptimizerFault | INV060 | Inverter 060 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_OutputDCComponentOverhigh | INV060 | Inverter 060 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_OutputOvercurrent | INV060 | Inverter 060 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_PVStringLoss | INV060 | Inverter 060 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_PassiveIslanding | INV060 | Inverter 060 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_PeripheralPortShortCircuit | INV060 | Inverter 060 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_PhaseWireShortCircuitedPE | INV060 | Inverter 060 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_PowerCurtailmentStatus | INV060 | Inverter 060 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_PowerFactor | INV060 | Inverter 060 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_PowerLimitationActiveGridCommand | INV060 | Inverter 060 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_ReactivePower | INV060 | Inverter 060 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV060_RemoteOFFStatus | INV060 | Inverter 060 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_Shutdown | INV060 | Inverter 060 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_ShutdownPowerRationing | INV060 | Inverter 060 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_SpotCheck | INV060 | Inverter 060 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_Standby | INV060 | Inverter 060 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_StringCurrentBackfeed | INV060 | Inverter 060 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_StringReverseConnection | INV060 | Inverter 060 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_StringReversePolarity | INV060 | Inverter 060 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_TotalEnergyYield | INV060 | Inverter 060 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV060_TransientACOvervoltage | INV060 | Inverter 060 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_UnstableGridFrequency | INV060 | Inverter 060 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_UpgradeFailed | INV060 | Inverter 060 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV060_WarningActive | INV060 | Inverter 060 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_ACCurrent | INV061 | Inverter 061 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_ACOvervoltage | INV061 | Inverter 061 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_ACUndervoltage | INV061 | Inverter 061 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_ACVoltage | INV061 | Inverter 061 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_AFCISelfCheckFailure | INV061 | Inverter 061 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_AbnormalGrounding | INV061 | Inverter 061 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_AbnormalPVModuleConfiguration | INV061 | Inverter 061 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_AbnormalResidualCurrent | INV061 | Inverter 061 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_AbnormalStringPower | INV061 | Inverter 061 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_ActiveIslanding | INV061 | Inverter 061 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_ActivePower | INV061 | Inverter 061 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_ApparentPower | INV061 | Inverter 061 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV061_BuiltPIDOperationAbnormal | INV061 | Inverter 061 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_CabinetOvertemperature | INV061 | Inverter 061 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_CommunicationFailure | INV061 | Inverter 061 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_CommunicationStatus | INV061 | Inverter 061 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_DCArcFault | INV061 | Inverter 061 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_DCCurrent | INV061 | Inverter 061 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_DCInsulationFault | INV061 | Inverter 061 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_DCOvervoltage | INV061 | Inverter 061 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_DCPower | INV061 | Inverter 061 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV061_DCVoltage | INV061 | Inverter 061 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_DailyEnergyYield | INV061 | Inverter 061 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV061_DeviceFault | INV061 | Inverter 061 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_ExternalFanAbnormal | INV061 | Inverter 061 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_FanFailure | INV061 | Inverter 061 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_Faulty | INV061 | Inverter 061 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_FaultyMonitoringUnit | INV061 | Inverter 061 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_FaultyPowerCollector | INV061 | Inverter 061 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_Frequency | INV061 | Inverter 061 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_GeneralFaultTrip | INV061 | Inverter 061 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_Grid | INV061 | Inverter 061 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GridConnectionDeratingInverterInternalCauses | INV061 | Inverter 061 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GridConnectionDeratingPowerRationing | INV061 | Inverter 061 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GridLoss | INV061 | Inverter 061 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GridOverfrequency | INV061 | Inverter 061 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GridOvervoltage | INV061 | Inverter 061 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GridTiedOffGridControllerAbnormal | INV061 | Inverter 061 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GridUnderfrequency | INV061 | Inverter 061 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GridUndervoltage | INV061 | Inverter 061 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GridVoltageImbalance | INV061 | Inverter 061 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_GroundFault | INV061 | Inverter 061 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_HighInputStringVoltageGround | INV061 | Inverter 061 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_HighStringInputVoltage | INV061 | Inverter 061 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_InverterEfficiency | INV061 | Inverter 061 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_InverterGridConnectionStatus | INV061 | Inverter 061 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_InverterOverTemperature | INV061 | Inverter 061 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_InverterRunningStopped | INV061 | Inverter 061 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_InverterStartupShutdownStatus | INV061 | Inverter 061 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_InverterTripHistoryAvailable | INV061 | Inverter 061 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_IslandingDetectionStatus | INV061 | Inverter 061 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_LicenseExpired | INV061 | Inverter 061 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_LockingStatus | INV061 | Inverter 061 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_LowInsulationResistance | INV061 | Inverter 061 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_NormalGridConnection | INV061 | Inverter 061 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_NormalShutdown | INV061 | Inverter 061 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_OffGridOutputOverload | INV061 | Inverter 061 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_OptimizerFault | INV061 | Inverter 061 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_OutputDCComponentOverhigh | INV061 | Inverter 061 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_OutputOvercurrent | INV061 | Inverter 061 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_PVStringLoss | INV061 | Inverter 061 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_PassiveIslanding | INV061 | Inverter 061 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_PeripheralPortShortCircuit | INV061 | Inverter 061 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_PhaseWireShortCircuitedPE | INV061 | Inverter 061 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_PowerCurtailmentStatus | INV061 | Inverter 061 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_PowerFactor | INV061 | Inverter 061 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_PowerLimitationActiveGridCommand | INV061 | Inverter 061 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_ReactivePower | INV061 | Inverter 061 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV061_RemoteOFFStatus | INV061 | Inverter 061 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_Shutdown | INV061 | Inverter 061 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_ShutdownPowerRationing | INV061 | Inverter 061 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_SpotCheck | INV061 | Inverter 061 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_Standby | INV061 | Inverter 061 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_StringCurrentBackfeed | INV061 | Inverter 061 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_StringReverseConnection | INV061 | Inverter 061 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_StringReversePolarity | INV061 | Inverter 061 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_TotalEnergyYield | INV061 | Inverter 061 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV061_TransientACOvervoltage | INV061 | Inverter 061 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_UnstableGridFrequency | INV061 | Inverter 061 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_UpgradeFailed | INV061 | Inverter 061 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV061_WarningActive | INV061 | Inverter 061 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_ACCurrent | INV062 | Inverter 062 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_ACOvervoltage | INV062 | Inverter 062 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_ACUndervoltage | INV062 | Inverter 062 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_ACVoltage | INV062 | Inverter 062 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_AFCISelfCheckFailure | INV062 | Inverter 062 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_AbnormalGrounding | INV062 | Inverter 062 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_AbnormalPVModuleConfiguration | INV062 | Inverter 062 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_AbnormalResidualCurrent | INV062 | Inverter 062 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_AbnormalStringPower | INV062 | Inverter 062 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_ActiveIslanding | INV062 | Inverter 062 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_ActivePower | INV062 | Inverter 062 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_ApparentPower | INV062 | Inverter 062 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV062_BuiltPIDOperationAbnormal | INV062 | Inverter 062 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_CabinetOvertemperature | INV062 | Inverter 062 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_CommunicationFailure | INV062 | Inverter 062 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_CommunicationStatus | INV062 | Inverter 062 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_DCArcFault | INV062 | Inverter 062 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_DCCurrent | INV062 | Inverter 062 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_DCInsulationFault | INV062 | Inverter 062 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_DCOvervoltage | INV062 | Inverter 062 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_DCPower | INV062 | Inverter 062 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV062_DCVoltage | INV062 | Inverter 062 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_DailyEnergyYield | INV062 | Inverter 062 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV062_DeviceFault | INV062 | Inverter 062 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_ExternalFanAbnormal | INV062 | Inverter 062 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_FanFailure | INV062 | Inverter 062 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_Faulty | INV062 | Inverter 062 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_FaultyMonitoringUnit | INV062 | Inverter 062 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_FaultyPowerCollector | INV062 | Inverter 062 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_Frequency | INV062 | Inverter 062 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_GeneralFaultTrip | INV062 | Inverter 062 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_Grid | INV062 | Inverter 062 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GridConnectionDeratingInverterInternalCauses | INV062 | Inverter 062 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GridConnectionDeratingPowerRationing | INV062 | Inverter 062 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GridLoss | INV062 | Inverter 062 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GridOverfrequency | INV062 | Inverter 062 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GridOvervoltage | INV062 | Inverter 062 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GridTiedOffGridControllerAbnormal | INV062 | Inverter 062 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GridUnderfrequency | INV062 | Inverter 062 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GridUndervoltage | INV062 | Inverter 062 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GridVoltageImbalance | INV062 | Inverter 062 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_GroundFault | INV062 | Inverter 062 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_HighInputStringVoltageGround | INV062 | Inverter 062 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_HighStringInputVoltage | INV062 | Inverter 062 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_InverterEfficiency | INV062 | Inverter 062 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_InverterGridConnectionStatus | INV062 | Inverter 062 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_InverterOverTemperature | INV062 | Inverter 062 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_InverterRunningStopped | INV062 | Inverter 062 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_InverterStartupShutdownStatus | INV062 | Inverter 062 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_InverterTripHistoryAvailable | INV062 | Inverter 062 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_IslandingDetectionStatus | INV062 | Inverter 062 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_LicenseExpired | INV062 | Inverter 062 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_LockingStatus | INV062 | Inverter 062 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_LowInsulationResistance | INV062 | Inverter 062 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_NormalGridConnection | INV062 | Inverter 062 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_NormalShutdown | INV062 | Inverter 062 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_OffGridOutputOverload | INV062 | Inverter 062 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_OptimizerFault | INV062 | Inverter 062 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_OutputDCComponentOverhigh | INV062 | Inverter 062 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_OutputOvercurrent | INV062 | Inverter 062 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_PVStringLoss | INV062 | Inverter 062 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_PassiveIslanding | INV062 | Inverter 062 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_PeripheralPortShortCircuit | INV062 | Inverter 062 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_PhaseWireShortCircuitedPE | INV062 | Inverter 062 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_PowerCurtailmentStatus | INV062 | Inverter 062 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_PowerFactor | INV062 | Inverter 062 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_PowerLimitationActiveGridCommand | INV062 | Inverter 062 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_ReactivePower | INV062 | Inverter 062 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV062_RemoteOFFStatus | INV062 | Inverter 062 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_Shutdown | INV062 | Inverter 062 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_ShutdownPowerRationing | INV062 | Inverter 062 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_SpotCheck | INV062 | Inverter 062 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_Standby | INV062 | Inverter 062 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_StringCurrentBackfeed | INV062 | Inverter 062 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_StringReverseConnection | INV062 | Inverter 062 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_StringReversePolarity | INV062 | Inverter 062 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_TotalEnergyYield | INV062 | Inverter 062 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV062_TransientACOvervoltage | INV062 | Inverter 062 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_UnstableGridFrequency | INV062 | Inverter 062 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_UpgradeFailed | INV062 | Inverter 062 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV062_WarningActive | INV062 | Inverter 062 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_ACCurrent | INV063 | Inverter 063 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_ACOvervoltage | INV063 | Inverter 063 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_ACUndervoltage | INV063 | Inverter 063 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_ACVoltage | INV063 | Inverter 063 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_AFCISelfCheckFailure | INV063 | Inverter 063 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_AbnormalGrounding | INV063 | Inverter 063 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_AbnormalPVModuleConfiguration | INV063 | Inverter 063 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_AbnormalResidualCurrent | INV063 | Inverter 063 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_AbnormalStringPower | INV063 | Inverter 063 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_ActiveIslanding | INV063 | Inverter 063 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_ActivePower | INV063 | Inverter 063 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_ApparentPower | INV063 | Inverter 063 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV063_BuiltPIDOperationAbnormal | INV063 | Inverter 063 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_CabinetOvertemperature | INV063 | Inverter 063 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_CommunicationFailure | INV063 | Inverter 063 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_CommunicationStatus | INV063 | Inverter 063 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_DCArcFault | INV063 | Inverter 063 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_DCCurrent | INV063 | Inverter 063 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_DCInsulationFault | INV063 | Inverter 063 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_DCOvervoltage | INV063 | Inverter 063 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_DCPower | INV063 | Inverter 063 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV063_DCVoltage | INV063 | Inverter 063 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_DailyEnergyYield | INV063 | Inverter 063 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV063_DeviceFault | INV063 | Inverter 063 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_ExternalFanAbnormal | INV063 | Inverter 063 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_FanFailure | INV063 | Inverter 063 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_Faulty | INV063 | Inverter 063 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_FaultyMonitoringUnit | INV063 | Inverter 063 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_FaultyPowerCollector | INV063 | Inverter 063 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_Frequency | INV063 | Inverter 063 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_GeneralFaultTrip | INV063 | Inverter 063 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_Grid | INV063 | Inverter 063 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GridConnectionDeratingInverterInternalCauses | INV063 | Inverter 063 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GridConnectionDeratingPowerRationing | INV063 | Inverter 063 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GridLoss | INV063 | Inverter 063 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GridOverfrequency | INV063 | Inverter 063 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GridOvervoltage | INV063 | Inverter 063 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GridTiedOffGridControllerAbnormal | INV063 | Inverter 063 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GridUnderfrequency | INV063 | Inverter 063 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GridUndervoltage | INV063 | Inverter 063 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GridVoltageImbalance | INV063 | Inverter 063 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_GroundFault | INV063 | Inverter 063 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_HighInputStringVoltageGround | INV063 | Inverter 063 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_HighStringInputVoltage | INV063 | Inverter 063 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_InverterEfficiency | INV063 | Inverter 063 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_InverterGridConnectionStatus | INV063 | Inverter 063 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_InverterOverTemperature | INV063 | Inverter 063 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_InverterRunningStopped | INV063 | Inverter 063 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_InverterStartupShutdownStatus | INV063 | Inverter 063 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_InverterTripHistoryAvailable | INV063 | Inverter 063 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_IslandingDetectionStatus | INV063 | Inverter 063 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_LicenseExpired | INV063 | Inverter 063 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_LockingStatus | INV063 | Inverter 063 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_LowInsulationResistance | INV063 | Inverter 063 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_NormalGridConnection | INV063 | Inverter 063 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_NormalShutdown | INV063 | Inverter 063 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_OffGridOutputOverload | INV063 | Inverter 063 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_OptimizerFault | INV063 | Inverter 063 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_OutputDCComponentOverhigh | INV063 | Inverter 063 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_OutputOvercurrent | INV063 | Inverter 063 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_PVStringLoss | INV063 | Inverter 063 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_PassiveIslanding | INV063 | Inverter 063 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_PeripheralPortShortCircuit | INV063 | Inverter 063 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_PhaseWireShortCircuitedPE | INV063 | Inverter 063 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_PowerCurtailmentStatus | INV063 | Inverter 063 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_PowerFactor | INV063 | Inverter 063 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_PowerLimitationActiveGridCommand | INV063 | Inverter 063 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_ReactivePower | INV063 | Inverter 063 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV063_RemoteOFFStatus | INV063 | Inverter 063 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_Shutdown | INV063 | Inverter 063 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_ShutdownPowerRationing | INV063 | Inverter 063 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_SpotCheck | INV063 | Inverter 063 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_Standby | INV063 | Inverter 063 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_StringCurrentBackfeed | INV063 | Inverter 063 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_StringReverseConnection | INV063 | Inverter 063 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_StringReversePolarity | INV063 | Inverter 063 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_TotalEnergyYield | INV063 | Inverter 063 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV063_TransientACOvervoltage | INV063 | Inverter 063 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_UnstableGridFrequency | INV063 | Inverter 063 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_UpgradeFailed | INV063 | Inverter 063 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV063_WarningActive | INV063 | Inverter 063 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_ACCurrent | INV064 | Inverter 064 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_ACOvervoltage | INV064 | Inverter 064 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_ACUndervoltage | INV064 | Inverter 064 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_ACVoltage | INV064 | Inverter 064 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_AFCISelfCheckFailure | INV064 | Inverter 064 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_AbnormalGrounding | INV064 | Inverter 064 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_AbnormalPVModuleConfiguration | INV064 | Inverter 064 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_AbnormalResidualCurrent | INV064 | Inverter 064 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_AbnormalStringPower | INV064 | Inverter 064 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_ActiveIslanding | INV064 | Inverter 064 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_ActivePower | INV064 | Inverter 064 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_ApparentPower | INV064 | Inverter 064 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV064_BuiltPIDOperationAbnormal | INV064 | Inverter 064 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_CabinetOvertemperature | INV064 | Inverter 064 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_CommunicationFailure | INV064 | Inverter 064 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_CommunicationStatus | INV064 | Inverter 064 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_DCArcFault | INV064 | Inverter 064 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_DCCurrent | INV064 | Inverter 064 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_DCInsulationFault | INV064 | Inverter 064 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_DCOvervoltage | INV064 | Inverter 064 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_DCPower | INV064 | Inverter 064 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV064_DCVoltage | INV064 | Inverter 064 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_DailyEnergyYield | INV064 | Inverter 064 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV064_DeviceFault | INV064 | Inverter 064 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_ExternalFanAbnormal | INV064 | Inverter 064 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_FanFailure | INV064 | Inverter 064 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_Faulty | INV064 | Inverter 064 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_FaultyMonitoringUnit | INV064 | Inverter 064 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_FaultyPowerCollector | INV064 | Inverter 064 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_Frequency | INV064 | Inverter 064 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_GeneralFaultTrip | INV064 | Inverter 064 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_Grid | INV064 | Inverter 064 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GridConnectionDeratingInverterInternalCauses | INV064 | Inverter 064 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GridConnectionDeratingPowerRationing | INV064 | Inverter 064 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GridLoss | INV064 | Inverter 064 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GridOverfrequency | INV064 | Inverter 064 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GridOvervoltage | INV064 | Inverter 064 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GridTiedOffGridControllerAbnormal | INV064 | Inverter 064 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GridUnderfrequency | INV064 | Inverter 064 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GridUndervoltage | INV064 | Inverter 064 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GridVoltageImbalance | INV064 | Inverter 064 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_GroundFault | INV064 | Inverter 064 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_HighInputStringVoltageGround | INV064 | Inverter 064 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_HighStringInputVoltage | INV064 | Inverter 064 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_InverterEfficiency | INV064 | Inverter 064 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_InverterGridConnectionStatus | INV064 | Inverter 064 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_InverterOverTemperature | INV064 | Inverter 064 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_InverterRunningStopped | INV064 | Inverter 064 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_InverterStartupShutdownStatus | INV064 | Inverter 064 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_InverterTripHistoryAvailable | INV064 | Inverter 064 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_IslandingDetectionStatus | INV064 | Inverter 064 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_LicenseExpired | INV064 | Inverter 064 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_LockingStatus | INV064 | Inverter 064 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_LowInsulationResistance | INV064 | Inverter 064 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_NormalGridConnection | INV064 | Inverter 064 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_NormalShutdown | INV064 | Inverter 064 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_OffGridOutputOverload | INV064 | Inverter 064 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_OptimizerFault | INV064 | Inverter 064 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_OutputDCComponentOverhigh | INV064 | Inverter 064 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_OutputOvercurrent | INV064 | Inverter 064 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_PVStringLoss | INV064 | Inverter 064 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_PassiveIslanding | INV064 | Inverter 064 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_PeripheralPortShortCircuit | INV064 | Inverter 064 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_PhaseWireShortCircuitedPE | INV064 | Inverter 064 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_PowerCurtailmentStatus | INV064 | Inverter 064 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_PowerFactor | INV064 | Inverter 064 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_PowerLimitationActiveGridCommand | INV064 | Inverter 064 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_ReactivePower | INV064 | Inverter 064 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV064_RemoteOFFStatus | INV064 | Inverter 064 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_Shutdown | INV064 | Inverter 064 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_ShutdownPowerRationing | INV064 | Inverter 064 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_SpotCheck | INV064 | Inverter 064 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_Standby | INV064 | Inverter 064 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_StringCurrentBackfeed | INV064 | Inverter 064 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_StringReverseConnection | INV064 | Inverter 064 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_StringReversePolarity | INV064 | Inverter 064 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_TotalEnergyYield | INV064 | Inverter 064 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV064_TransientACOvervoltage | INV064 | Inverter 064 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_UnstableGridFrequency | INV064 | Inverter 064 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_UpgradeFailed | INV064 | Inverter 064 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV064_WarningActive | INV064 | Inverter 064 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_ACCurrent | INV065 | Inverter 065 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_ACOvervoltage | INV065 | Inverter 065 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_ACUndervoltage | INV065 | Inverter 065 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_ACVoltage | INV065 | Inverter 065 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_AFCISelfCheckFailure | INV065 | Inverter 065 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_AbnormalGrounding | INV065 | Inverter 065 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_AbnormalPVModuleConfiguration | INV065 | Inverter 065 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_AbnormalResidualCurrent | INV065 | Inverter 065 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_AbnormalStringPower | INV065 | Inverter 065 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_ActiveIslanding | INV065 | Inverter 065 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_ActivePower | INV065 | Inverter 065 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_ApparentPower | INV065 | Inverter 065 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV065_BuiltPIDOperationAbnormal | INV065 | Inverter 065 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_CabinetOvertemperature | INV065 | Inverter 065 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_CommunicationFailure | INV065 | Inverter 065 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_CommunicationStatus | INV065 | Inverter 065 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_DCArcFault | INV065 | Inverter 065 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_DCCurrent | INV065 | Inverter 065 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_DCInsulationFault | INV065 | Inverter 065 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_DCOvervoltage | INV065 | Inverter 065 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_DCPower | INV065 | Inverter 065 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV065_DCVoltage | INV065 | Inverter 065 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_DailyEnergyYield | INV065 | Inverter 065 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV065_DeviceFault | INV065 | Inverter 065 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_ExternalFanAbnormal | INV065 | Inverter 065 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_FanFailure | INV065 | Inverter 065 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_Faulty | INV065 | Inverter 065 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_FaultyMonitoringUnit | INV065 | Inverter 065 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_FaultyPowerCollector | INV065 | Inverter 065 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_Frequency | INV065 | Inverter 065 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_GeneralFaultTrip | INV065 | Inverter 065 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_Grid | INV065 | Inverter 065 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GridConnectionDeratingInverterInternalCauses | INV065 | Inverter 065 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GridConnectionDeratingPowerRationing | INV065 | Inverter 065 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GridLoss | INV065 | Inverter 065 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GridOverfrequency | INV065 | Inverter 065 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GridOvervoltage | INV065 | Inverter 065 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GridTiedOffGridControllerAbnormal | INV065 | Inverter 065 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GridUnderfrequency | INV065 | Inverter 065 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GridUndervoltage | INV065 | Inverter 065 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GridVoltageImbalance | INV065 | Inverter 065 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_GroundFault | INV065 | Inverter 065 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_HighInputStringVoltageGround | INV065 | Inverter 065 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_HighStringInputVoltage | INV065 | Inverter 065 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_InverterEfficiency | INV065 | Inverter 065 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_InverterGridConnectionStatus | INV065 | Inverter 065 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_InverterOverTemperature | INV065 | Inverter 065 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_InverterRunningStopped | INV065 | Inverter 065 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_InverterStartupShutdownStatus | INV065 | Inverter 065 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_InverterTripHistoryAvailable | INV065 | Inverter 065 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_IslandingDetectionStatus | INV065 | Inverter 065 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_LicenseExpired | INV065 | Inverter 065 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_LockingStatus | INV065 | Inverter 065 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_LowInsulationResistance | INV065 | Inverter 065 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_NormalGridConnection | INV065 | Inverter 065 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_NormalShutdown | INV065 | Inverter 065 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_OffGridOutputOverload | INV065 | Inverter 065 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_OptimizerFault | INV065 | Inverter 065 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_OutputDCComponentOverhigh | INV065 | Inverter 065 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_OutputOvercurrent | INV065 | Inverter 065 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_PVStringLoss | INV065 | Inverter 065 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_PassiveIslanding | INV065 | Inverter 065 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_PeripheralPortShortCircuit | INV065 | Inverter 065 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_PhaseWireShortCircuitedPE | INV065 | Inverter 065 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_PowerCurtailmentStatus | INV065 | Inverter 065 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_PowerFactor | INV065 | Inverter 065 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_PowerLimitationActiveGridCommand | INV065 | Inverter 065 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_ReactivePower | INV065 | Inverter 065 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV065_RemoteOFFStatus | INV065 | Inverter 065 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_Shutdown | INV065 | Inverter 065 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_ShutdownPowerRationing | INV065 | Inverter 065 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_SpotCheck | INV065 | Inverter 065 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_Standby | INV065 | Inverter 065 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_StringCurrentBackfeed | INV065 | Inverter 065 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_StringReverseConnection | INV065 | Inverter 065 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_StringReversePolarity | INV065 | Inverter 065 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_TotalEnergyYield | INV065 | Inverter 065 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV065_TransientACOvervoltage | INV065 | Inverter 065 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_UnstableGridFrequency | INV065 | Inverter 065 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_UpgradeFailed | INV065 | Inverter 065 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV065_WarningActive | INV065 | Inverter 065 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_ACCurrent | INV066 | Inverter 066 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_ACOvervoltage | INV066 | Inverter 066 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_ACUndervoltage | INV066 | Inverter 066 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_ACVoltage | INV066 | Inverter 066 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_AFCISelfCheckFailure | INV066 | Inverter 066 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_AbnormalGrounding | INV066 | Inverter 066 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_AbnormalPVModuleConfiguration | INV066 | Inverter 066 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_AbnormalResidualCurrent | INV066 | Inverter 066 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_AbnormalStringPower | INV066 | Inverter 066 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_ActiveIslanding | INV066 | Inverter 066 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_ActivePower | INV066 | Inverter 066 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_ApparentPower | INV066 | Inverter 066 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV066_BuiltPIDOperationAbnormal | INV066 | Inverter 066 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_CabinetOvertemperature | INV066 | Inverter 066 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_CommunicationFailure | INV066 | Inverter 066 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_CommunicationStatus | INV066 | Inverter 066 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_DCArcFault | INV066 | Inverter 066 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_DCCurrent | INV066 | Inverter 066 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_DCInsulationFault | INV066 | Inverter 066 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_DCOvervoltage | INV066 | Inverter 066 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_DCPower | INV066 | Inverter 066 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV066_DCVoltage | INV066 | Inverter 066 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_DailyEnergyYield | INV066 | Inverter 066 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV066_DeviceFault | INV066 | Inverter 066 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_ExternalFanAbnormal | INV066 | Inverter 066 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_FanFailure | INV066 | Inverter 066 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_Faulty | INV066 | Inverter 066 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_FaultyMonitoringUnit | INV066 | Inverter 066 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_FaultyPowerCollector | INV066 | Inverter 066 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_Frequency | INV066 | Inverter 066 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_GeneralFaultTrip | INV066 | Inverter 066 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_Grid | INV066 | Inverter 066 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GridConnectionDeratingInverterInternalCauses | INV066 | Inverter 066 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GridConnectionDeratingPowerRationing | INV066 | Inverter 066 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GridLoss | INV066 | Inverter 066 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GridOverfrequency | INV066 | Inverter 066 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GridOvervoltage | INV066 | Inverter 066 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GridTiedOffGridControllerAbnormal | INV066 | Inverter 066 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GridUnderfrequency | INV066 | Inverter 066 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GridUndervoltage | INV066 | Inverter 066 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GridVoltageImbalance | INV066 | Inverter 066 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_GroundFault | INV066 | Inverter 066 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_HighInputStringVoltageGround | INV066 | Inverter 066 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_HighStringInputVoltage | INV066 | Inverter 066 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_InverterEfficiency | INV066 | Inverter 066 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_InverterGridConnectionStatus | INV066 | Inverter 066 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_InverterOverTemperature | INV066 | Inverter 066 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_InverterRunningStopped | INV066 | Inverter 066 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_InverterStartupShutdownStatus | INV066 | Inverter 066 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_InverterTripHistoryAvailable | INV066 | Inverter 066 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_IslandingDetectionStatus | INV066 | Inverter 066 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_LicenseExpired | INV066 | Inverter 066 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_LockingStatus | INV066 | Inverter 066 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_LowInsulationResistance | INV066 | Inverter 066 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_NormalGridConnection | INV066 | Inverter 066 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_NormalShutdown | INV066 | Inverter 066 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_OffGridOutputOverload | INV066 | Inverter 066 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_OptimizerFault | INV066 | Inverter 066 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_OutputDCComponentOverhigh | INV066 | Inverter 066 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_OutputOvercurrent | INV066 | Inverter 066 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_PVStringLoss | INV066 | Inverter 066 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_PassiveIslanding | INV066 | Inverter 066 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_PeripheralPortShortCircuit | INV066 | Inverter 066 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_PhaseWireShortCircuitedPE | INV066 | Inverter 066 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_PowerCurtailmentStatus | INV066 | Inverter 066 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_PowerFactor | INV066 | Inverter 066 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_PowerLimitationActiveGridCommand | INV066 | Inverter 066 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_ReactivePower | INV066 | Inverter 066 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV066_RemoteOFFStatus | INV066 | Inverter 066 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_Shutdown | INV066 | Inverter 066 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_ShutdownPowerRationing | INV066 | Inverter 066 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_SpotCheck | INV066 | Inverter 066 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_Standby | INV066 | Inverter 066 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_StringCurrentBackfeed | INV066 | Inverter 066 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_StringReverseConnection | INV066 | Inverter 066 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_StringReversePolarity | INV066 | Inverter 066 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_TotalEnergyYield | INV066 | Inverter 066 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV066_TransientACOvervoltage | INV066 | Inverter 066 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_UnstableGridFrequency | INV066 | Inverter 066 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_UpgradeFailed | INV066 | Inverter 066 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV066_WarningActive | INV066 | Inverter 066 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_ACCurrent | INV067 | Inverter 067 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_ACOvervoltage | INV067 | Inverter 067 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_ACUndervoltage | INV067 | Inverter 067 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_ACVoltage | INV067 | Inverter 067 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_AFCISelfCheckFailure | INV067 | Inverter 067 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_AbnormalGrounding | INV067 | Inverter 067 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_AbnormalPVModuleConfiguration | INV067 | Inverter 067 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_AbnormalResidualCurrent | INV067 | Inverter 067 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_AbnormalStringPower | INV067 | Inverter 067 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_ActiveIslanding | INV067 | Inverter 067 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_ActivePower | INV067 | Inverter 067 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_ApparentPower | INV067 | Inverter 067 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV067_BuiltPIDOperationAbnormal | INV067 | Inverter 067 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_CabinetOvertemperature | INV067 | Inverter 067 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_CommunicationFailure | INV067 | Inverter 067 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_CommunicationStatus | INV067 | Inverter 067 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_DCArcFault | INV067 | Inverter 067 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_DCCurrent | INV067 | Inverter 067 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_DCInsulationFault | INV067 | Inverter 067 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_DCOvervoltage | INV067 | Inverter 067 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_DCPower | INV067 | Inverter 067 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV067_DCVoltage | INV067 | Inverter 067 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_DailyEnergyYield | INV067 | Inverter 067 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV067_DeviceFault | INV067 | Inverter 067 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_ExternalFanAbnormal | INV067 | Inverter 067 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_FanFailure | INV067 | Inverter 067 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_Faulty | INV067 | Inverter 067 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_FaultyMonitoringUnit | INV067 | Inverter 067 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_FaultyPowerCollector | INV067 | Inverter 067 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_Frequency | INV067 | Inverter 067 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_GeneralFaultTrip | INV067 | Inverter 067 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_Grid | INV067 | Inverter 067 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GridConnectionDeratingInverterInternalCauses | INV067 | Inverter 067 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GridConnectionDeratingPowerRationing | INV067 | Inverter 067 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GridLoss | INV067 | Inverter 067 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GridOverfrequency | INV067 | Inverter 067 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GridOvervoltage | INV067 | Inverter 067 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GridTiedOffGridControllerAbnormal | INV067 | Inverter 067 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GridUnderfrequency | INV067 | Inverter 067 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GridUndervoltage | INV067 | Inverter 067 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GridVoltageImbalance | INV067 | Inverter 067 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_GroundFault | INV067 | Inverter 067 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_HighInputStringVoltageGround | INV067 | Inverter 067 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_HighStringInputVoltage | INV067 | Inverter 067 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_InverterEfficiency | INV067 | Inverter 067 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_InverterGridConnectionStatus | INV067 | Inverter 067 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_InverterOverTemperature | INV067 | Inverter 067 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_InverterRunningStopped | INV067 | Inverter 067 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_InverterStartupShutdownStatus | INV067 | Inverter 067 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_InverterTripHistoryAvailable | INV067 | Inverter 067 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_IslandingDetectionStatus | INV067 | Inverter 067 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_LicenseExpired | INV067 | Inverter 067 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_LockingStatus | INV067 | Inverter 067 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_LowInsulationResistance | INV067 | Inverter 067 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_NormalGridConnection | INV067 | Inverter 067 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_NormalShutdown | INV067 | Inverter 067 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_OffGridOutputOverload | INV067 | Inverter 067 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_OptimizerFault | INV067 | Inverter 067 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_OutputDCComponentOverhigh | INV067 | Inverter 067 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_OutputOvercurrent | INV067 | Inverter 067 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_PVStringLoss | INV067 | Inverter 067 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_PassiveIslanding | INV067 | Inverter 067 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_PeripheralPortShortCircuit | INV067 | Inverter 067 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_PhaseWireShortCircuitedPE | INV067 | Inverter 067 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_PowerCurtailmentStatus | INV067 | Inverter 067 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_PowerFactor | INV067 | Inverter 067 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_PowerLimitationActiveGridCommand | INV067 | Inverter 067 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_ReactivePower | INV067 | Inverter 067 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV067_RemoteOFFStatus | INV067 | Inverter 067 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_Shutdown | INV067 | Inverter 067 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_ShutdownPowerRationing | INV067 | Inverter 067 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_SpotCheck | INV067 | Inverter 067 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_Standby | INV067 | Inverter 067 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_StringCurrentBackfeed | INV067 | Inverter 067 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_StringReverseConnection | INV067 | Inverter 067 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_StringReversePolarity | INV067 | Inverter 067 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_TotalEnergyYield | INV067 | Inverter 067 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV067_TransientACOvervoltage | INV067 | Inverter 067 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_UnstableGridFrequency | INV067 | Inverter 067 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_UpgradeFailed | INV067 | Inverter 067 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV067_WarningActive | INV067 | Inverter 067 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_ACCurrent | INV068 | Inverter 068 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_ACOvervoltage | INV068 | Inverter 068 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_ACUndervoltage | INV068 | Inverter 068 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_ACVoltage | INV068 | Inverter 068 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_AFCISelfCheckFailure | INV068 | Inverter 068 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_AbnormalGrounding | INV068 | Inverter 068 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_AbnormalPVModuleConfiguration | INV068 | Inverter 068 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_AbnormalResidualCurrent | INV068 | Inverter 068 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_AbnormalStringPower | INV068 | Inverter 068 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_ActiveIslanding | INV068 | Inverter 068 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_ActivePower | INV068 | Inverter 068 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_ApparentPower | INV068 | Inverter 068 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV068_BuiltPIDOperationAbnormal | INV068 | Inverter 068 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_CabinetOvertemperature | INV068 | Inverter 068 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_CommunicationFailure | INV068 | Inverter 068 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_CommunicationStatus | INV068 | Inverter 068 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_DCArcFault | INV068 | Inverter 068 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_DCCurrent | INV068 | Inverter 068 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_DCInsulationFault | INV068 | Inverter 068 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_DCOvervoltage | INV068 | Inverter 068 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_DCPower | INV068 | Inverter 068 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV068_DCVoltage | INV068 | Inverter 068 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_DailyEnergyYield | INV068 | Inverter 068 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV068_DeviceFault | INV068 | Inverter 068 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_ExternalFanAbnormal | INV068 | Inverter 068 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_FanFailure | INV068 | Inverter 068 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_Faulty | INV068 | Inverter 068 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_FaultyMonitoringUnit | INV068 | Inverter 068 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_FaultyPowerCollector | INV068 | Inverter 068 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_Frequency | INV068 | Inverter 068 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_GeneralFaultTrip | INV068 | Inverter 068 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_Grid | INV068 | Inverter 068 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GridConnectionDeratingInverterInternalCauses | INV068 | Inverter 068 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GridConnectionDeratingPowerRationing | INV068 | Inverter 068 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GridLoss | INV068 | Inverter 068 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GridOverfrequency | INV068 | Inverter 068 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GridOvervoltage | INV068 | Inverter 068 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GridTiedOffGridControllerAbnormal | INV068 | Inverter 068 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GridUnderfrequency | INV068 | Inverter 068 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GridUndervoltage | INV068 | Inverter 068 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GridVoltageImbalance | INV068 | Inverter 068 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_GroundFault | INV068 | Inverter 068 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_HighInputStringVoltageGround | INV068 | Inverter 068 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_HighStringInputVoltage | INV068 | Inverter 068 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_InverterEfficiency | INV068 | Inverter 068 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_InverterGridConnectionStatus | INV068 | Inverter 068 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_InverterOverTemperature | INV068 | Inverter 068 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_InverterRunningStopped | INV068 | Inverter 068 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_InverterStartupShutdownStatus | INV068 | Inverter 068 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_InverterTripHistoryAvailable | INV068 | Inverter 068 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_IslandingDetectionStatus | INV068 | Inverter 068 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_LicenseExpired | INV068 | Inverter 068 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_LockingStatus | INV068 | Inverter 068 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_LowInsulationResistance | INV068 | Inverter 068 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_NormalGridConnection | INV068 | Inverter 068 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_NormalShutdown | INV068 | Inverter 068 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_OffGridOutputOverload | INV068 | Inverter 068 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_OptimizerFault | INV068 | Inverter 068 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_OutputDCComponentOverhigh | INV068 | Inverter 068 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_OutputOvercurrent | INV068 | Inverter 068 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_PVStringLoss | INV068 | Inverter 068 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_PassiveIslanding | INV068 | Inverter 068 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_PeripheralPortShortCircuit | INV068 | Inverter 068 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_PhaseWireShortCircuitedPE | INV068 | Inverter 068 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_PowerCurtailmentStatus | INV068 | Inverter 068 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_PowerFactor | INV068 | Inverter 068 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_PowerLimitationActiveGridCommand | INV068 | Inverter 068 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_ReactivePower | INV068 | Inverter 068 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV068_RemoteOFFStatus | INV068 | Inverter 068 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_Shutdown | INV068 | Inverter 068 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_ShutdownPowerRationing | INV068 | Inverter 068 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_SpotCheck | INV068 | Inverter 068 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_Standby | INV068 | Inverter 068 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_StringCurrentBackfeed | INV068 | Inverter 068 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_StringReverseConnection | INV068 | Inverter 068 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_StringReversePolarity | INV068 | Inverter 068 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_TotalEnergyYield | INV068 | Inverter 068 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV068_TransientACOvervoltage | INV068 | Inverter 068 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_UnstableGridFrequency | INV068 | Inverter 068 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_UpgradeFailed | INV068 | Inverter 068 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV068_WarningActive | INV068 | Inverter 068 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_ACCurrent | INV069 | Inverter 069 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_ACOvervoltage | INV069 | Inverter 069 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_ACUndervoltage | INV069 | Inverter 069 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_ACVoltage | INV069 | Inverter 069 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_AFCISelfCheckFailure | INV069 | Inverter 069 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_AbnormalGrounding | INV069 | Inverter 069 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_AbnormalPVModuleConfiguration | INV069 | Inverter 069 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_AbnormalResidualCurrent | INV069 | Inverter 069 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_AbnormalStringPower | INV069 | Inverter 069 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_ActiveIslanding | INV069 | Inverter 069 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_ActivePower | INV069 | Inverter 069 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_ApparentPower | INV069 | Inverter 069 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV069_BuiltPIDOperationAbnormal | INV069 | Inverter 069 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_CabinetOvertemperature | INV069 | Inverter 069 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_CommunicationFailure | INV069 | Inverter 069 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_CommunicationStatus | INV069 | Inverter 069 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_DCArcFault | INV069 | Inverter 069 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_DCCurrent | INV069 | Inverter 069 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_DCInsulationFault | INV069 | Inverter 069 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_DCOvervoltage | INV069 | Inverter 069 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_DCPower | INV069 | Inverter 069 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV069_DCVoltage | INV069 | Inverter 069 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_DailyEnergyYield | INV069 | Inverter 069 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV069_DeviceFault | INV069 | Inverter 069 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_ExternalFanAbnormal | INV069 | Inverter 069 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_FanFailure | INV069 | Inverter 069 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_Faulty | INV069 | Inverter 069 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_FaultyMonitoringUnit | INV069 | Inverter 069 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_FaultyPowerCollector | INV069 | Inverter 069 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_Frequency | INV069 | Inverter 069 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_GeneralFaultTrip | INV069 | Inverter 069 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_Grid | INV069 | Inverter 069 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GridConnectionDeratingInverterInternalCauses | INV069 | Inverter 069 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GridConnectionDeratingPowerRationing | INV069 | Inverter 069 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GridLoss | INV069 | Inverter 069 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GridOverfrequency | INV069 | Inverter 069 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GridOvervoltage | INV069 | Inverter 069 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GridTiedOffGridControllerAbnormal | INV069 | Inverter 069 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GridUnderfrequency | INV069 | Inverter 069 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GridUndervoltage | INV069 | Inverter 069 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GridVoltageImbalance | INV069 | Inverter 069 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_GroundFault | INV069 | Inverter 069 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_HighInputStringVoltageGround | INV069 | Inverter 069 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_HighStringInputVoltage | INV069 | Inverter 069 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_InverterEfficiency | INV069 | Inverter 069 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_InverterGridConnectionStatus | INV069 | Inverter 069 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_InverterOverTemperature | INV069 | Inverter 069 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_InverterRunningStopped | INV069 | Inverter 069 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_InverterStartupShutdownStatus | INV069 | Inverter 069 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_InverterTripHistoryAvailable | INV069 | Inverter 069 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_IslandingDetectionStatus | INV069 | Inverter 069 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_LicenseExpired | INV069 | Inverter 069 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_LockingStatus | INV069 | Inverter 069 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_LowInsulationResistance | INV069 | Inverter 069 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_NormalGridConnection | INV069 | Inverter 069 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_NormalShutdown | INV069 | Inverter 069 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_OffGridOutputOverload | INV069 | Inverter 069 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_OptimizerFault | INV069 | Inverter 069 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_OutputDCComponentOverhigh | INV069 | Inverter 069 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_OutputOvercurrent | INV069 | Inverter 069 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_PVStringLoss | INV069 | Inverter 069 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_PassiveIslanding | INV069 | Inverter 069 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_PeripheralPortShortCircuit | INV069 | Inverter 069 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_PhaseWireShortCircuitedPE | INV069 | Inverter 069 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_PowerCurtailmentStatus | INV069 | Inverter 069 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_PowerFactor | INV069 | Inverter 069 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_PowerLimitationActiveGridCommand | INV069 | Inverter 069 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_ReactivePower | INV069 | Inverter 069 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV069_RemoteOFFStatus | INV069 | Inverter 069 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_Shutdown | INV069 | Inverter 069 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_ShutdownPowerRationing | INV069 | Inverter 069 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_SpotCheck | INV069 | Inverter 069 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_Standby | INV069 | Inverter 069 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_StringCurrentBackfeed | INV069 | Inverter 069 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_StringReverseConnection | INV069 | Inverter 069 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_StringReversePolarity | INV069 | Inverter 069 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_TotalEnergyYield | INV069 | Inverter 069 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV069_TransientACOvervoltage | INV069 | Inverter 069 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_UnstableGridFrequency | INV069 | Inverter 069 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_UpgradeFailed | INV069 | Inverter 069 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV069_WarningActive | INV069 | Inverter 069 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_ACCurrent | INV070 | Inverter 070 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_ACOvervoltage | INV070 | Inverter 070 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_ACUndervoltage | INV070 | Inverter 070 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_ACVoltage | INV070 | Inverter 070 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_AFCISelfCheckFailure | INV070 | Inverter 070 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_AbnormalGrounding | INV070 | Inverter 070 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_AbnormalPVModuleConfiguration | INV070 | Inverter 070 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_AbnormalResidualCurrent | INV070 | Inverter 070 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_AbnormalStringPower | INV070 | Inverter 070 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_ActiveIslanding | INV070 | Inverter 070 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_ActivePower | INV070 | Inverter 070 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_ApparentPower | INV070 | Inverter 070 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV070_BuiltPIDOperationAbnormal | INV070 | Inverter 070 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_CabinetOvertemperature | INV070 | Inverter 070 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_CommunicationFailure | INV070 | Inverter 070 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_CommunicationStatus | INV070 | Inverter 070 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_DCArcFault | INV070 | Inverter 070 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_DCCurrent | INV070 | Inverter 070 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_DCInsulationFault | INV070 | Inverter 070 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_DCOvervoltage | INV070 | Inverter 070 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_DCPower | INV070 | Inverter 070 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV070_DCVoltage | INV070 | Inverter 070 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_DailyEnergyYield | INV070 | Inverter 070 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV070_DeviceFault | INV070 | Inverter 070 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_ExternalFanAbnormal | INV070 | Inverter 070 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_FanFailure | INV070 | Inverter 070 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_Faulty | INV070 | Inverter 070 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_FaultyMonitoringUnit | INV070 | Inverter 070 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_FaultyPowerCollector | INV070 | Inverter 070 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_Frequency | INV070 | Inverter 070 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_GeneralFaultTrip | INV070 | Inverter 070 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_Grid | INV070 | Inverter 070 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GridConnectionDeratingInverterInternalCauses | INV070 | Inverter 070 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GridConnectionDeratingPowerRationing | INV070 | Inverter 070 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GridLoss | INV070 | Inverter 070 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GridOverfrequency | INV070 | Inverter 070 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GridOvervoltage | INV070 | Inverter 070 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GridTiedOffGridControllerAbnormal | INV070 | Inverter 070 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GridUnderfrequency | INV070 | Inverter 070 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GridUndervoltage | INV070 | Inverter 070 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GridVoltageImbalance | INV070 | Inverter 070 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_GroundFault | INV070 | Inverter 070 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_HighInputStringVoltageGround | INV070 | Inverter 070 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_HighStringInputVoltage | INV070 | Inverter 070 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_InverterEfficiency | INV070 | Inverter 070 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_InverterGridConnectionStatus | INV070 | Inverter 070 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_InverterOverTemperature | INV070 | Inverter 070 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_InverterRunningStopped | INV070 | Inverter 070 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_InverterStartupShutdownStatus | INV070 | Inverter 070 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_InverterTripHistoryAvailable | INV070 | Inverter 070 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_IslandingDetectionStatus | INV070 | Inverter 070 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_LicenseExpired | INV070 | Inverter 070 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_LockingStatus | INV070 | Inverter 070 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_LowInsulationResistance | INV070 | Inverter 070 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_NormalGridConnection | INV070 | Inverter 070 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_NormalShutdown | INV070 | Inverter 070 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_OffGridOutputOverload | INV070 | Inverter 070 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_OptimizerFault | INV070 | Inverter 070 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_OutputDCComponentOverhigh | INV070 | Inverter 070 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_OutputOvercurrent | INV070 | Inverter 070 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_PVStringLoss | INV070 | Inverter 070 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_PassiveIslanding | INV070 | Inverter 070 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_PeripheralPortShortCircuit | INV070 | Inverter 070 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_PhaseWireShortCircuitedPE | INV070 | Inverter 070 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_PowerCurtailmentStatus | INV070 | Inverter 070 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_PowerFactor | INV070 | Inverter 070 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_PowerLimitationActiveGridCommand | INV070 | Inverter 070 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_ReactivePower | INV070 | Inverter 070 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV070_RemoteOFFStatus | INV070 | Inverter 070 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_Shutdown | INV070 | Inverter 070 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_ShutdownPowerRationing | INV070 | Inverter 070 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_SpotCheck | INV070 | Inverter 070 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_Standby | INV070 | Inverter 070 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_StringCurrentBackfeed | INV070 | Inverter 070 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_StringReverseConnection | INV070 | Inverter 070 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_StringReversePolarity | INV070 | Inverter 070 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_TotalEnergyYield | INV070 | Inverter 070 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV070_TransientACOvervoltage | INV070 | Inverter 070 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_UnstableGridFrequency | INV070 | Inverter 070 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_UpgradeFailed | INV070 | Inverter 070 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV070_WarningActive | INV070 | Inverter 070 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_ACCurrent | INV071 | Inverter 071 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_ACOvervoltage | INV071 | Inverter 071 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_ACUndervoltage | INV071 | Inverter 071 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_ACVoltage | INV071 | Inverter 071 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_AFCISelfCheckFailure | INV071 | Inverter 071 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_AbnormalGrounding | INV071 | Inverter 071 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_AbnormalPVModuleConfiguration | INV071 | Inverter 071 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_AbnormalResidualCurrent | INV071 | Inverter 071 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_AbnormalStringPower | INV071 | Inverter 071 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_ActiveIslanding | INV071 | Inverter 071 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_ActivePower | INV071 | Inverter 071 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_ApparentPower | INV071 | Inverter 071 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV071_BuiltPIDOperationAbnormal | INV071 | Inverter 071 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_CabinetOvertemperature | INV071 | Inverter 071 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_CommunicationFailure | INV071 | Inverter 071 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_CommunicationStatus | INV071 | Inverter 071 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_DCArcFault | INV071 | Inverter 071 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_DCCurrent | INV071 | Inverter 071 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_DCInsulationFault | INV071 | Inverter 071 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_DCOvervoltage | INV071 | Inverter 071 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_DCPower | INV071 | Inverter 071 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV071_DCVoltage | INV071 | Inverter 071 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_DailyEnergyYield | INV071 | Inverter 071 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV071_DeviceFault | INV071 | Inverter 071 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_ExternalFanAbnormal | INV071 | Inverter 071 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_FanFailure | INV071 | Inverter 071 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_Faulty | INV071 | Inverter 071 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_FaultyMonitoringUnit | INV071 | Inverter 071 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_FaultyPowerCollector | INV071 | Inverter 071 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_Frequency | INV071 | Inverter 071 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_GeneralFaultTrip | INV071 | Inverter 071 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_Grid | INV071 | Inverter 071 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GridConnectionDeratingInverterInternalCauses | INV071 | Inverter 071 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GridConnectionDeratingPowerRationing | INV071 | Inverter 071 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GridLoss | INV071 | Inverter 071 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GridOverfrequency | INV071 | Inverter 071 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GridOvervoltage | INV071 | Inverter 071 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GridTiedOffGridControllerAbnormal | INV071 | Inverter 071 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GridUnderfrequency | INV071 | Inverter 071 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GridUndervoltage | INV071 | Inverter 071 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GridVoltageImbalance | INV071 | Inverter 071 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_GroundFault | INV071 | Inverter 071 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_HighInputStringVoltageGround | INV071 | Inverter 071 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_HighStringInputVoltage | INV071 | Inverter 071 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_InverterEfficiency | INV071 | Inverter 071 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_InverterGridConnectionStatus | INV071 | Inverter 071 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_InverterOverTemperature | INV071 | Inverter 071 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_InverterRunningStopped | INV071 | Inverter 071 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_InverterStartupShutdownStatus | INV071 | Inverter 071 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_InverterTripHistoryAvailable | INV071 | Inverter 071 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_IslandingDetectionStatus | INV071 | Inverter 071 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_LicenseExpired | INV071 | Inverter 071 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_LockingStatus | INV071 | Inverter 071 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_LowInsulationResistance | INV071 | Inverter 071 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_NormalGridConnection | INV071 | Inverter 071 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_NormalShutdown | INV071 | Inverter 071 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_OffGridOutputOverload | INV071 | Inverter 071 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_OptimizerFault | INV071 | Inverter 071 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_OutputDCComponentOverhigh | INV071 | Inverter 071 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_OutputOvercurrent | INV071 | Inverter 071 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_PVStringLoss | INV071 | Inverter 071 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_PassiveIslanding | INV071 | Inverter 071 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_PeripheralPortShortCircuit | INV071 | Inverter 071 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_PhaseWireShortCircuitedPE | INV071 | Inverter 071 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_PowerCurtailmentStatus | INV071 | Inverter 071 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_PowerFactor | INV071 | Inverter 071 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_PowerLimitationActiveGridCommand | INV071 | Inverter 071 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_ReactivePower | INV071 | Inverter 071 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV071_RemoteOFFStatus | INV071 | Inverter 071 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_Shutdown | INV071 | Inverter 071 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_ShutdownPowerRationing | INV071 | Inverter 071 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_SpotCheck | INV071 | Inverter 071 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_Standby | INV071 | Inverter 071 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_StringCurrentBackfeed | INV071 | Inverter 071 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_StringReverseConnection | INV071 | Inverter 071 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_StringReversePolarity | INV071 | Inverter 071 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_TotalEnergyYield | INV071 | Inverter 071 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV071_TransientACOvervoltage | INV071 | Inverter 071 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_UnstableGridFrequency | INV071 | Inverter 071 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_UpgradeFailed | INV071 | Inverter 071 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV071_WarningActive | INV071 | Inverter 071 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_ACCurrent | INV072 | Inverter 072 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_ACOvervoltage | INV072 | Inverter 072 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_ACUndervoltage | INV072 | Inverter 072 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_ACVoltage | INV072 | Inverter 072 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_AFCISelfCheckFailure | INV072 | Inverter 072 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_AbnormalGrounding | INV072 | Inverter 072 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_AbnormalPVModuleConfiguration | INV072 | Inverter 072 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_AbnormalResidualCurrent | INV072 | Inverter 072 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_AbnormalStringPower | INV072 | Inverter 072 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_ActiveIslanding | INV072 | Inverter 072 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_ActivePower | INV072 | Inverter 072 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_ApparentPower | INV072 | Inverter 072 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV072_BuiltPIDOperationAbnormal | INV072 | Inverter 072 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_CabinetOvertemperature | INV072 | Inverter 072 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_CommunicationFailure | INV072 | Inverter 072 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_CommunicationStatus | INV072 | Inverter 072 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_DCArcFault | INV072 | Inverter 072 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_DCCurrent | INV072 | Inverter 072 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_DCInsulationFault | INV072 | Inverter 072 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_DCOvervoltage | INV072 | Inverter 072 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_DCPower | INV072 | Inverter 072 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV072_DCVoltage | INV072 | Inverter 072 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_DailyEnergyYield | INV072 | Inverter 072 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV072_DeviceFault | INV072 | Inverter 072 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_ExternalFanAbnormal | INV072 | Inverter 072 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_FanFailure | INV072 | Inverter 072 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_Faulty | INV072 | Inverter 072 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_FaultyMonitoringUnit | INV072 | Inverter 072 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_FaultyPowerCollector | INV072 | Inverter 072 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_Frequency | INV072 | Inverter 072 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_GeneralFaultTrip | INV072 | Inverter 072 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_Grid | INV072 | Inverter 072 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GridConnectionDeratingInverterInternalCauses | INV072 | Inverter 072 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GridConnectionDeratingPowerRationing | INV072 | Inverter 072 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GridLoss | INV072 | Inverter 072 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GridOverfrequency | INV072 | Inverter 072 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GridOvervoltage | INV072 | Inverter 072 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GridTiedOffGridControllerAbnormal | INV072 | Inverter 072 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GridUnderfrequency | INV072 | Inverter 072 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GridUndervoltage | INV072 | Inverter 072 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GridVoltageImbalance | INV072 | Inverter 072 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_GroundFault | INV072 | Inverter 072 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_HighInputStringVoltageGround | INV072 | Inverter 072 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_HighStringInputVoltage | INV072 | Inverter 072 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_InverterEfficiency | INV072 | Inverter 072 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_InverterGridConnectionStatus | INV072 | Inverter 072 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_InverterOverTemperature | INV072 | Inverter 072 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_InverterRunningStopped | INV072 | Inverter 072 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_InverterStartupShutdownStatus | INV072 | Inverter 072 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_InverterTripHistoryAvailable | INV072 | Inverter 072 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_IslandingDetectionStatus | INV072 | Inverter 072 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_LicenseExpired | INV072 | Inverter 072 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_LockingStatus | INV072 | Inverter 072 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_LowInsulationResistance | INV072 | Inverter 072 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_NormalGridConnection | INV072 | Inverter 072 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_NormalShutdown | INV072 | Inverter 072 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_OffGridOutputOverload | INV072 | Inverter 072 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_OptimizerFault | INV072 | Inverter 072 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_OutputDCComponentOverhigh | INV072 | Inverter 072 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_OutputOvercurrent | INV072 | Inverter 072 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_PVStringLoss | INV072 | Inverter 072 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_PassiveIslanding | INV072 | Inverter 072 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_PeripheralPortShortCircuit | INV072 | Inverter 072 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_PhaseWireShortCircuitedPE | INV072 | Inverter 072 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_PowerCurtailmentStatus | INV072 | Inverter 072 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_PowerFactor | INV072 | Inverter 072 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_PowerLimitationActiveGridCommand | INV072 | Inverter 072 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_ReactivePower | INV072 | Inverter 072 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV072_RemoteOFFStatus | INV072 | Inverter 072 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_Shutdown | INV072 | Inverter 072 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_ShutdownPowerRationing | INV072 | Inverter 072 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_SpotCheck | INV072 | Inverter 072 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_Standby | INV072 | Inverter 072 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_StringCurrentBackfeed | INV072 | Inverter 072 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_StringReverseConnection | INV072 | Inverter 072 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_StringReversePolarity | INV072 | Inverter 072 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_TotalEnergyYield | INV072 | Inverter 072 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV072_TransientACOvervoltage | INV072 | Inverter 072 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_UnstableGridFrequency | INV072 | Inverter 072 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_UpgradeFailed | INV072 | Inverter 072 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV072_WarningActive | INV072 | Inverter 072 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_ACCurrent | INV073 | Inverter 073 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_ACOvervoltage | INV073 | Inverter 073 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_ACUndervoltage | INV073 | Inverter 073 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_ACVoltage | INV073 | Inverter 073 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_AFCISelfCheckFailure | INV073 | Inverter 073 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_AbnormalGrounding | INV073 | Inverter 073 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_AbnormalPVModuleConfiguration | INV073 | Inverter 073 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_AbnormalResidualCurrent | INV073 | Inverter 073 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_AbnormalStringPower | INV073 | Inverter 073 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_ActiveIslanding | INV073 | Inverter 073 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_ActivePower | INV073 | Inverter 073 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_ApparentPower | INV073 | Inverter 073 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV073_BuiltPIDOperationAbnormal | INV073 | Inverter 073 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_CabinetOvertemperature | INV073 | Inverter 073 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_CommunicationFailure | INV073 | Inverter 073 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_CommunicationStatus | INV073 | Inverter 073 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_DCArcFault | INV073 | Inverter 073 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_DCCurrent | INV073 | Inverter 073 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_DCInsulationFault | INV073 | Inverter 073 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_DCOvervoltage | INV073 | Inverter 073 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_DCPower | INV073 | Inverter 073 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV073_DCVoltage | INV073 | Inverter 073 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_DailyEnergyYield | INV073 | Inverter 073 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV073_DeviceFault | INV073 | Inverter 073 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_ExternalFanAbnormal | INV073 | Inverter 073 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_FanFailure | INV073 | Inverter 073 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_Faulty | INV073 | Inverter 073 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_FaultyMonitoringUnit | INV073 | Inverter 073 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_FaultyPowerCollector | INV073 | Inverter 073 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_Frequency | INV073 | Inverter 073 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_GeneralFaultTrip | INV073 | Inverter 073 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_Grid | INV073 | Inverter 073 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GridConnectionDeratingInverterInternalCauses | INV073 | Inverter 073 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GridConnectionDeratingPowerRationing | INV073 | Inverter 073 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GridLoss | INV073 | Inverter 073 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GridOverfrequency | INV073 | Inverter 073 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GridOvervoltage | INV073 | Inverter 073 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GridTiedOffGridControllerAbnormal | INV073 | Inverter 073 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GridUnderfrequency | INV073 | Inverter 073 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GridUndervoltage | INV073 | Inverter 073 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GridVoltageImbalance | INV073 | Inverter 073 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_GroundFault | INV073 | Inverter 073 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_HighInputStringVoltageGround | INV073 | Inverter 073 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_HighStringInputVoltage | INV073 | Inverter 073 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_InverterEfficiency | INV073 | Inverter 073 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_InverterGridConnectionStatus | INV073 | Inverter 073 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_InverterOverTemperature | INV073 | Inverter 073 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_InverterRunningStopped | INV073 | Inverter 073 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_InverterStartupShutdownStatus | INV073 | Inverter 073 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_InverterTripHistoryAvailable | INV073 | Inverter 073 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_IslandingDetectionStatus | INV073 | Inverter 073 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_LicenseExpired | INV073 | Inverter 073 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_LockingStatus | INV073 | Inverter 073 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_LowInsulationResistance | INV073 | Inverter 073 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_NormalGridConnection | INV073 | Inverter 073 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_NormalShutdown | INV073 | Inverter 073 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_OffGridOutputOverload | INV073 | Inverter 073 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_OptimizerFault | INV073 | Inverter 073 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_OutputDCComponentOverhigh | INV073 | Inverter 073 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_OutputOvercurrent | INV073 | Inverter 073 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_PVStringLoss | INV073 | Inverter 073 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_PassiveIslanding | INV073 | Inverter 073 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_PeripheralPortShortCircuit | INV073 | Inverter 073 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_PhaseWireShortCircuitedPE | INV073 | Inverter 073 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_PowerCurtailmentStatus | INV073 | Inverter 073 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_PowerFactor | INV073 | Inverter 073 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_PowerLimitationActiveGridCommand | INV073 | Inverter 073 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_ReactivePower | INV073 | Inverter 073 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV073_RemoteOFFStatus | INV073 | Inverter 073 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_Shutdown | INV073 | Inverter 073 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_ShutdownPowerRationing | INV073 | Inverter 073 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_SpotCheck | INV073 | Inverter 073 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_Standby | INV073 | Inverter 073 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_StringCurrentBackfeed | INV073 | Inverter 073 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_StringReverseConnection | INV073 | Inverter 073 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_StringReversePolarity | INV073 | Inverter 073 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_TotalEnergyYield | INV073 | Inverter 073 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV073_TransientACOvervoltage | INV073 | Inverter 073 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_UnstableGridFrequency | INV073 | Inverter 073 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_UpgradeFailed | INV073 | Inverter 073 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV073_WarningActive | INV073 | Inverter 073 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_ACCurrent | INV074 | Inverter 074 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_ACOvervoltage | INV074 | Inverter 074 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_ACUndervoltage | INV074 | Inverter 074 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_ACVoltage | INV074 | Inverter 074 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_AFCISelfCheckFailure | INV074 | Inverter 074 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_AbnormalGrounding | INV074 | Inverter 074 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_AbnormalPVModuleConfiguration | INV074 | Inverter 074 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_AbnormalResidualCurrent | INV074 | Inverter 074 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_AbnormalStringPower | INV074 | Inverter 074 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_ActiveIslanding | INV074 | Inverter 074 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_ActivePower | INV074 | Inverter 074 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_ApparentPower | INV074 | Inverter 074 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV074_BuiltPIDOperationAbnormal | INV074 | Inverter 074 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_CabinetOvertemperature | INV074 | Inverter 074 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_CommunicationFailure | INV074 | Inverter 074 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_CommunicationStatus | INV074 | Inverter 074 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_DCArcFault | INV074 | Inverter 074 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_DCCurrent | INV074 | Inverter 074 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_DCInsulationFault | INV074 | Inverter 074 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_DCOvervoltage | INV074 | Inverter 074 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_DCPower | INV074 | Inverter 074 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV074_DCVoltage | INV074 | Inverter 074 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_DailyEnergyYield | INV074 | Inverter 074 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV074_DeviceFault | INV074 | Inverter 074 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_ExternalFanAbnormal | INV074 | Inverter 074 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_FanFailure | INV074 | Inverter 074 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_Faulty | INV074 | Inverter 074 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_FaultyMonitoringUnit | INV074 | Inverter 074 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_FaultyPowerCollector | INV074 | Inverter 074 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_Frequency | INV074 | Inverter 074 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_GeneralFaultTrip | INV074 | Inverter 074 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_Grid | INV074 | Inverter 074 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GridConnectionDeratingInverterInternalCauses | INV074 | Inverter 074 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GridConnectionDeratingPowerRationing | INV074 | Inverter 074 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GridLoss | INV074 | Inverter 074 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GridOverfrequency | INV074 | Inverter 074 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GridOvervoltage | INV074 | Inverter 074 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GridTiedOffGridControllerAbnormal | INV074 | Inverter 074 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GridUnderfrequency | INV074 | Inverter 074 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GridUndervoltage | INV074 | Inverter 074 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GridVoltageImbalance | INV074 | Inverter 074 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_GroundFault | INV074 | Inverter 074 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_HighInputStringVoltageGround | INV074 | Inverter 074 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_HighStringInputVoltage | INV074 | Inverter 074 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_InverterEfficiency | INV074 | Inverter 074 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_InverterGridConnectionStatus | INV074 | Inverter 074 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_InverterOverTemperature | INV074 | Inverter 074 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_InverterRunningStopped | INV074 | Inverter 074 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_InverterStartupShutdownStatus | INV074 | Inverter 074 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_InverterTripHistoryAvailable | INV074 | Inverter 074 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_IslandingDetectionStatus | INV074 | Inverter 074 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_LicenseExpired | INV074 | Inverter 074 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_LockingStatus | INV074 | Inverter 074 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_LowInsulationResistance | INV074 | Inverter 074 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_NormalGridConnection | INV074 | Inverter 074 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_NormalShutdown | INV074 | Inverter 074 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_OffGridOutputOverload | INV074 | Inverter 074 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_OptimizerFault | INV074 | Inverter 074 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_OutputDCComponentOverhigh | INV074 | Inverter 074 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_OutputOvercurrent | INV074 | Inverter 074 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_PVStringLoss | INV074 | Inverter 074 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_PassiveIslanding | INV074 | Inverter 074 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_PeripheralPortShortCircuit | INV074 | Inverter 074 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_PhaseWireShortCircuitedPE | INV074 | Inverter 074 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_PowerCurtailmentStatus | INV074 | Inverter 074 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_PowerFactor | INV074 | Inverter 074 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_PowerLimitationActiveGridCommand | INV074 | Inverter 074 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_ReactivePower | INV074 | Inverter 074 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV074_RemoteOFFStatus | INV074 | Inverter 074 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_Shutdown | INV074 | Inverter 074 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_ShutdownPowerRationing | INV074 | Inverter 074 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_SpotCheck | INV074 | Inverter 074 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_Standby | INV074 | Inverter 074 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_StringCurrentBackfeed | INV074 | Inverter 074 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_StringReverseConnection | INV074 | Inverter 074 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_StringReversePolarity | INV074 | Inverter 074 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_TotalEnergyYield | INV074 | Inverter 074 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV074_TransientACOvervoltage | INV074 | Inverter 074 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_UnstableGridFrequency | INV074 | Inverter 074 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_UpgradeFailed | INV074 | Inverter 074 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV074_WarningActive | INV074 | Inverter 074 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_ACCurrent | INV075 | Inverter 075 | Inverter | AC Current (per phase) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_ACOvervoltage | INV075 | Inverter 075 | Inverter | AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_ACUndervoltage | INV075 | Inverter 075 | Inverter | AC Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_ACVoltage | INV075 | Inverter 075 | Inverter | AC Voltage (L-L or L-N) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_AFCISelfCheckFailure | INV075 | Inverter 075 | Inverter | AFCI Self-Check Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_AbnormalGrounding | INV075 | Inverter 075 | Inverter | Abnormal Grounding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_AbnormalPVModuleConfiguration | INV075 | Inverter 075 | Inverter | Abnormal PV module configuration | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_AbnormalResidualCurrent | INV075 | Inverter 075 | Inverter | Abnormal Residual Current | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_AbnormalStringPower | INV075 | Inverter 075 | Inverter | Abnormal String Power | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_ActiveIslanding | INV075 | Inverter 075 | Inverter | Active Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_ActivePower | INV075 | Inverter 075 | Inverter | Active Power (per inverter and total) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_ApparentPower | INV075 | Inverter 075 | Inverter | Apparent Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV075_BuiltPIDOperationAbnormal | INV075 | Inverter 075 | Inverter | Built-in PID operation abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_CabinetOvertemperature | INV075 | Inverter 075 | Inverter | Cabinet Overtemperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_CommunicationFailure | INV075 | Inverter 075 | Inverter | Communication Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_CommunicationStatus | INV075 | Inverter 075 | Inverter | Communication Status (Healthy / Lost) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_DCArcFault | INV075 | Inverter 075 | Inverter | DC Arc Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_DCCurrent | INV075 | Inverter 075 | Inverter | DC Current | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_DCInsulationFault | INV075 | Inverter 075 | Inverter | DC Insulation Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_DCOvervoltage | INV075 | Inverter 075 | Inverter | DC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_DCPower | INV075 | Inverter 075 | Inverter | DC Power | Calc | Analog | Derived | Calculated in SCADA | Calculated | Periodic | 60 s
INV075_DCVoltage | INV075 | Inverter 075 | Inverter | DC Voltage ( String Level) | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_DailyEnergyYield | INV075 | Inverter 075 | Inverter | Daily Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV075_DeviceFault | INV075 | Inverter 075 | Inverter | Device Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_ExternalFanAbnormal | INV075 | Inverter 075 | Inverter | External fan abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_FanFailure | INV075 | Inverter 075 | Inverter | Fan Failure | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_Faulty | INV075 | Inverter 075 | Inverter | Faulty | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_FaultyMonitoringUnit | INV075 | Inverter 075 | Inverter | Faulty Monitoring Unit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_FaultyPowerCollector | INV075 | Inverter 075 | Inverter | Faulty Power Collector | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_Frequency | INV075 | Inverter 075 | Inverter | Frequency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_GeneralFaultTrip | INV075 | Inverter 075 | Inverter | General Fault Trip | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_Grid | INV075 | Inverter 075 | Inverter | On-grid | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GridConnectionDeratingInverterInternalCauses | INV075 | Inverter 075 | Inverter | Grid connection with derating due to inverter internal causes | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GridConnectionDeratingPowerRationing | INV075 | Inverter 075 | Inverter | Grid connection with derating due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GridLoss | INV075 | Inverter 075 | Inverter | Grid Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GridOverfrequency | INV075 | Inverter 075 | Inverter | Grid Overfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GridOvervoltage | INV075 | Inverter 075 | Inverter | Grid Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GridTiedOffGridControllerAbnormal | INV075 | Inverter 075 | Inverter | Grid-tied/Off-grid controller abnormal | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GridUnderfrequency | INV075 | Inverter 075 | Inverter | Grid Underfrequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GridUndervoltage | INV075 | Inverter 075 | Inverter | Grid Undervoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GridVoltageImbalance | INV075 | Inverter 075 | Inverter | Grid Voltage Imbalance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_GroundFault | INV075 | Inverter 075 | Inverter | Ground Fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_HighInputStringVoltageGround | INV075 | Inverter 075 | Inverter | High input string voltage to ground | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_HighStringInputVoltage | INV075 | Inverter 075 | Inverter | High string input voltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_InverterEfficiency | INV075 | Inverter 075 | Inverter | Inverter Efficiency | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_InverterGridConnectionStatus | INV075 | Inverter 075 | Inverter | Inverter Grid Connection Status (Connected / Disconnected) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_InverterOverTemperature | INV075 | Inverter 075 | Inverter | Inverter Over temperature | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_InverterRunningStopped | INV075 | Inverter 075 | Inverter | Inverter Running / Stopped | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_InverterStartupShutdownStatus | INV075 | Inverter 075 | Inverter | Inverter startup/shutdown status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_InverterTripHistoryAvailable | INV075 | Inverter 075 | Inverter | Inverter Trip History Available | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_IslandingDetectionStatus | INV075 | Inverter 075 | Inverter | Islanding Detection Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_LicenseExpired | INV075 | Inverter 075 | Inverter | License Expired | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_LockingStatus | INV075 | Inverter 075 | Inverter | Locking status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_LowInsulationResistance | INV075 | Inverter 075 | Inverter | Low Insulation Resistance | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_NormalGridConnection | INV075 | Inverter 075 | Inverter | Normal grid connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_NormalShutdown | INV075 | Inverter 075 | Inverter | Normal shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_OffGridOutputOverload | INV075 | Inverter 075 | Inverter | Off-grid output overload | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_OptimizerFault | INV075 | Inverter 075 | Inverter | Optimizer fault | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_OutputDCComponentOverhigh | INV075 | Inverter 075 | Inverter | Output DC Component Overhigh | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_OutputOvercurrent | INV075 | Inverter 075 | Inverter | Output Overcurrent | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_PVStringLoss | INV075 | Inverter 075 | Inverter | PV String Loss | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_PassiveIslanding | INV075 | Inverter 075 | Inverter | Passive Islanding | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_PeripheralPortShortCircuit | INV075 | Inverter 075 | Inverter | Peripheral port short circuit | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_PhaseWireShortCircuitedPE | INV075 | Inverter 075 | Inverter | Phase Wire Short-Circuited to PE | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_PowerCurtailmentStatus | INV075 | Inverter 075 | Inverter | Power Curtailment Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_PowerFactor | INV075 | Inverter 075 | Inverter | Power Factor | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_PowerLimitationActiveGridCommand | INV075 | Inverter 075 | Inverter | Power Limitation Active due to Grid Command | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_ReactivePower | INV075 | Inverter 075 | Inverter | Reactive Power | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 60 s
INV075_RemoteOFFStatus | INV075 | Inverter 075 | Inverter | Remote ON/OFF Status | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_Shutdown | INV075 | Inverter 075 | Inverter | Shutdown | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_ShutdownPowerRationing | INV075 | Inverter 075 | Inverter | Shutdown due to power rationing | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_SpotCheck | INV075 | Inverter 075 | Inverter | Spot-check | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_Standby | INV075 | Inverter 075 | Inverter | Standby | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_StringCurrentBackfeed | INV075 | Inverter 075 | Inverter | String current backfeed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_StringReverseConnection | INV075 | Inverter 075 | Inverter | String Reverse Connection | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_StringReversePolarity | INV075 | Inverter 075 | Inverter | String Reverse Polarity | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_TotalEnergyYield | INV075 | Inverter 075 | Inverter | Total Energy Yield | AI | Analog | IEC 104 | Direct | TELEMERTY | Periodic | 300 s
INV075_TransientACOvervoltage | INV075 | Inverter 075 | Inverter | Transient AC Overvoltage | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_UnstableGridFrequency | INV075 | Inverter 075 | Inverter | Unstable Grid Frequency | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_UpgradeFailed | INV075 | Inverter 075 | Inverter | Upgrade Failed | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
INV075_WarningActive | INV075 | Inverter 075 | Inverter | Warning Active (Derating, Overtemperature) | DI | Digital | IEC 104 | Direct | Teleindication | On Change | On Change
PR001_CircuitBreakerClosePosition | PR001 | Protection Relay 001 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_CircuitBreakerFailureFailExternalTrip | PR001 | Protection Relay 001 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_CircuitBreakerFailureInternalReTrip | PR001 | Protection Relay 001 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_CircuitBreakerFailureTimerRunning | PR001 | Protection Relay 001 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_CircuitBreakerOpenPosition | PR001 | Protection Relay 001 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_ACTripFlag | PR001 | Protection Relay 001 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_DCTripFlag | PR001 | Protection Relay 001 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_MCBTripFlag | PR001 | Protection Relay 001 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_RelayTripFlag | PR001 | Protection Relay 001 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_CircuitBreakerTripMaster1 | PR001 | Protection Relay 001 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_DirectionalEarthFault | PR001 | Protection Relay 001 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_DirectionalOvercurrentHighStage | PR001 | Protection Relay 001 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_DirectionalOvercurrentLowStage | PR001 | Protection Relay 001 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_EarthSwitchClosePosition | PR001 | Protection Relay 001 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_EarthSwitchOpenPosition | PR001 | Protection Relay 001 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_InstantaneousOvercurrent | PR001 | Protection Relay 001 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_LockoutRelayStatus | PR001 | Protection Relay 001 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_NegativeSequenceOvercurrentProtection | PR001 | Protection Relay 001 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_ProtectionRelayStatus | PR001 | Protection Relay 001 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_RemoteLocalControlStatus | PR001 | Protection Relay 001 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_RemoteLocalControlStatusR129_02 | PR001 | Protection Relay 001 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_SpringChargedDischargedAlarm | PR001 | Protection Relay 001 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_TestServicePositionStatus | PR001 | Protection Relay 001 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR001_TimeOvercurrent | PR001 | Protection Relay 001 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_CircuitBreakerClosePosition | PR002 | Protection Relay 002 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_CircuitBreakerFailureFailExternalTrip | PR002 | Protection Relay 002 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_CircuitBreakerFailureInternalReTrip | PR002 | Protection Relay 002 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_CircuitBreakerFailureTimerRunning | PR002 | Protection Relay 002 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_CircuitBreakerOpenPosition | PR002 | Protection Relay 002 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_ACTripFlag | PR002 | Protection Relay 002 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_DCTripFlag | PR002 | Protection Relay 002 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_MCBTripFlag | PR002 | Protection Relay 002 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_RelayTripFlag | PR002 | Protection Relay 002 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_CircuitBreakerTripMaster1 | PR002 | Protection Relay 002 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_DirectionalEarthFault | PR002 | Protection Relay 002 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_DirectionalOvercurrentHighStage | PR002 | Protection Relay 002 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_DirectionalOvercurrentLowStage | PR002 | Protection Relay 002 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_EarthSwitchClosePosition | PR002 | Protection Relay 002 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_EarthSwitchOpenPosition | PR002 | Protection Relay 002 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_InstantaneousOvercurrent | PR002 | Protection Relay 002 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_LockoutRelayStatus | PR002 | Protection Relay 002 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_NegativeSequenceOvercurrentProtection | PR002 | Protection Relay 002 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_ProtectionRelayStatus | PR002 | Protection Relay 002 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_RemoteLocalControlStatus | PR002 | Protection Relay 002 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_RemoteLocalControlStatusR129_02 | PR002 | Protection Relay 002 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_SpringChargedDischargedAlarm | PR002 | Protection Relay 002 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_TestServicePositionStatus | PR002 | Protection Relay 002 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR002_TimeOvercurrent | PR002 | Protection Relay 002 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_CircuitBreakerClosePosition | PR003 | Protection Relay 003 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_CircuitBreakerFailureFailExternalTrip | PR003 | Protection Relay 003 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_CircuitBreakerFailureInternalReTrip | PR003 | Protection Relay 003 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_CircuitBreakerFailureTimerRunning | PR003 | Protection Relay 003 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_CircuitBreakerOpenPosition | PR003 | Protection Relay 003 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_ACTripFlag | PR003 | Protection Relay 003 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_DCTripFlag | PR003 | Protection Relay 003 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_MCBTripFlag | PR003 | Protection Relay 003 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_RelayTripFlag | PR003 | Protection Relay 003 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_CircuitBreakerTripMaster1 | PR003 | Protection Relay 003 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_DirectionalEarthFault | PR003 | Protection Relay 003 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_DirectionalOvercurrentHighStage | PR003 | Protection Relay 003 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_DirectionalOvercurrentLowStage | PR003 | Protection Relay 003 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_EarthSwitchClosePosition | PR003 | Protection Relay 003 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_EarthSwitchOpenPosition | PR003 | Protection Relay 003 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_InstantaneousOvercurrent | PR003 | Protection Relay 003 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_LockoutRelayStatus | PR003 | Protection Relay 003 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_NegativeSequenceOvercurrentProtection | PR003 | Protection Relay 003 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_ProtectionRelayStatus | PR003 | Protection Relay 003 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_RemoteLocalControlStatus | PR003 | Protection Relay 003 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_RemoteLocalControlStatusR129_02 | PR003 | Protection Relay 003 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_SpringChargedDischargedAlarm | PR003 | Protection Relay 003 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_TestServicePositionStatus | PR003 | Protection Relay 003 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR003_TimeOvercurrent | PR003 | Protection Relay 003 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_CircuitBreakerClosePosition | PR004 | Protection Relay 004 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_CircuitBreakerFailureFailExternalTrip | PR004 | Protection Relay 004 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_CircuitBreakerFailureInternalReTrip | PR004 | Protection Relay 004 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_CircuitBreakerFailureTimerRunning | PR004 | Protection Relay 004 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_CircuitBreakerOpenPosition | PR004 | Protection Relay 004 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_ACTripFlag | PR004 | Protection Relay 004 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_DCTripFlag | PR004 | Protection Relay 004 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_MCBTripFlag | PR004 | Protection Relay 004 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_RelayTripFlag | PR004 | Protection Relay 004 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_CircuitBreakerTripMaster1 | PR004 | Protection Relay 004 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_DirectionalEarthFault | PR004 | Protection Relay 004 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_DirectionalOvercurrentHighStage | PR004 | Protection Relay 004 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_DirectionalOvercurrentLowStage | PR004 | Protection Relay 004 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_EarthSwitchClosePosition | PR004 | Protection Relay 004 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_EarthSwitchOpenPosition | PR004 | Protection Relay 004 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_InstantaneousOvercurrent | PR004 | Protection Relay 004 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_LockoutRelayStatus | PR004 | Protection Relay 004 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_NegativeSequenceOvercurrentProtection | PR004 | Protection Relay 004 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_ProtectionRelayStatus | PR004 | Protection Relay 004 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_RemoteLocalControlStatus | PR004 | Protection Relay 004 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_RemoteLocalControlStatusR129_02 | PR004 | Protection Relay 004 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_SpringChargedDischargedAlarm | PR004 | Protection Relay 004 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_TestServicePositionStatus | PR004 | Protection Relay 004 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR004_TimeOvercurrent | PR004 | Protection Relay 004 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_CircuitBreakerClosePosition | PR005 | Protection Relay 005 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_CircuitBreakerFailureFailExternalTrip | PR005 | Protection Relay 005 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_CircuitBreakerFailureInternalReTrip | PR005 | Protection Relay 005 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_CircuitBreakerFailureTimerRunning | PR005 | Protection Relay 005 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_CircuitBreakerOpenPosition | PR005 | Protection Relay 005 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_ACTripFlag | PR005 | Protection Relay 005 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_DCTripFlag | PR005 | Protection Relay 005 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_MCBTripFlag | PR005 | Protection Relay 005 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_RelayTripFlag | PR005 | Protection Relay 005 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_CircuitBreakerTripMaster1 | PR005 | Protection Relay 005 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_DirectionalEarthFault | PR005 | Protection Relay 005 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_DirectionalOvercurrentHighStage | PR005 | Protection Relay 005 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_DirectionalOvercurrentLowStage | PR005 | Protection Relay 005 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_EarthSwitchClosePosition | PR005 | Protection Relay 005 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_EarthSwitchOpenPosition | PR005 | Protection Relay 005 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_InstantaneousOvercurrent | PR005 | Protection Relay 005 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_LockoutRelayStatus | PR005 | Protection Relay 005 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_NegativeSequenceOvercurrentProtection | PR005 | Protection Relay 005 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_ProtectionRelayStatus | PR005 | Protection Relay 005 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_RemoteLocalControlStatus | PR005 | Protection Relay 005 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_RemoteLocalControlStatusR129_02 | PR005 | Protection Relay 005 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_SpringChargedDischargedAlarm | PR005 | Protection Relay 005 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_TestServicePositionStatus | PR005 | Protection Relay 005 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR005_TimeOvercurrent | PR005 | Protection Relay 005 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_CircuitBreakerClosePosition | PR006 | Protection Relay 006 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_CircuitBreakerFailureFailExternalTrip | PR006 | Protection Relay 006 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_CircuitBreakerFailureInternalReTrip | PR006 | Protection Relay 006 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_CircuitBreakerFailureTimerRunning | PR006 | Protection Relay 006 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_CircuitBreakerOpenPosition | PR006 | Protection Relay 006 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_ACTripFlag | PR006 | Protection Relay 006 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_DCTripFlag | PR006 | Protection Relay 006 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_MCBTripFlag | PR006 | Protection Relay 006 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_RelayTripFlag | PR006 | Protection Relay 006 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_CircuitBreakerTripMaster1 | PR006 | Protection Relay 006 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_DirectionalEarthFault | PR006 | Protection Relay 006 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_DirectionalOvercurrentHighStage | PR006 | Protection Relay 006 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_DirectionalOvercurrentLowStage | PR006 | Protection Relay 006 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_EarthSwitchClosePosition | PR006 | Protection Relay 006 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_EarthSwitchOpenPosition | PR006 | Protection Relay 006 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_InstantaneousOvercurrent | PR006 | Protection Relay 006 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_LockoutRelayStatus | PR006 | Protection Relay 006 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_NegativeSequenceOvercurrentProtection | PR006 | Protection Relay 006 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_ProtectionRelayStatus | PR006 | Protection Relay 006 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_RemoteLocalControlStatus | PR006 | Protection Relay 006 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_RemoteLocalControlStatusR129_02 | PR006 | Protection Relay 006 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_SpringChargedDischargedAlarm | PR006 | Protection Relay 006 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_TestServicePositionStatus | PR006 | Protection Relay 006 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR006_TimeOvercurrent | PR006 | Protection Relay 006 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_CircuitBreakerClosePosition | PR007 | Protection Relay 007 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_CircuitBreakerFailureFailExternalTrip | PR007 | Protection Relay 007 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_CircuitBreakerFailureInternalReTrip | PR007 | Protection Relay 007 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_CircuitBreakerFailureTimerRunning | PR007 | Protection Relay 007 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_CircuitBreakerOpenPosition | PR007 | Protection Relay 007 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_ACTripFlag | PR007 | Protection Relay 007 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_DCTripFlag | PR007 | Protection Relay 007 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_MCBTripFlag | PR007 | Protection Relay 007 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_RelayTripFlag | PR007 | Protection Relay 007 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_CircuitBreakerTripMaster1 | PR007 | Protection Relay 007 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_DirectionalEarthFault | PR007 | Protection Relay 007 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_DirectionalOvercurrentHighStage | PR007 | Protection Relay 007 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_DirectionalOvercurrentLowStage | PR007 | Protection Relay 007 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_EarthSwitchClosePosition | PR007 | Protection Relay 007 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_EarthSwitchOpenPosition | PR007 | Protection Relay 007 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_InstantaneousOvercurrent | PR007 | Protection Relay 007 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_LockoutRelayStatus | PR007 | Protection Relay 007 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_NegativeSequenceOvercurrentProtection | PR007 | Protection Relay 007 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_ProtectionRelayStatus | PR007 | Protection Relay 007 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_RemoteLocalControlStatus | PR007 | Protection Relay 007 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_RemoteLocalControlStatusR129_02 | PR007 | Protection Relay 007 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_SpringChargedDischargedAlarm | PR007 | Protection Relay 007 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_TestServicePositionStatus | PR007 | Protection Relay 007 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR007_TimeOvercurrent | PR007 | Protection Relay 007 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_CircuitBreakerClosePosition | PR008 | Protection Relay 008 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_CircuitBreakerFailureFailExternalTrip | PR008 | Protection Relay 008 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_CircuitBreakerFailureInternalReTrip | PR008 | Protection Relay 008 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_CircuitBreakerFailureTimerRunning | PR008 | Protection Relay 008 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_CircuitBreakerOpenPosition | PR008 | Protection Relay 008 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_ACTripFlag | PR008 | Protection Relay 008 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_DCTripFlag | PR008 | Protection Relay 008 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_MCBTripFlag | PR008 | Protection Relay 008 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_RelayTripFlag | PR008 | Protection Relay 008 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_CircuitBreakerTripMaster1 | PR008 | Protection Relay 008 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_DirectionalEarthFault | PR008 | Protection Relay 008 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_DirectionalOvercurrentHighStage | PR008 | Protection Relay 008 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_DirectionalOvercurrentLowStage | PR008 | Protection Relay 008 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_EarthSwitchClosePosition | PR008 | Protection Relay 008 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_EarthSwitchOpenPosition | PR008 | Protection Relay 008 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_InstantaneousOvercurrent | PR008 | Protection Relay 008 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_LockoutRelayStatus | PR008 | Protection Relay 008 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_NegativeSequenceOvercurrentProtection | PR008 | Protection Relay 008 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_ProtectionRelayStatus | PR008 | Protection Relay 008 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_RemoteLocalControlStatus | PR008 | Protection Relay 008 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_RemoteLocalControlStatusR129_02 | PR008 | Protection Relay 008 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_SpringChargedDischargedAlarm | PR008 | Protection Relay 008 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_TestServicePositionStatus | PR008 | Protection Relay 008 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR008_TimeOvercurrent | PR008 | Protection Relay 008 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_CircuitBreakerClosePosition | PR009 | Protection Relay 009 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_CircuitBreakerFailureFailExternalTrip | PR009 | Protection Relay 009 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_CircuitBreakerFailureInternalReTrip | PR009 | Protection Relay 009 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_CircuitBreakerFailureTimerRunning | PR009 | Protection Relay 009 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_CircuitBreakerOpenPosition | PR009 | Protection Relay 009 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_ACTripFlag | PR009 | Protection Relay 009 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_DCTripFlag | PR009 | Protection Relay 009 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_MCBTripFlag | PR009 | Protection Relay 009 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_RelayTripFlag | PR009 | Protection Relay 009 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_CircuitBreakerTripMaster1 | PR009 | Protection Relay 009 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_DirectionalEarthFault | PR009 | Protection Relay 009 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_DirectionalOvercurrentHighStage | PR009 | Protection Relay 009 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_DirectionalOvercurrentLowStage | PR009 | Protection Relay 009 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_EarthSwitchClosePosition | PR009 | Protection Relay 009 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_EarthSwitchOpenPosition | PR009 | Protection Relay 009 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_InstantaneousOvercurrent | PR009 | Protection Relay 009 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_LockoutRelayStatus | PR009 | Protection Relay 009 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_NegativeSequenceOvercurrentProtection | PR009 | Protection Relay 009 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_ProtectionRelayStatus | PR009 | Protection Relay 009 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_RemoteLocalControlStatus | PR009 | Protection Relay 009 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_RemoteLocalControlStatusR129_02 | PR009 | Protection Relay 009 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_SpringChargedDischargedAlarm | PR009 | Protection Relay 009 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_TestServicePositionStatus | PR009 | Protection Relay 009 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR009_TimeOvercurrent | PR009 | Protection Relay 009 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_CircuitBreakerClosePosition | PR010 | Protection Relay 010 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_CircuitBreakerFailureFailExternalTrip | PR010 | Protection Relay 010 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_CircuitBreakerFailureInternalReTrip | PR010 | Protection Relay 010 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_CircuitBreakerFailureTimerRunning | PR010 | Protection Relay 010 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_CircuitBreakerOpenPosition | PR010 | Protection Relay 010 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_ACTripFlag | PR010 | Protection Relay 010 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_DCTripFlag | PR010 | Protection Relay 010 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_MCBTripFlag | PR010 | Protection Relay 010 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_RelayTripFlag | PR010 | Protection Relay 010 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_CircuitBreakerTripMaster1 | PR010 | Protection Relay 010 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_DirectionalEarthFault | PR010 | Protection Relay 010 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_DirectionalOvercurrentHighStage | PR010 | Protection Relay 010 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_DirectionalOvercurrentLowStage | PR010 | Protection Relay 010 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_EarthSwitchClosePosition | PR010 | Protection Relay 010 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_EarthSwitchOpenPosition | PR010 | Protection Relay 010 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_InstantaneousOvercurrent | PR010 | Protection Relay 010 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_LockoutRelayStatus | PR010 | Protection Relay 010 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_NegativeSequenceOvercurrentProtection | PR010 | Protection Relay 010 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_ProtectionRelayStatus | PR010 | Protection Relay 010 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_RemoteLocalControlStatus | PR010 | Protection Relay 010 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_RemoteLocalControlStatusR129_02 | PR010 | Protection Relay 010 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_SpringChargedDischargedAlarm | PR010 | Protection Relay 010 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_TestServicePositionStatus | PR010 | Protection Relay 010 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR010_TimeOvercurrent | PR010 | Protection Relay 010 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_CircuitBreakerClosePosition | PR011 | Protection Relay 011 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_CircuitBreakerFailureFailExternalTrip | PR011 | Protection Relay 011 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_CircuitBreakerFailureInternalReTrip | PR011 | Protection Relay 011 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_CircuitBreakerFailureTimerRunning | PR011 | Protection Relay 011 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_CircuitBreakerOpenPosition | PR011 | Protection Relay 011 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_ACTripFlag | PR011 | Protection Relay 011 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_DCTripFlag | PR011 | Protection Relay 011 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_MCBTripFlag | PR011 | Protection Relay 011 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_RelayTripFlag | PR011 | Protection Relay 011 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_CircuitBreakerTripMaster1 | PR011 | Protection Relay 011 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_DirectionalEarthFault | PR011 | Protection Relay 011 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_DirectionalOvercurrentHighStage | PR011 | Protection Relay 011 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_DirectionalOvercurrentLowStage | PR011 | Protection Relay 011 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_EarthSwitchClosePosition | PR011 | Protection Relay 011 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_EarthSwitchOpenPosition | PR011 | Protection Relay 011 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_InstantaneousOvercurrent | PR011 | Protection Relay 011 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_LockoutRelayStatus | PR011 | Protection Relay 011 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_NegativeSequenceOvercurrentProtection | PR011 | Protection Relay 011 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_ProtectionRelayStatus | PR011 | Protection Relay 011 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_RemoteLocalControlStatus | PR011 | Protection Relay 011 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_RemoteLocalControlStatusR129_02 | PR011 | Protection Relay 011 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_SpringChargedDischargedAlarm | PR011 | Protection Relay 011 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_TestServicePositionStatus | PR011 | Protection Relay 011 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR011_TimeOvercurrent | PR011 | Protection Relay 011 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_CircuitBreakerClosePosition | PR012 | Protection Relay 012 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_CircuitBreakerFailureFailExternalTrip | PR012 | Protection Relay 012 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_CircuitBreakerFailureInternalReTrip | PR012 | Protection Relay 012 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_CircuitBreakerFailureTimerRunning | PR012 | Protection Relay 012 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_CircuitBreakerOpenPosition | PR012 | Protection Relay 012 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_ACTripFlag | PR012 | Protection Relay 012 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_DCTripFlag | PR012 | Protection Relay 012 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_MCBTripFlag | PR012 | Protection Relay 012 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_RelayTripFlag | PR012 | Protection Relay 012 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_CircuitBreakerTripMaster1 | PR012 | Protection Relay 012 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_DirectionalEarthFault | PR012 | Protection Relay 012 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_DirectionalOvercurrentHighStage | PR012 | Protection Relay 012 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_DirectionalOvercurrentLowStage | PR012 | Protection Relay 012 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_EarthSwitchClosePosition | PR012 | Protection Relay 012 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_EarthSwitchOpenPosition | PR012 | Protection Relay 012 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_InstantaneousOvercurrent | PR012 | Protection Relay 012 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_LockoutRelayStatus | PR012 | Protection Relay 012 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_NegativeSequenceOvercurrentProtection | PR012 | Protection Relay 012 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_ProtectionRelayStatus | PR012 | Protection Relay 012 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_RemoteLocalControlStatus | PR012 | Protection Relay 012 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_RemoteLocalControlStatusR129_02 | PR012 | Protection Relay 012 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_SpringChargedDischargedAlarm | PR012 | Protection Relay 012 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_TestServicePositionStatus | PR012 | Protection Relay 012 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR012_TimeOvercurrent | PR012 | Protection Relay 012 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_CircuitBreakerClosePosition | PR013 | Protection Relay 013 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_CircuitBreakerFailureFailExternalTrip | PR013 | Protection Relay 013 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_CircuitBreakerFailureInternalReTrip | PR013 | Protection Relay 013 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_CircuitBreakerFailureTimerRunning | PR013 | Protection Relay 013 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_CircuitBreakerOpenPosition | PR013 | Protection Relay 013 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_ACTripFlag | PR013 | Protection Relay 013 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_DCTripFlag | PR013 | Protection Relay 013 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_MCBTripFlag | PR013 | Protection Relay 013 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_RelayTripFlag | PR013 | Protection Relay 013 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_CircuitBreakerTripMaster1 | PR013 | Protection Relay 013 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_DirectionalEarthFault | PR013 | Protection Relay 013 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_DirectionalOvercurrentHighStage | PR013 | Protection Relay 013 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_DirectionalOvercurrentLowStage | PR013 | Protection Relay 013 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_EarthSwitchClosePosition | PR013 | Protection Relay 013 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_EarthSwitchOpenPosition | PR013 | Protection Relay 013 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_InstantaneousOvercurrent | PR013 | Protection Relay 013 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_LockoutRelayStatus | PR013 | Protection Relay 013 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_NegativeSequenceOvercurrentProtection | PR013 | Protection Relay 013 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_ProtectionRelayStatus | PR013 | Protection Relay 013 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_RemoteLocalControlStatus | PR013 | Protection Relay 013 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_RemoteLocalControlStatusR129_02 | PR013 | Protection Relay 013 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_SpringChargedDischargedAlarm | PR013 | Protection Relay 013 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_TestServicePositionStatus | PR013 | Protection Relay 013 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR013_TimeOvercurrent | PR013 | Protection Relay 013 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_CircuitBreakerClosePosition | PR014 | Protection Relay 014 | Protection Relay | Circuit breaker close position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_CircuitBreakerFailureFailExternalTrip | PR014 | Protection Relay 014 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_CircuitBreakerFailureInternalReTrip | PR014 | Protection Relay 014 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_CircuitBreakerFailureTimerRunning | PR014 | Protection Relay 014 | Protection Relay | - (51BF) Circuit breaker failure Timer running | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_CircuitBreakerOpenPosition | PR014 | Protection Relay 014 | Protection Relay | Circuit breaker open position | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_ACTripFlag | PR014 | Protection Relay 014 | Protection Relay | AC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_DCTripFlag | PR014 | Protection Relay 014 | Protection Relay | DC Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_MCBTripFlag | PR014 | Protection Relay 014 | Protection Relay | MCB Trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_RelayTripFlag | PR014 | Protection Relay 014 | Protection Relay | Relay trip Flag | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_CircuitBreakerTripMaster1 | PR014 | Protection Relay 014 | Protection Relay | Circuit breaker tripMaster1 | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_DirectionalEarthFault | PR014 | Protection Relay 014 | Protection Relay | - (67N) Directional Earth Fault | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_DirectionalOvercurrentHighStage | PR014 | Protection Relay 014 | Protection Relay | - (67) Directional overcurrent high stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_DirectionalOvercurrentLowStage | PR014 | Protection Relay 014 | Protection Relay | - (67) Directional overcurrent low stage (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_EarthSwitchClosePosition | PR014 | Protection Relay 014 | Protection Relay | Earth switch close position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_EarthSwitchOpenPosition | PR014 | Protection Relay 014 | Protection Relay | Earth switch open position (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_InstantaneousOvercurrent | PR014 | Protection Relay 014 | Protection Relay | - (50) instantaneous overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_LockoutRelayStatus | PR014 | Protection Relay 014 | Protection Relay | - (86) Lockout Relay Status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_NegativeSequenceOvercurrentProtection | PR014 | Protection Relay 014 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_ProtectionRelayStatus | PR014 | Protection Relay 014 | Protection Relay | Protection Relay Status ( Alarm) | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_RemoteLocalControlStatus | PR014 | Protection Relay 014 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_RemoteLocalControlStatusR129_02 | PR014 | Protection Relay 014 | Protection Relay | Remote/local control status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_SpringChargedDischargedAlarm | PR014 | Protection Relay 014 | Protection Relay | Spring charged/discharged Alarm | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_TestServicePositionStatus | PR014 | Protection Relay 014 | Protection Relay | Test/service position status | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
PR014_TimeOvercurrent | PR014 | Protection Relay 014 | Protection Relay | - (51) Time Overcurrent | DI | Digital | Modbus | Direct | Teleindication | On Change | On Change
WS001_AmbientHumidity | WS001 | Weather Station 001 | Weather Station | Ambient Humidity | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
WS001_AmbientTemperature | WS001 | Weather Station 001 | Weather Station | Ambient temperature | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
WS001_CumulativeValueDirectRadiation | WS001 | Weather Station 001 | Weather Station | Cumulative value of direct radiation | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_CumulativeValuePhotosynthetic | WS001 | Weather Station 001 | Weather Station | Cumulative value of photosynthetic | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_CumulativeValueScatteredRadiation | WS001 | Weather Station 001 | Weather Station | Cumulative value of scattered radiation | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_CumulativeValueSunshineDuration | WS001 | Weather Station 001 | Weather Station | Cumulative value of sunshine duration | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_CumulativeValueTotalRadiation1 | WS001 | Weather Station 001 | Weather Station | Cumulative value of total radiation 1 | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_DailyCumulativeValueDirectRadiation | WS001 | Weather Station 001 | Weather Station | Daily cumulative value of direct radiation | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_DailyCumulativeValueNetRadiation | WS001 | Weather Station 001 | Weather Station | Daily cumulative value of net radiation | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_DailyCumulativeValuePhotosyntheticRadiation | WS001 | Weather Station 001 | Weather Station | Daily cumulative value of photosynthetic radiation | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_DailyCumulativeValueScatteredRadiation | WS001 | Weather Station 001 | Weather Station | Daily cumulative value of scattered radiation | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_DailyCumulativeValueTotalRadiation1 | WS001 | Weather Station 001 | Weather Station | Daily cumulative value of total radiation 1 | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_DailySunshineDuration | WS001 | Weather Station 001 | Weather Station | Daily sunshine duration | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_DewPointTemperature | WS001 | Weather Station 001 | Weather Station | Dew-point Temperature | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
WS001_InstantaneousValueTotalRadiation1 | WS001 | Weather Station 001 | Weather Station | Instantaneous value of total radiation 1 | AI | Analog | Modbus | Direct | Telemetry | Periodic | 300 s
WS001_InstantaneousWindDirection | WS001 | Weather Station 001 | Weather Station | Instantaneous wind direction | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
WS001_InstantaneousWindSpeed | WS001 | Weather Station 001 | Weather Station | Instantaneous wind speed | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
WS001_Temperature1 | WS001 | Weather Station 001 | Weather Station | Temperature 1 (Bracket) | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s
WS001_WindSpeed2Minutes | WS001 | Weather Station 001 | Weather Station | Wind speed in 2 minutes | AI | Analog | Modbus | Direct | Telemetry | Periodic | 60 s

## Alarm_List
Alarm List
Alarm Name | Source Tag | Device ID | Device Type | Signal Description | Acknowledge Required
ALM_INV001_ACOvervoltage | INV001_ACOvervoltage | INV001 | Inverter | AC Overvoltage | Yes
ALM_INV001_ACUndervoltage | INV001_ACUndervoltage | INV001 | Inverter | AC Undervoltage | Yes
ALM_INV001_AFCISelfCheckFailure | INV001_AFCISelfCheckFailure | INV001 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV001_AbnormalGrounding | INV001_AbnormalGrounding | INV001 | Inverter | Abnormal Grounding | Yes
ALM_INV001_AbnormalPVModuleConfiguration | INV001_AbnormalPVModuleConfiguration | INV001 | Inverter | Abnormal PV module configuration | Yes
ALM_INV001_AbnormalResidualCurrent | INV001_AbnormalResidualCurrent | INV001 | Inverter | Abnormal Residual Current | Yes
ALM_INV001_AbnormalStringPower | INV001_AbnormalStringPower | INV001 | Inverter | Abnormal String Power | Yes
ALM_INV001_ActiveIslanding | INV001_ActiveIslanding | INV001 | Inverter | Active Islanding | Yes
ALM_INV001_BuiltPIDOperationAbnormal | INV001_BuiltPIDOperationAbnormal | INV001 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV001_CabinetOvertemperature | INV001_CabinetOvertemperature | INV001 | Inverter | Cabinet Overtemperature | Yes
ALM_INV001_CommunicationFailure | INV001_CommunicationFailure | INV001 | Inverter | Communication Failure | Yes
ALM_INV001_CommunicationStatus | INV001_CommunicationStatus | INV001 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV001_DCArcFault | INV001_DCArcFault | INV001 | Inverter | DC Arc Fault | Yes
ALM_INV001_DCInsulationFault | INV001_DCInsulationFault | INV001 | Inverter | DC Insulation Fault | Yes
ALM_INV001_DCOvervoltage | INV001_DCOvervoltage | INV001 | Inverter | DC Overvoltage | Yes
ALM_INV001_DeviceFault | INV001_DeviceFault | INV001 | Inverter | Device Fault | Yes
ALM_INV001_ExternalFanAbnormal | INV001_ExternalFanAbnormal | INV001 | Inverter | External fan abnormal | Yes
ALM_INV001_FanFailure | INV001_FanFailure | INV001 | Inverter | Fan Failure | Yes
ALM_INV001_Faulty | INV001_Faulty | INV001 | Inverter | Faulty | Yes
ALM_INV001_FaultyMonitoringUnit | INV001_FaultyMonitoringUnit | INV001 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV001_FaultyPowerCollector | INV001_FaultyPowerCollector | INV001 | Inverter | Faulty Power Collector | Yes
ALM_INV001_GeneralFaultTrip | INV001_GeneralFaultTrip | INV001 | Inverter | General Fault Trip | Yes
ALM_INV001_GridConnectionDeratingInverterInternalCauses | INV001_GridConnectionDeratingInverterInternalCauses | INV001 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV001_GridConnectionDeratingPowerRationing | INV001_GridConnectionDeratingPowerRationing | INV001 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV001_GridLoss | INV001_GridLoss | INV001 | Inverter | Grid Loss | Yes
ALM_INV001_GridOverfrequency | INV001_GridOverfrequency | INV001 | Inverter | Grid Overfrequency | Yes
ALM_INV001_GridOvervoltage | INV001_GridOvervoltage | INV001 | Inverter | Grid Overvoltage | Yes
ALM_INV001_GridTiedOffGridControllerAbnormal | INV001_GridTiedOffGridControllerAbnormal | INV001 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV001_GridUnderfrequency | INV001_GridUnderfrequency | INV001 | Inverter | Grid Underfrequency | Yes
ALM_INV001_GridUndervoltage | INV001_GridUndervoltage | INV001 | Inverter | Grid Undervoltage | Yes
ALM_INV001_GroundFault | INV001_GroundFault | INV001 | Inverter | Ground Fault | Yes
ALM_INV001_HighInputStringVoltageGround | INV001_HighInputStringVoltageGround | INV001 | Inverter | High input string voltage to ground | Yes
ALM_INV001_HighStringInputVoltage | INV001_HighStringInputVoltage | INV001 | Inverter | High string input voltage | Yes
ALM_INV001_InverterTripHistoryAvailable | INV001_InverterTripHistoryAvailable | INV001 | Inverter | Inverter Trip History Available | Yes
ALM_INV001_IslandingDetectionStatus | INV001_IslandingDetectionStatus | INV001 | Inverter | Islanding Detection Status | Yes
ALM_INV001_LicenseExpired | INV001_LicenseExpired | INV001 | Inverter | License Expired | Yes
ALM_INV001_LockingStatus | INV001_LockingStatus | INV001 | Inverter | Locking status | Yes
ALM_INV001_LowInsulationResistance | INV001_LowInsulationResistance | INV001 | Inverter | Low Insulation Resistance | Yes
ALM_INV001_OffGridOutputOverload | INV001_OffGridOutputOverload | INV001 | Inverter | Off-grid output overload | Yes
ALM_INV001_OptimizerFault | INV001_OptimizerFault | INV001 | Inverter | Optimizer fault | Yes
ALM_INV001_OutputDCComponentOverhigh | INV001_OutputDCComponentOverhigh | INV001 | Inverter | Output DC Component Overhigh | Yes
ALM_INV001_OutputOvercurrent | INV001_OutputOvercurrent | INV001 | Inverter | Output Overcurrent | Yes
ALM_INV001_PVStringLoss | INV001_PVStringLoss | INV001 | Inverter | PV String Loss | Yes
ALM_INV001_PassiveIslanding | INV001_PassiveIslanding | INV001 | Inverter | Passive Islanding | Yes
ALM_INV001_PeripheralPortShortCircuit | INV001_PeripheralPortShortCircuit | INV001 | Inverter | Peripheral port short circuit | Yes
ALM_INV001_PhaseWireShortCircuitedPE | INV001_PhaseWireShortCircuitedPE | INV001 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV001_PowerLimitationActiveGridCommand | INV001_PowerLimitationActiveGridCommand | INV001 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV001_StringReverseConnection | INV001_StringReverseConnection | INV001 | Inverter | String Reverse Connection | Yes
ALM_INV001_StringReversePolarity | INV001_StringReversePolarity | INV001 | Inverter | String Reverse Polarity | Yes
ALM_INV001_TransientACOvervoltage | INV001_TransientACOvervoltage | INV001 | Inverter | Transient AC Overvoltage | Yes
ALM_INV001_WarningActive | INV001_WarningActive | INV001 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV002_ACOvervoltage | INV002_ACOvervoltage | INV002 | Inverter | AC Overvoltage | Yes
ALM_INV002_ACUndervoltage | INV002_ACUndervoltage | INV002 | Inverter | AC Undervoltage | Yes
ALM_INV002_AFCISelfCheckFailure | INV002_AFCISelfCheckFailure | INV002 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV002_AbnormalGrounding | INV002_AbnormalGrounding | INV002 | Inverter | Abnormal Grounding | Yes
ALM_INV002_AbnormalPVModuleConfiguration | INV002_AbnormalPVModuleConfiguration | INV002 | Inverter | Abnormal PV module configuration | Yes
ALM_INV002_AbnormalResidualCurrent | INV002_AbnormalResidualCurrent | INV002 | Inverter | Abnormal Residual Current | Yes
ALM_INV002_AbnormalStringPower | INV002_AbnormalStringPower | INV002 | Inverter | Abnormal String Power | Yes
ALM_INV002_ActiveIslanding | INV002_ActiveIslanding | INV002 | Inverter | Active Islanding | Yes
ALM_INV002_BuiltPIDOperationAbnormal | INV002_BuiltPIDOperationAbnormal | INV002 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV002_CabinetOvertemperature | INV002_CabinetOvertemperature | INV002 | Inverter | Cabinet Overtemperature | Yes
ALM_INV002_CommunicationFailure | INV002_CommunicationFailure | INV002 | Inverter | Communication Failure | Yes
ALM_INV002_CommunicationStatus | INV002_CommunicationStatus | INV002 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV002_DCArcFault | INV002_DCArcFault | INV002 | Inverter | DC Arc Fault | Yes
ALM_INV002_DCInsulationFault | INV002_DCInsulationFault | INV002 | Inverter | DC Insulation Fault | Yes
ALM_INV002_DCOvervoltage | INV002_DCOvervoltage | INV002 | Inverter | DC Overvoltage | Yes
ALM_INV002_DeviceFault | INV002_DeviceFault | INV002 | Inverter | Device Fault | Yes
ALM_INV002_ExternalFanAbnormal | INV002_ExternalFanAbnormal | INV002 | Inverter | External fan abnormal | Yes
ALM_INV002_FanFailure | INV002_FanFailure | INV002 | Inverter | Fan Failure | Yes
ALM_INV002_Faulty | INV002_Faulty | INV002 | Inverter | Faulty | Yes
ALM_INV002_FaultyMonitoringUnit | INV002_FaultyMonitoringUnit | INV002 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV002_FaultyPowerCollector | INV002_FaultyPowerCollector | INV002 | Inverter | Faulty Power Collector | Yes
ALM_INV002_GeneralFaultTrip | INV002_GeneralFaultTrip | INV002 | Inverter | General Fault Trip | Yes
ALM_INV002_GridConnectionDeratingInverterInternalCauses | INV002_GridConnectionDeratingInverterInternalCauses | INV002 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV002_GridConnectionDeratingPowerRationing | INV002_GridConnectionDeratingPowerRationing | INV002 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV002_GridLoss | INV002_GridLoss | INV002 | Inverter | Grid Loss | Yes
ALM_INV002_GridOverfrequency | INV002_GridOverfrequency | INV002 | Inverter | Grid Overfrequency | Yes
ALM_INV002_GridOvervoltage | INV002_GridOvervoltage | INV002 | Inverter | Grid Overvoltage | Yes
ALM_INV002_GridTiedOffGridControllerAbnormal | INV002_GridTiedOffGridControllerAbnormal | INV002 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV002_GridUnderfrequency | INV002_GridUnderfrequency | INV002 | Inverter | Grid Underfrequency | Yes
ALM_INV002_GridUndervoltage | INV002_GridUndervoltage | INV002 | Inverter | Grid Undervoltage | Yes
ALM_INV002_GroundFault | INV002_GroundFault | INV002 | Inverter | Ground Fault | Yes
ALM_INV002_HighInputStringVoltageGround | INV002_HighInputStringVoltageGround | INV002 | Inverter | High input string voltage to ground | Yes
ALM_INV002_HighStringInputVoltage | INV002_HighStringInputVoltage | INV002 | Inverter | High string input voltage | Yes
ALM_INV002_InverterTripHistoryAvailable | INV002_InverterTripHistoryAvailable | INV002 | Inverter | Inverter Trip History Available | Yes
ALM_INV002_IslandingDetectionStatus | INV002_IslandingDetectionStatus | INV002 | Inverter | Islanding Detection Status | Yes
ALM_INV002_LicenseExpired | INV002_LicenseExpired | INV002 | Inverter | License Expired | Yes
ALM_INV002_LockingStatus | INV002_LockingStatus | INV002 | Inverter | Locking status | Yes
ALM_INV002_LowInsulationResistance | INV002_LowInsulationResistance | INV002 | Inverter | Low Insulation Resistance | Yes
ALM_INV002_OffGridOutputOverload | INV002_OffGridOutputOverload | INV002 | Inverter | Off-grid output overload | Yes
ALM_INV002_OptimizerFault | INV002_OptimizerFault | INV002 | Inverter | Optimizer fault | Yes
ALM_INV002_OutputDCComponentOverhigh | INV002_OutputDCComponentOverhigh | INV002 | Inverter | Output DC Component Overhigh | Yes
ALM_INV002_OutputOvercurrent | INV002_OutputOvercurrent | INV002 | Inverter | Output Overcurrent | Yes
ALM_INV002_PVStringLoss | INV002_PVStringLoss | INV002 | Inverter | PV String Loss | Yes
ALM_INV002_PassiveIslanding | INV002_PassiveIslanding | INV002 | Inverter | Passive Islanding | Yes
ALM_INV002_PeripheralPortShortCircuit | INV002_PeripheralPortShortCircuit | INV002 | Inverter | Peripheral port short circuit | Yes
ALM_INV002_PhaseWireShortCircuitedPE | INV002_PhaseWireShortCircuitedPE | INV002 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV002_PowerLimitationActiveGridCommand | INV002_PowerLimitationActiveGridCommand | INV002 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV002_StringReverseConnection | INV002_StringReverseConnection | INV002 | Inverter | String Reverse Connection | Yes
ALM_INV002_StringReversePolarity | INV002_StringReversePolarity | INV002 | Inverter | String Reverse Polarity | Yes
ALM_INV002_TransientACOvervoltage | INV002_TransientACOvervoltage | INV002 | Inverter | Transient AC Overvoltage | Yes
ALM_INV002_WarningActive | INV002_WarningActive | INV002 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV003_ACOvervoltage | INV003_ACOvervoltage | INV003 | Inverter | AC Overvoltage | Yes
ALM_INV003_ACUndervoltage | INV003_ACUndervoltage | INV003 | Inverter | AC Undervoltage | Yes
ALM_INV003_AFCISelfCheckFailure | INV003_AFCISelfCheckFailure | INV003 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV003_AbnormalGrounding | INV003_AbnormalGrounding | INV003 | Inverter | Abnormal Grounding | Yes
ALM_INV003_AbnormalPVModuleConfiguration | INV003_AbnormalPVModuleConfiguration | INV003 | Inverter | Abnormal PV module configuration | Yes
ALM_INV003_AbnormalResidualCurrent | INV003_AbnormalResidualCurrent | INV003 | Inverter | Abnormal Residual Current | Yes
ALM_INV003_AbnormalStringPower | INV003_AbnormalStringPower | INV003 | Inverter | Abnormal String Power | Yes
ALM_INV003_ActiveIslanding | INV003_ActiveIslanding | INV003 | Inverter | Active Islanding | Yes
ALM_INV003_BuiltPIDOperationAbnormal | INV003_BuiltPIDOperationAbnormal | INV003 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV003_CabinetOvertemperature | INV003_CabinetOvertemperature | INV003 | Inverter | Cabinet Overtemperature | Yes
ALM_INV003_CommunicationFailure | INV003_CommunicationFailure | INV003 | Inverter | Communication Failure | Yes
ALM_INV003_CommunicationStatus | INV003_CommunicationStatus | INV003 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV003_DCArcFault | INV003_DCArcFault | INV003 | Inverter | DC Arc Fault | Yes
ALM_INV003_DCInsulationFault | INV003_DCInsulationFault | INV003 | Inverter | DC Insulation Fault | Yes
ALM_INV003_DCOvervoltage | INV003_DCOvervoltage | INV003 | Inverter | DC Overvoltage | Yes
ALM_INV003_DeviceFault | INV003_DeviceFault | INV003 | Inverter | Device Fault | Yes
ALM_INV003_ExternalFanAbnormal | INV003_ExternalFanAbnormal | INV003 | Inverter | External fan abnormal | Yes
ALM_INV003_FanFailure | INV003_FanFailure | INV003 | Inverter | Fan Failure | Yes
ALM_INV003_Faulty | INV003_Faulty | INV003 | Inverter | Faulty | Yes
ALM_INV003_FaultyMonitoringUnit | INV003_FaultyMonitoringUnit | INV003 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV003_FaultyPowerCollector | INV003_FaultyPowerCollector | INV003 | Inverter | Faulty Power Collector | Yes
ALM_INV003_GeneralFaultTrip | INV003_GeneralFaultTrip | INV003 | Inverter | General Fault Trip | Yes
ALM_INV003_GridConnectionDeratingInverterInternalCauses | INV003_GridConnectionDeratingInverterInternalCauses | INV003 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV003_GridConnectionDeratingPowerRationing | INV003_GridConnectionDeratingPowerRationing | INV003 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV003_GridLoss | INV003_GridLoss | INV003 | Inverter | Grid Loss | Yes
ALM_INV003_GridOverfrequency | INV003_GridOverfrequency | INV003 | Inverter | Grid Overfrequency | Yes
ALM_INV003_GridOvervoltage | INV003_GridOvervoltage | INV003 | Inverter | Grid Overvoltage | Yes
ALM_INV003_GridTiedOffGridControllerAbnormal | INV003_GridTiedOffGridControllerAbnormal | INV003 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV003_GridUnderfrequency | INV003_GridUnderfrequency | INV003 | Inverter | Grid Underfrequency | Yes
ALM_INV003_GridUndervoltage | INV003_GridUndervoltage | INV003 | Inverter | Grid Undervoltage | Yes
ALM_INV003_GroundFault | INV003_GroundFault | INV003 | Inverter | Ground Fault | Yes
ALM_INV003_HighInputStringVoltageGround | INV003_HighInputStringVoltageGround | INV003 | Inverter | High input string voltage to ground | Yes
ALM_INV003_HighStringInputVoltage | INV003_HighStringInputVoltage | INV003 | Inverter | High string input voltage | Yes
ALM_INV003_InverterTripHistoryAvailable | INV003_InverterTripHistoryAvailable | INV003 | Inverter | Inverter Trip History Available | Yes
ALM_INV003_IslandingDetectionStatus | INV003_IslandingDetectionStatus | INV003 | Inverter | Islanding Detection Status | Yes
ALM_INV003_LicenseExpired | INV003_LicenseExpired | INV003 | Inverter | License Expired | Yes
ALM_INV003_LockingStatus | INV003_LockingStatus | INV003 | Inverter | Locking status | Yes
ALM_INV003_LowInsulationResistance | INV003_LowInsulationResistance | INV003 | Inverter | Low Insulation Resistance | Yes
ALM_INV003_OffGridOutputOverload | INV003_OffGridOutputOverload | INV003 | Inverter | Off-grid output overload | Yes
ALM_INV003_OptimizerFault | INV003_OptimizerFault | INV003 | Inverter | Optimizer fault | Yes
ALM_INV003_OutputDCComponentOverhigh | INV003_OutputDCComponentOverhigh | INV003 | Inverter | Output DC Component Overhigh | Yes
ALM_INV003_OutputOvercurrent | INV003_OutputOvercurrent | INV003 | Inverter | Output Overcurrent | Yes
ALM_INV003_PVStringLoss | INV003_PVStringLoss | INV003 | Inverter | PV String Loss | Yes
ALM_INV003_PassiveIslanding | INV003_PassiveIslanding | INV003 | Inverter | Passive Islanding | Yes
ALM_INV003_PeripheralPortShortCircuit | INV003_PeripheralPortShortCircuit | INV003 | Inverter | Peripheral port short circuit | Yes
ALM_INV003_PhaseWireShortCircuitedPE | INV003_PhaseWireShortCircuitedPE | INV003 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV003_PowerLimitationActiveGridCommand | INV003_PowerLimitationActiveGridCommand | INV003 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV003_StringReverseConnection | INV003_StringReverseConnection | INV003 | Inverter | String Reverse Connection | Yes
ALM_INV003_StringReversePolarity | INV003_StringReversePolarity | INV003 | Inverter | String Reverse Polarity | Yes
ALM_INV003_TransientACOvervoltage | INV003_TransientACOvervoltage | INV003 | Inverter | Transient AC Overvoltage | Yes
ALM_INV003_WarningActive | INV003_WarningActive | INV003 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV004_ACOvervoltage | INV004_ACOvervoltage | INV004 | Inverter | AC Overvoltage | Yes
ALM_INV004_ACUndervoltage | INV004_ACUndervoltage | INV004 | Inverter | AC Undervoltage | Yes
ALM_INV004_AFCISelfCheckFailure | INV004_AFCISelfCheckFailure | INV004 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV004_AbnormalGrounding | INV004_AbnormalGrounding | INV004 | Inverter | Abnormal Grounding | Yes
ALM_INV004_AbnormalPVModuleConfiguration | INV004_AbnormalPVModuleConfiguration | INV004 | Inverter | Abnormal PV module configuration | Yes
ALM_INV004_AbnormalResidualCurrent | INV004_AbnormalResidualCurrent | INV004 | Inverter | Abnormal Residual Current | Yes
ALM_INV004_AbnormalStringPower | INV004_AbnormalStringPower | INV004 | Inverter | Abnormal String Power | Yes
ALM_INV004_ActiveIslanding | INV004_ActiveIslanding | INV004 | Inverter | Active Islanding | Yes
ALM_INV004_BuiltPIDOperationAbnormal | INV004_BuiltPIDOperationAbnormal | INV004 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV004_CabinetOvertemperature | INV004_CabinetOvertemperature | INV004 | Inverter | Cabinet Overtemperature | Yes
ALM_INV004_CommunicationFailure | INV004_CommunicationFailure | INV004 | Inverter | Communication Failure | Yes
ALM_INV004_CommunicationStatus | INV004_CommunicationStatus | INV004 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV004_DCArcFault | INV004_DCArcFault | INV004 | Inverter | DC Arc Fault | Yes
ALM_INV004_DCInsulationFault | INV004_DCInsulationFault | INV004 | Inverter | DC Insulation Fault | Yes
ALM_INV004_DCOvervoltage | INV004_DCOvervoltage | INV004 | Inverter | DC Overvoltage | Yes
ALM_INV004_DeviceFault | INV004_DeviceFault | INV004 | Inverter | Device Fault | Yes
ALM_INV004_ExternalFanAbnormal | INV004_ExternalFanAbnormal | INV004 | Inverter | External fan abnormal | Yes
ALM_INV004_FanFailure | INV004_FanFailure | INV004 | Inverter | Fan Failure | Yes
ALM_INV004_Faulty | INV004_Faulty | INV004 | Inverter | Faulty | Yes
ALM_INV004_FaultyMonitoringUnit | INV004_FaultyMonitoringUnit | INV004 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV004_FaultyPowerCollector | INV004_FaultyPowerCollector | INV004 | Inverter | Faulty Power Collector | Yes
ALM_INV004_GeneralFaultTrip | INV004_GeneralFaultTrip | INV004 | Inverter | General Fault Trip | Yes
ALM_INV004_GridConnectionDeratingInverterInternalCauses | INV004_GridConnectionDeratingInverterInternalCauses | INV004 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV004_GridConnectionDeratingPowerRationing | INV004_GridConnectionDeratingPowerRationing | INV004 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV004_GridLoss | INV004_GridLoss | INV004 | Inverter | Grid Loss | Yes
ALM_INV004_GridOverfrequency | INV004_GridOverfrequency | INV004 | Inverter | Grid Overfrequency | Yes
ALM_INV004_GridOvervoltage | INV004_GridOvervoltage | INV004 | Inverter | Grid Overvoltage | Yes
ALM_INV004_GridTiedOffGridControllerAbnormal | INV004_GridTiedOffGridControllerAbnormal | INV004 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV004_GridUnderfrequency | INV004_GridUnderfrequency | INV004 | Inverter | Grid Underfrequency | Yes
ALM_INV004_GridUndervoltage | INV004_GridUndervoltage | INV004 | Inverter | Grid Undervoltage | Yes
ALM_INV004_GroundFault | INV004_GroundFault | INV004 | Inverter | Ground Fault | Yes
ALM_INV004_HighInputStringVoltageGround | INV004_HighInputStringVoltageGround | INV004 | Inverter | High input string voltage to ground | Yes
ALM_INV004_HighStringInputVoltage | INV004_HighStringInputVoltage | INV004 | Inverter | High string input voltage | Yes
ALM_INV004_InverterTripHistoryAvailable | INV004_InverterTripHistoryAvailable | INV004 | Inverter | Inverter Trip History Available | Yes
ALM_INV004_IslandingDetectionStatus | INV004_IslandingDetectionStatus | INV004 | Inverter | Islanding Detection Status | Yes
ALM_INV004_LicenseExpired | INV004_LicenseExpired | INV004 | Inverter | License Expired | Yes
ALM_INV004_LockingStatus | INV004_LockingStatus | INV004 | Inverter | Locking status | Yes
ALM_INV004_LowInsulationResistance | INV004_LowInsulationResistance | INV004 | Inverter | Low Insulation Resistance | Yes
ALM_INV004_OffGridOutputOverload | INV004_OffGridOutputOverload | INV004 | Inverter | Off-grid output overload | Yes
ALM_INV004_OptimizerFault | INV004_OptimizerFault | INV004 | Inverter | Optimizer fault | Yes
ALM_INV004_OutputDCComponentOverhigh | INV004_OutputDCComponentOverhigh | INV004 | Inverter | Output DC Component Overhigh | Yes
ALM_INV004_OutputOvercurrent | INV004_OutputOvercurrent | INV004 | Inverter | Output Overcurrent | Yes
ALM_INV004_PVStringLoss | INV004_PVStringLoss | INV004 | Inverter | PV String Loss | Yes
ALM_INV004_PassiveIslanding | INV004_PassiveIslanding | INV004 | Inverter | Passive Islanding | Yes
ALM_INV004_PeripheralPortShortCircuit | INV004_PeripheralPortShortCircuit | INV004 | Inverter | Peripheral port short circuit | Yes
ALM_INV004_PhaseWireShortCircuitedPE | INV004_PhaseWireShortCircuitedPE | INV004 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV004_PowerLimitationActiveGridCommand | INV004_PowerLimitationActiveGridCommand | INV004 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV004_StringReverseConnection | INV004_StringReverseConnection | INV004 | Inverter | String Reverse Connection | Yes
ALM_INV004_StringReversePolarity | INV004_StringReversePolarity | INV004 | Inverter | String Reverse Polarity | Yes
ALM_INV004_TransientACOvervoltage | INV004_TransientACOvervoltage | INV004 | Inverter | Transient AC Overvoltage | Yes
ALM_INV004_WarningActive | INV004_WarningActive | INV004 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV005_ACOvervoltage | INV005_ACOvervoltage | INV005 | Inverter | AC Overvoltage | Yes
ALM_INV005_ACUndervoltage | INV005_ACUndervoltage | INV005 | Inverter | AC Undervoltage | Yes
ALM_INV005_AFCISelfCheckFailure | INV005_AFCISelfCheckFailure | INV005 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV005_AbnormalGrounding | INV005_AbnormalGrounding | INV005 | Inverter | Abnormal Grounding | Yes
ALM_INV005_AbnormalPVModuleConfiguration | INV005_AbnormalPVModuleConfiguration | INV005 | Inverter | Abnormal PV module configuration | Yes
ALM_INV005_AbnormalResidualCurrent | INV005_AbnormalResidualCurrent | INV005 | Inverter | Abnormal Residual Current | Yes
ALM_INV005_AbnormalStringPower | INV005_AbnormalStringPower | INV005 | Inverter | Abnormal String Power | Yes
ALM_INV005_ActiveIslanding | INV005_ActiveIslanding | INV005 | Inverter | Active Islanding | Yes
ALM_INV005_BuiltPIDOperationAbnormal | INV005_BuiltPIDOperationAbnormal | INV005 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV005_CabinetOvertemperature | INV005_CabinetOvertemperature | INV005 | Inverter | Cabinet Overtemperature | Yes
ALM_INV005_CommunicationFailure | INV005_CommunicationFailure | INV005 | Inverter | Communication Failure | Yes
ALM_INV005_CommunicationStatus | INV005_CommunicationStatus | INV005 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV005_DCArcFault | INV005_DCArcFault | INV005 | Inverter | DC Arc Fault | Yes
ALM_INV005_DCInsulationFault | INV005_DCInsulationFault | INV005 | Inverter | DC Insulation Fault | Yes
ALM_INV005_DCOvervoltage | INV005_DCOvervoltage | INV005 | Inverter | DC Overvoltage | Yes
ALM_INV005_DeviceFault | INV005_DeviceFault | INV005 | Inverter | Device Fault | Yes
ALM_INV005_ExternalFanAbnormal | INV005_ExternalFanAbnormal | INV005 | Inverter | External fan abnormal | Yes
ALM_INV005_FanFailure | INV005_FanFailure | INV005 | Inverter | Fan Failure | Yes
ALM_INV005_Faulty | INV005_Faulty | INV005 | Inverter | Faulty | Yes
ALM_INV005_FaultyMonitoringUnit | INV005_FaultyMonitoringUnit | INV005 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV005_FaultyPowerCollector | INV005_FaultyPowerCollector | INV005 | Inverter | Faulty Power Collector | Yes
ALM_INV005_GeneralFaultTrip | INV005_GeneralFaultTrip | INV005 | Inverter | General Fault Trip | Yes
ALM_INV005_GridConnectionDeratingInverterInternalCauses | INV005_GridConnectionDeratingInverterInternalCauses | INV005 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV005_GridConnectionDeratingPowerRationing | INV005_GridConnectionDeratingPowerRationing | INV005 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV005_GridLoss | INV005_GridLoss | INV005 | Inverter | Grid Loss | Yes
ALM_INV005_GridOverfrequency | INV005_GridOverfrequency | INV005 | Inverter | Grid Overfrequency | Yes
ALM_INV005_GridOvervoltage | INV005_GridOvervoltage | INV005 | Inverter | Grid Overvoltage | Yes
ALM_INV005_GridTiedOffGridControllerAbnormal | INV005_GridTiedOffGridControllerAbnormal | INV005 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV005_GridUnderfrequency | INV005_GridUnderfrequency | INV005 | Inverter | Grid Underfrequency | Yes
ALM_INV005_GridUndervoltage | INV005_GridUndervoltage | INV005 | Inverter | Grid Undervoltage | Yes
ALM_INV005_GroundFault | INV005_GroundFault | INV005 | Inverter | Ground Fault | Yes
ALM_INV005_HighInputStringVoltageGround | INV005_HighInputStringVoltageGround | INV005 | Inverter | High input string voltage to ground | Yes
ALM_INV005_HighStringInputVoltage | INV005_HighStringInputVoltage | INV005 | Inverter | High string input voltage | Yes
ALM_INV005_InverterTripHistoryAvailable | INV005_InverterTripHistoryAvailable | INV005 | Inverter | Inverter Trip History Available | Yes
ALM_INV005_IslandingDetectionStatus | INV005_IslandingDetectionStatus | INV005 | Inverter | Islanding Detection Status | Yes
ALM_INV005_LicenseExpired | INV005_LicenseExpired | INV005 | Inverter | License Expired | Yes
ALM_INV005_LockingStatus | INV005_LockingStatus | INV005 | Inverter | Locking status | Yes
ALM_INV005_LowInsulationResistance | INV005_LowInsulationResistance | INV005 | Inverter | Low Insulation Resistance | Yes
ALM_INV005_OffGridOutputOverload | INV005_OffGridOutputOverload | INV005 | Inverter | Off-grid output overload | Yes
ALM_INV005_OptimizerFault | INV005_OptimizerFault | INV005 | Inverter | Optimizer fault | Yes
ALM_INV005_OutputDCComponentOverhigh | INV005_OutputDCComponentOverhigh | INV005 | Inverter | Output DC Component Overhigh | Yes
ALM_INV005_OutputOvercurrent | INV005_OutputOvercurrent | INV005 | Inverter | Output Overcurrent | Yes
ALM_INV005_PVStringLoss | INV005_PVStringLoss | INV005 | Inverter | PV String Loss | Yes
ALM_INV005_PassiveIslanding | INV005_PassiveIslanding | INV005 | Inverter | Passive Islanding | Yes
ALM_INV005_PeripheralPortShortCircuit | INV005_PeripheralPortShortCircuit | INV005 | Inverter | Peripheral port short circuit | Yes
ALM_INV005_PhaseWireShortCircuitedPE | INV005_PhaseWireShortCircuitedPE | INV005 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV005_PowerLimitationActiveGridCommand | INV005_PowerLimitationActiveGridCommand | INV005 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV005_StringReverseConnection | INV005_StringReverseConnection | INV005 | Inverter | String Reverse Connection | Yes
ALM_INV005_StringReversePolarity | INV005_StringReversePolarity | INV005 | Inverter | String Reverse Polarity | Yes
ALM_INV005_TransientACOvervoltage | INV005_TransientACOvervoltage | INV005 | Inverter | Transient AC Overvoltage | Yes
ALM_INV005_WarningActive | INV005_WarningActive | INV005 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV006_ACOvervoltage | INV006_ACOvervoltage | INV006 | Inverter | AC Overvoltage | Yes
ALM_INV006_ACUndervoltage | INV006_ACUndervoltage | INV006 | Inverter | AC Undervoltage | Yes
ALM_INV006_AFCISelfCheckFailure | INV006_AFCISelfCheckFailure | INV006 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV006_AbnormalGrounding | INV006_AbnormalGrounding | INV006 | Inverter | Abnormal Grounding | Yes
ALM_INV006_AbnormalPVModuleConfiguration | INV006_AbnormalPVModuleConfiguration | INV006 | Inverter | Abnormal PV module configuration | Yes
ALM_INV006_AbnormalResidualCurrent | INV006_AbnormalResidualCurrent | INV006 | Inverter | Abnormal Residual Current | Yes
ALM_INV006_AbnormalStringPower | INV006_AbnormalStringPower | INV006 | Inverter | Abnormal String Power | Yes
ALM_INV006_ActiveIslanding | INV006_ActiveIslanding | INV006 | Inverter | Active Islanding | Yes
ALM_INV006_BuiltPIDOperationAbnormal | INV006_BuiltPIDOperationAbnormal | INV006 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV006_CabinetOvertemperature | INV006_CabinetOvertemperature | INV006 | Inverter | Cabinet Overtemperature | Yes
ALM_INV006_CommunicationFailure | INV006_CommunicationFailure | INV006 | Inverter | Communication Failure | Yes
ALM_INV006_CommunicationStatus | INV006_CommunicationStatus | INV006 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV006_DCArcFault | INV006_DCArcFault | INV006 | Inverter | DC Arc Fault | Yes
ALM_INV006_DCInsulationFault | INV006_DCInsulationFault | INV006 | Inverter | DC Insulation Fault | Yes
ALM_INV006_DCOvervoltage | INV006_DCOvervoltage | INV006 | Inverter | DC Overvoltage | Yes
ALM_INV006_DeviceFault | INV006_DeviceFault | INV006 | Inverter | Device Fault | Yes
ALM_INV006_ExternalFanAbnormal | INV006_ExternalFanAbnormal | INV006 | Inverter | External fan abnormal | Yes
ALM_INV006_FanFailure | INV006_FanFailure | INV006 | Inverter | Fan Failure | Yes
ALM_INV006_Faulty | INV006_Faulty | INV006 | Inverter | Faulty | Yes
ALM_INV006_FaultyMonitoringUnit | INV006_FaultyMonitoringUnit | INV006 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV006_FaultyPowerCollector | INV006_FaultyPowerCollector | INV006 | Inverter | Faulty Power Collector | Yes
ALM_INV006_GeneralFaultTrip | INV006_GeneralFaultTrip | INV006 | Inverter | General Fault Trip | Yes
ALM_INV006_GridConnectionDeratingInverterInternalCauses | INV006_GridConnectionDeratingInverterInternalCauses | INV006 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV006_GridConnectionDeratingPowerRationing | INV006_GridConnectionDeratingPowerRationing | INV006 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV006_GridLoss | INV006_GridLoss | INV006 | Inverter | Grid Loss | Yes
ALM_INV006_GridOverfrequency | INV006_GridOverfrequency | INV006 | Inverter | Grid Overfrequency | Yes
ALM_INV006_GridOvervoltage | INV006_GridOvervoltage | INV006 | Inverter | Grid Overvoltage | Yes
ALM_INV006_GridTiedOffGridControllerAbnormal | INV006_GridTiedOffGridControllerAbnormal | INV006 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV006_GridUnderfrequency | INV006_GridUnderfrequency | INV006 | Inverter | Grid Underfrequency | Yes
ALM_INV006_GridUndervoltage | INV006_GridUndervoltage | INV006 | Inverter | Grid Undervoltage | Yes
ALM_INV006_GroundFault | INV006_GroundFault | INV006 | Inverter | Ground Fault | Yes
ALM_INV006_HighInputStringVoltageGround | INV006_HighInputStringVoltageGround | INV006 | Inverter | High input string voltage to ground | Yes
ALM_INV006_HighStringInputVoltage | INV006_HighStringInputVoltage | INV006 | Inverter | High string input voltage | Yes
ALM_INV006_InverterTripHistoryAvailable | INV006_InverterTripHistoryAvailable | INV006 | Inverter | Inverter Trip History Available | Yes
ALM_INV006_IslandingDetectionStatus | INV006_IslandingDetectionStatus | INV006 | Inverter | Islanding Detection Status | Yes
ALM_INV006_LicenseExpired | INV006_LicenseExpired | INV006 | Inverter | License Expired | Yes
ALM_INV006_LockingStatus | INV006_LockingStatus | INV006 | Inverter | Locking status | Yes
ALM_INV006_LowInsulationResistance | INV006_LowInsulationResistance | INV006 | Inverter | Low Insulation Resistance | Yes
ALM_INV006_OffGridOutputOverload | INV006_OffGridOutputOverload | INV006 | Inverter | Off-grid output overload | Yes
ALM_INV006_OptimizerFault | INV006_OptimizerFault | INV006 | Inverter | Optimizer fault | Yes
ALM_INV006_OutputDCComponentOverhigh | INV006_OutputDCComponentOverhigh | INV006 | Inverter | Output DC Component Overhigh | Yes
ALM_INV006_OutputOvercurrent | INV006_OutputOvercurrent | INV006 | Inverter | Output Overcurrent | Yes
ALM_INV006_PVStringLoss | INV006_PVStringLoss | INV006 | Inverter | PV String Loss | Yes
ALM_INV006_PassiveIslanding | INV006_PassiveIslanding | INV006 | Inverter | Passive Islanding | Yes
ALM_INV006_PeripheralPortShortCircuit | INV006_PeripheralPortShortCircuit | INV006 | Inverter | Peripheral port short circuit | Yes
ALM_INV006_PhaseWireShortCircuitedPE | INV006_PhaseWireShortCircuitedPE | INV006 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV006_PowerLimitationActiveGridCommand | INV006_PowerLimitationActiveGridCommand | INV006 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV006_StringReverseConnection | INV006_StringReverseConnection | INV006 | Inverter | String Reverse Connection | Yes
ALM_INV006_StringReversePolarity | INV006_StringReversePolarity | INV006 | Inverter | String Reverse Polarity | Yes
ALM_INV006_TransientACOvervoltage | INV006_TransientACOvervoltage | INV006 | Inverter | Transient AC Overvoltage | Yes
ALM_INV006_WarningActive | INV006_WarningActive | INV006 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV007_ACOvervoltage | INV007_ACOvervoltage | INV007 | Inverter | AC Overvoltage | Yes
ALM_INV007_ACUndervoltage | INV007_ACUndervoltage | INV007 | Inverter | AC Undervoltage | Yes
ALM_INV007_AFCISelfCheckFailure | INV007_AFCISelfCheckFailure | INV007 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV007_AbnormalGrounding | INV007_AbnormalGrounding | INV007 | Inverter | Abnormal Grounding | Yes
ALM_INV007_AbnormalPVModuleConfiguration | INV007_AbnormalPVModuleConfiguration | INV007 | Inverter | Abnormal PV module configuration | Yes
ALM_INV007_AbnormalResidualCurrent | INV007_AbnormalResidualCurrent | INV007 | Inverter | Abnormal Residual Current | Yes
ALM_INV007_AbnormalStringPower | INV007_AbnormalStringPower | INV007 | Inverter | Abnormal String Power | Yes
ALM_INV007_ActiveIslanding | INV007_ActiveIslanding | INV007 | Inverter | Active Islanding | Yes
ALM_INV007_BuiltPIDOperationAbnormal | INV007_BuiltPIDOperationAbnormal | INV007 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV007_CabinetOvertemperature | INV007_CabinetOvertemperature | INV007 | Inverter | Cabinet Overtemperature | Yes
ALM_INV007_CommunicationFailure | INV007_CommunicationFailure | INV007 | Inverter | Communication Failure | Yes
ALM_INV007_CommunicationStatus | INV007_CommunicationStatus | INV007 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV007_DCArcFault | INV007_DCArcFault | INV007 | Inverter | DC Arc Fault | Yes
ALM_INV007_DCInsulationFault | INV007_DCInsulationFault | INV007 | Inverter | DC Insulation Fault | Yes
ALM_INV007_DCOvervoltage | INV007_DCOvervoltage | INV007 | Inverter | DC Overvoltage | Yes
ALM_INV007_DeviceFault | INV007_DeviceFault | INV007 | Inverter | Device Fault | Yes
ALM_INV007_ExternalFanAbnormal | INV007_ExternalFanAbnormal | INV007 | Inverter | External fan abnormal | Yes
ALM_INV007_FanFailure | INV007_FanFailure | INV007 | Inverter | Fan Failure | Yes
ALM_INV007_Faulty | INV007_Faulty | INV007 | Inverter | Faulty | Yes
ALM_INV007_FaultyMonitoringUnit | INV007_FaultyMonitoringUnit | INV007 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV007_FaultyPowerCollector | INV007_FaultyPowerCollector | INV007 | Inverter | Faulty Power Collector | Yes
ALM_INV007_GeneralFaultTrip | INV007_GeneralFaultTrip | INV007 | Inverter | General Fault Trip | Yes
ALM_INV007_GridConnectionDeratingInverterInternalCauses | INV007_GridConnectionDeratingInverterInternalCauses | INV007 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV007_GridConnectionDeratingPowerRationing | INV007_GridConnectionDeratingPowerRationing | INV007 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV007_GridLoss | INV007_GridLoss | INV007 | Inverter | Grid Loss | Yes
ALM_INV007_GridOverfrequency | INV007_GridOverfrequency | INV007 | Inverter | Grid Overfrequency | Yes
ALM_INV007_GridOvervoltage | INV007_GridOvervoltage | INV007 | Inverter | Grid Overvoltage | Yes
ALM_INV007_GridTiedOffGridControllerAbnormal | INV007_GridTiedOffGridControllerAbnormal | INV007 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV007_GridUnderfrequency | INV007_GridUnderfrequency | INV007 | Inverter | Grid Underfrequency | Yes
ALM_INV007_GridUndervoltage | INV007_GridUndervoltage | INV007 | Inverter | Grid Undervoltage | Yes
ALM_INV007_GroundFault | INV007_GroundFault | INV007 | Inverter | Ground Fault | Yes
ALM_INV007_HighInputStringVoltageGround | INV007_HighInputStringVoltageGround | INV007 | Inverter | High input string voltage to ground | Yes
ALM_INV007_HighStringInputVoltage | INV007_HighStringInputVoltage | INV007 | Inverter | High string input voltage | Yes
ALM_INV007_InverterTripHistoryAvailable | INV007_InverterTripHistoryAvailable | INV007 | Inverter | Inverter Trip History Available | Yes
ALM_INV007_IslandingDetectionStatus | INV007_IslandingDetectionStatus | INV007 | Inverter | Islanding Detection Status | Yes
ALM_INV007_LicenseExpired | INV007_LicenseExpired | INV007 | Inverter | License Expired | Yes
ALM_INV007_LockingStatus | INV007_LockingStatus | INV007 | Inverter | Locking status | Yes
ALM_INV007_LowInsulationResistance | INV007_LowInsulationResistance | INV007 | Inverter | Low Insulation Resistance | Yes
ALM_INV007_OffGridOutputOverload | INV007_OffGridOutputOverload | INV007 | Inverter | Off-grid output overload | Yes
ALM_INV007_OptimizerFault | INV007_OptimizerFault | INV007 | Inverter | Optimizer fault | Yes
ALM_INV007_OutputDCComponentOverhigh | INV007_OutputDCComponentOverhigh | INV007 | Inverter | Output DC Component Overhigh | Yes
ALM_INV007_OutputOvercurrent | INV007_OutputOvercurrent | INV007 | Inverter | Output Overcurrent | Yes
ALM_INV007_PVStringLoss | INV007_PVStringLoss | INV007 | Inverter | PV String Loss | Yes
ALM_INV007_PassiveIslanding | INV007_PassiveIslanding | INV007 | Inverter | Passive Islanding | Yes
ALM_INV007_PeripheralPortShortCircuit | INV007_PeripheralPortShortCircuit | INV007 | Inverter | Peripheral port short circuit | Yes
ALM_INV007_PhaseWireShortCircuitedPE | INV007_PhaseWireShortCircuitedPE | INV007 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV007_PowerLimitationActiveGridCommand | INV007_PowerLimitationActiveGridCommand | INV007 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV007_StringReverseConnection | INV007_StringReverseConnection | INV007 | Inverter | String Reverse Connection | Yes
ALM_INV007_StringReversePolarity | INV007_StringReversePolarity | INV007 | Inverter | String Reverse Polarity | Yes
ALM_INV007_TransientACOvervoltage | INV007_TransientACOvervoltage | INV007 | Inverter | Transient AC Overvoltage | Yes
ALM_INV007_WarningActive | INV007_WarningActive | INV007 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV008_ACOvervoltage | INV008_ACOvervoltage | INV008 | Inverter | AC Overvoltage | Yes
ALM_INV008_ACUndervoltage | INV008_ACUndervoltage | INV008 | Inverter | AC Undervoltage | Yes
ALM_INV008_AFCISelfCheckFailure | INV008_AFCISelfCheckFailure | INV008 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV008_AbnormalGrounding | INV008_AbnormalGrounding | INV008 | Inverter | Abnormal Grounding | Yes
ALM_INV008_AbnormalPVModuleConfiguration | INV008_AbnormalPVModuleConfiguration | INV008 | Inverter | Abnormal PV module configuration | Yes
ALM_INV008_AbnormalResidualCurrent | INV008_AbnormalResidualCurrent | INV008 | Inverter | Abnormal Residual Current | Yes
ALM_INV008_AbnormalStringPower | INV008_AbnormalStringPower | INV008 | Inverter | Abnormal String Power | Yes
ALM_INV008_ActiveIslanding | INV008_ActiveIslanding | INV008 | Inverter | Active Islanding | Yes
ALM_INV008_BuiltPIDOperationAbnormal | INV008_BuiltPIDOperationAbnormal | INV008 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV008_CabinetOvertemperature | INV008_CabinetOvertemperature | INV008 | Inverter | Cabinet Overtemperature | Yes
ALM_INV008_CommunicationFailure | INV008_CommunicationFailure | INV008 | Inverter | Communication Failure | Yes
ALM_INV008_CommunicationStatus | INV008_CommunicationStatus | INV008 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV008_DCArcFault | INV008_DCArcFault | INV008 | Inverter | DC Arc Fault | Yes
ALM_INV008_DCInsulationFault | INV008_DCInsulationFault | INV008 | Inverter | DC Insulation Fault | Yes
ALM_INV008_DCOvervoltage | INV008_DCOvervoltage | INV008 | Inverter | DC Overvoltage | Yes
ALM_INV008_DeviceFault | INV008_DeviceFault | INV008 | Inverter | Device Fault | Yes
ALM_INV008_ExternalFanAbnormal | INV008_ExternalFanAbnormal | INV008 | Inverter | External fan abnormal | Yes
ALM_INV008_FanFailure | INV008_FanFailure | INV008 | Inverter | Fan Failure | Yes
ALM_INV008_Faulty | INV008_Faulty | INV008 | Inverter | Faulty | Yes
ALM_INV008_FaultyMonitoringUnit | INV008_FaultyMonitoringUnit | INV008 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV008_FaultyPowerCollector | INV008_FaultyPowerCollector | INV008 | Inverter | Faulty Power Collector | Yes
ALM_INV008_GeneralFaultTrip | INV008_GeneralFaultTrip | INV008 | Inverter | General Fault Trip | Yes
ALM_INV008_GridConnectionDeratingInverterInternalCauses | INV008_GridConnectionDeratingInverterInternalCauses | INV008 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV008_GridConnectionDeratingPowerRationing | INV008_GridConnectionDeratingPowerRationing | INV008 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV008_GridLoss | INV008_GridLoss | INV008 | Inverter | Grid Loss | Yes
ALM_INV008_GridOverfrequency | INV008_GridOverfrequency | INV008 | Inverter | Grid Overfrequency | Yes
ALM_INV008_GridOvervoltage | INV008_GridOvervoltage | INV008 | Inverter | Grid Overvoltage | Yes
ALM_INV008_GridTiedOffGridControllerAbnormal | INV008_GridTiedOffGridControllerAbnormal | INV008 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV008_GridUnderfrequency | INV008_GridUnderfrequency | INV008 | Inverter | Grid Underfrequency | Yes
ALM_INV008_GridUndervoltage | INV008_GridUndervoltage | INV008 | Inverter | Grid Undervoltage | Yes
ALM_INV008_GroundFault | INV008_GroundFault | INV008 | Inverter | Ground Fault | Yes
ALM_INV008_HighInputStringVoltageGround | INV008_HighInputStringVoltageGround | INV008 | Inverter | High input string voltage to ground | Yes
ALM_INV008_HighStringInputVoltage | INV008_HighStringInputVoltage | INV008 | Inverter | High string input voltage | Yes
ALM_INV008_InverterTripHistoryAvailable | INV008_InverterTripHistoryAvailable | INV008 | Inverter | Inverter Trip History Available | Yes
ALM_INV008_IslandingDetectionStatus | INV008_IslandingDetectionStatus | INV008 | Inverter | Islanding Detection Status | Yes
ALM_INV008_LicenseExpired | INV008_LicenseExpired | INV008 | Inverter | License Expired | Yes
ALM_INV008_LockingStatus | INV008_LockingStatus | INV008 | Inverter | Locking status | Yes
ALM_INV008_LowInsulationResistance | INV008_LowInsulationResistance | INV008 | Inverter | Low Insulation Resistance | Yes
ALM_INV008_OffGridOutputOverload | INV008_OffGridOutputOverload | INV008 | Inverter | Off-grid output overload | Yes
ALM_INV008_OptimizerFault | INV008_OptimizerFault | INV008 | Inverter | Optimizer fault | Yes
ALM_INV008_OutputDCComponentOverhigh | INV008_OutputDCComponentOverhigh | INV008 | Inverter | Output DC Component Overhigh | Yes
ALM_INV008_OutputOvercurrent | INV008_OutputOvercurrent | INV008 | Inverter | Output Overcurrent | Yes
ALM_INV008_PVStringLoss | INV008_PVStringLoss | INV008 | Inverter | PV String Loss | Yes
ALM_INV008_PassiveIslanding | INV008_PassiveIslanding | INV008 | Inverter | Passive Islanding | Yes
ALM_INV008_PeripheralPortShortCircuit | INV008_PeripheralPortShortCircuit | INV008 | Inverter | Peripheral port short circuit | Yes
ALM_INV008_PhaseWireShortCircuitedPE | INV008_PhaseWireShortCircuitedPE | INV008 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV008_PowerLimitationActiveGridCommand | INV008_PowerLimitationActiveGridCommand | INV008 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV008_StringReverseConnection | INV008_StringReverseConnection | INV008 | Inverter | String Reverse Connection | Yes
ALM_INV008_StringReversePolarity | INV008_StringReversePolarity | INV008 | Inverter | String Reverse Polarity | Yes
ALM_INV008_TransientACOvervoltage | INV008_TransientACOvervoltage | INV008 | Inverter | Transient AC Overvoltage | Yes
ALM_INV008_WarningActive | INV008_WarningActive | INV008 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV009_ACOvervoltage | INV009_ACOvervoltage | INV009 | Inverter | AC Overvoltage | Yes
ALM_INV009_ACUndervoltage | INV009_ACUndervoltage | INV009 | Inverter | AC Undervoltage | Yes
ALM_INV009_AFCISelfCheckFailure | INV009_AFCISelfCheckFailure | INV009 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV009_AbnormalGrounding | INV009_AbnormalGrounding | INV009 | Inverter | Abnormal Grounding | Yes
ALM_INV009_AbnormalPVModuleConfiguration | INV009_AbnormalPVModuleConfiguration | INV009 | Inverter | Abnormal PV module configuration | Yes
ALM_INV009_AbnormalResidualCurrent | INV009_AbnormalResidualCurrent | INV009 | Inverter | Abnormal Residual Current | Yes
ALM_INV009_AbnormalStringPower | INV009_AbnormalStringPower | INV009 | Inverter | Abnormal String Power | Yes
ALM_INV009_ActiveIslanding | INV009_ActiveIslanding | INV009 | Inverter | Active Islanding | Yes
ALM_INV009_BuiltPIDOperationAbnormal | INV009_BuiltPIDOperationAbnormal | INV009 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV009_CabinetOvertemperature | INV009_CabinetOvertemperature | INV009 | Inverter | Cabinet Overtemperature | Yes
ALM_INV009_CommunicationFailure | INV009_CommunicationFailure | INV009 | Inverter | Communication Failure | Yes
ALM_INV009_CommunicationStatus | INV009_CommunicationStatus | INV009 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV009_DCArcFault | INV009_DCArcFault | INV009 | Inverter | DC Arc Fault | Yes
ALM_INV009_DCInsulationFault | INV009_DCInsulationFault | INV009 | Inverter | DC Insulation Fault | Yes
ALM_INV009_DCOvervoltage | INV009_DCOvervoltage | INV009 | Inverter | DC Overvoltage | Yes
ALM_INV009_DeviceFault | INV009_DeviceFault | INV009 | Inverter | Device Fault | Yes
ALM_INV009_ExternalFanAbnormal | INV009_ExternalFanAbnormal | INV009 | Inverter | External fan abnormal | Yes
ALM_INV009_FanFailure | INV009_FanFailure | INV009 | Inverter | Fan Failure | Yes
ALM_INV009_Faulty | INV009_Faulty | INV009 | Inverter | Faulty | Yes
ALM_INV009_FaultyMonitoringUnit | INV009_FaultyMonitoringUnit | INV009 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV009_FaultyPowerCollector | INV009_FaultyPowerCollector | INV009 | Inverter | Faulty Power Collector | Yes
ALM_INV009_GeneralFaultTrip | INV009_GeneralFaultTrip | INV009 | Inverter | General Fault Trip | Yes
ALM_INV009_GridConnectionDeratingInverterInternalCauses | INV009_GridConnectionDeratingInverterInternalCauses | INV009 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV009_GridConnectionDeratingPowerRationing | INV009_GridConnectionDeratingPowerRationing | INV009 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV009_GridLoss | INV009_GridLoss | INV009 | Inverter | Grid Loss | Yes
ALM_INV009_GridOverfrequency | INV009_GridOverfrequency | INV009 | Inverter | Grid Overfrequency | Yes
ALM_INV009_GridOvervoltage | INV009_GridOvervoltage | INV009 | Inverter | Grid Overvoltage | Yes
ALM_INV009_GridTiedOffGridControllerAbnormal | INV009_GridTiedOffGridControllerAbnormal | INV009 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV009_GridUnderfrequency | INV009_GridUnderfrequency | INV009 | Inverter | Grid Underfrequency | Yes
ALM_INV009_GridUndervoltage | INV009_GridUndervoltage | INV009 | Inverter | Grid Undervoltage | Yes
ALM_INV009_GroundFault | INV009_GroundFault | INV009 | Inverter | Ground Fault | Yes
ALM_INV009_HighInputStringVoltageGround | INV009_HighInputStringVoltageGround | INV009 | Inverter | High input string voltage to ground | Yes
ALM_INV009_HighStringInputVoltage | INV009_HighStringInputVoltage | INV009 | Inverter | High string input voltage | Yes
ALM_INV009_InverterTripHistoryAvailable | INV009_InverterTripHistoryAvailable | INV009 | Inverter | Inverter Trip History Available | Yes
ALM_INV009_IslandingDetectionStatus | INV009_IslandingDetectionStatus | INV009 | Inverter | Islanding Detection Status | Yes
ALM_INV009_LicenseExpired | INV009_LicenseExpired | INV009 | Inverter | License Expired | Yes
ALM_INV009_LockingStatus | INV009_LockingStatus | INV009 | Inverter | Locking status | Yes
ALM_INV009_LowInsulationResistance | INV009_LowInsulationResistance | INV009 | Inverter | Low Insulation Resistance | Yes
ALM_INV009_OffGridOutputOverload | INV009_OffGridOutputOverload | INV009 | Inverter | Off-grid output overload | Yes
ALM_INV009_OptimizerFault | INV009_OptimizerFault | INV009 | Inverter | Optimizer fault | Yes
ALM_INV009_OutputDCComponentOverhigh | INV009_OutputDCComponentOverhigh | INV009 | Inverter | Output DC Component Overhigh | Yes
ALM_INV009_OutputOvercurrent | INV009_OutputOvercurrent | INV009 | Inverter | Output Overcurrent | Yes
ALM_INV009_PVStringLoss | INV009_PVStringLoss | INV009 | Inverter | PV String Loss | Yes
ALM_INV009_PassiveIslanding | INV009_PassiveIslanding | INV009 | Inverter | Passive Islanding | Yes
ALM_INV009_PeripheralPortShortCircuit | INV009_PeripheralPortShortCircuit | INV009 | Inverter | Peripheral port short circuit | Yes
ALM_INV009_PhaseWireShortCircuitedPE | INV009_PhaseWireShortCircuitedPE | INV009 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV009_PowerLimitationActiveGridCommand | INV009_PowerLimitationActiveGridCommand | INV009 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV009_StringReverseConnection | INV009_StringReverseConnection | INV009 | Inverter | String Reverse Connection | Yes
ALM_INV009_StringReversePolarity | INV009_StringReversePolarity | INV009 | Inverter | String Reverse Polarity | Yes
ALM_INV009_TransientACOvervoltage | INV009_TransientACOvervoltage | INV009 | Inverter | Transient AC Overvoltage | Yes
ALM_INV009_WarningActive | INV009_WarningActive | INV009 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV010_ACOvervoltage | INV010_ACOvervoltage | INV010 | Inverter | AC Overvoltage | Yes
ALM_INV010_ACUndervoltage | INV010_ACUndervoltage | INV010 | Inverter | AC Undervoltage | Yes
ALM_INV010_AFCISelfCheckFailure | INV010_AFCISelfCheckFailure | INV010 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV010_AbnormalGrounding | INV010_AbnormalGrounding | INV010 | Inverter | Abnormal Grounding | Yes
ALM_INV010_AbnormalPVModuleConfiguration | INV010_AbnormalPVModuleConfiguration | INV010 | Inverter | Abnormal PV module configuration | Yes
ALM_INV010_AbnormalResidualCurrent | INV010_AbnormalResidualCurrent | INV010 | Inverter | Abnormal Residual Current | Yes
ALM_INV010_AbnormalStringPower | INV010_AbnormalStringPower | INV010 | Inverter | Abnormal String Power | Yes
ALM_INV010_ActiveIslanding | INV010_ActiveIslanding | INV010 | Inverter | Active Islanding | Yes
ALM_INV010_BuiltPIDOperationAbnormal | INV010_BuiltPIDOperationAbnormal | INV010 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV010_CabinetOvertemperature | INV010_CabinetOvertemperature | INV010 | Inverter | Cabinet Overtemperature | Yes
ALM_INV010_CommunicationFailure | INV010_CommunicationFailure | INV010 | Inverter | Communication Failure | Yes
ALM_INV010_CommunicationStatus | INV010_CommunicationStatus | INV010 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV010_DCArcFault | INV010_DCArcFault | INV010 | Inverter | DC Arc Fault | Yes
ALM_INV010_DCInsulationFault | INV010_DCInsulationFault | INV010 | Inverter | DC Insulation Fault | Yes
ALM_INV010_DCOvervoltage | INV010_DCOvervoltage | INV010 | Inverter | DC Overvoltage | Yes
ALM_INV010_DeviceFault | INV010_DeviceFault | INV010 | Inverter | Device Fault | Yes
ALM_INV010_ExternalFanAbnormal | INV010_ExternalFanAbnormal | INV010 | Inverter | External fan abnormal | Yes
ALM_INV010_FanFailure | INV010_FanFailure | INV010 | Inverter | Fan Failure | Yes
ALM_INV010_Faulty | INV010_Faulty | INV010 | Inverter | Faulty | Yes
ALM_INV010_FaultyMonitoringUnit | INV010_FaultyMonitoringUnit | INV010 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV010_FaultyPowerCollector | INV010_FaultyPowerCollector | INV010 | Inverter | Faulty Power Collector | Yes
ALM_INV010_GeneralFaultTrip | INV010_GeneralFaultTrip | INV010 | Inverter | General Fault Trip | Yes
ALM_INV010_GridConnectionDeratingInverterInternalCauses | INV010_GridConnectionDeratingInverterInternalCauses | INV010 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV010_GridConnectionDeratingPowerRationing | INV010_GridConnectionDeratingPowerRationing | INV010 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV010_GridLoss | INV010_GridLoss | INV010 | Inverter | Grid Loss | Yes
ALM_INV010_GridOverfrequency | INV010_GridOverfrequency | INV010 | Inverter | Grid Overfrequency | Yes
ALM_INV010_GridOvervoltage | INV010_GridOvervoltage | INV010 | Inverter | Grid Overvoltage | Yes
ALM_INV010_GridTiedOffGridControllerAbnormal | INV010_GridTiedOffGridControllerAbnormal | INV010 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV010_GridUnderfrequency | INV010_GridUnderfrequency | INV010 | Inverter | Grid Underfrequency | Yes
ALM_INV010_GridUndervoltage | INV010_GridUndervoltage | INV010 | Inverter | Grid Undervoltage | Yes
ALM_INV010_GroundFault | INV010_GroundFault | INV010 | Inverter | Ground Fault | Yes
ALM_INV010_HighInputStringVoltageGround | INV010_HighInputStringVoltageGround | INV010 | Inverter | High input string voltage to ground | Yes
ALM_INV010_HighStringInputVoltage | INV010_HighStringInputVoltage | INV010 | Inverter | High string input voltage | Yes
ALM_INV010_InverterTripHistoryAvailable | INV010_InverterTripHistoryAvailable | INV010 | Inverter | Inverter Trip History Available | Yes
ALM_INV010_IslandingDetectionStatus | INV010_IslandingDetectionStatus | INV010 | Inverter | Islanding Detection Status | Yes
ALM_INV010_LicenseExpired | INV010_LicenseExpired | INV010 | Inverter | License Expired | Yes
ALM_INV010_LockingStatus | INV010_LockingStatus | INV010 | Inverter | Locking status | Yes
ALM_INV010_LowInsulationResistance | INV010_LowInsulationResistance | INV010 | Inverter | Low Insulation Resistance | Yes
ALM_INV010_OffGridOutputOverload | INV010_OffGridOutputOverload | INV010 | Inverter | Off-grid output overload | Yes
ALM_INV010_OptimizerFault | INV010_OptimizerFault | INV010 | Inverter | Optimizer fault | Yes
ALM_INV010_OutputDCComponentOverhigh | INV010_OutputDCComponentOverhigh | INV010 | Inverter | Output DC Component Overhigh | Yes
ALM_INV010_OutputOvercurrent | INV010_OutputOvercurrent | INV010 | Inverter | Output Overcurrent | Yes
ALM_INV010_PVStringLoss | INV010_PVStringLoss | INV010 | Inverter | PV String Loss | Yes
ALM_INV010_PassiveIslanding | INV010_PassiveIslanding | INV010 | Inverter | Passive Islanding | Yes
ALM_INV010_PeripheralPortShortCircuit | INV010_PeripheralPortShortCircuit | INV010 | Inverter | Peripheral port short circuit | Yes
ALM_INV010_PhaseWireShortCircuitedPE | INV010_PhaseWireShortCircuitedPE | INV010 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV010_PowerLimitationActiveGridCommand | INV010_PowerLimitationActiveGridCommand | INV010 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV010_StringReverseConnection | INV010_StringReverseConnection | INV010 | Inverter | String Reverse Connection | Yes
ALM_INV010_StringReversePolarity | INV010_StringReversePolarity | INV010 | Inverter | String Reverse Polarity | Yes
ALM_INV010_TransientACOvervoltage | INV010_TransientACOvervoltage | INV010 | Inverter | Transient AC Overvoltage | Yes
ALM_INV010_WarningActive | INV010_WarningActive | INV010 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV011_ACOvervoltage | INV011_ACOvervoltage | INV011 | Inverter | AC Overvoltage | Yes
ALM_INV011_ACUndervoltage | INV011_ACUndervoltage | INV011 | Inverter | AC Undervoltage | Yes
ALM_INV011_AFCISelfCheckFailure | INV011_AFCISelfCheckFailure | INV011 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV011_AbnormalGrounding | INV011_AbnormalGrounding | INV011 | Inverter | Abnormal Grounding | Yes
ALM_INV011_AbnormalPVModuleConfiguration | INV011_AbnormalPVModuleConfiguration | INV011 | Inverter | Abnormal PV module configuration | Yes
ALM_INV011_AbnormalResidualCurrent | INV011_AbnormalResidualCurrent | INV011 | Inverter | Abnormal Residual Current | Yes
ALM_INV011_AbnormalStringPower | INV011_AbnormalStringPower | INV011 | Inverter | Abnormal String Power | Yes
ALM_INV011_ActiveIslanding | INV011_ActiveIslanding | INV011 | Inverter | Active Islanding | Yes
ALM_INV011_BuiltPIDOperationAbnormal | INV011_BuiltPIDOperationAbnormal | INV011 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV011_CabinetOvertemperature | INV011_CabinetOvertemperature | INV011 | Inverter | Cabinet Overtemperature | Yes
ALM_INV011_CommunicationFailure | INV011_CommunicationFailure | INV011 | Inverter | Communication Failure | Yes
ALM_INV011_CommunicationStatus | INV011_CommunicationStatus | INV011 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV011_DCArcFault | INV011_DCArcFault | INV011 | Inverter | DC Arc Fault | Yes
ALM_INV011_DCInsulationFault | INV011_DCInsulationFault | INV011 | Inverter | DC Insulation Fault | Yes
ALM_INV011_DCOvervoltage | INV011_DCOvervoltage | INV011 | Inverter | DC Overvoltage | Yes
ALM_INV011_DeviceFault | INV011_DeviceFault | INV011 | Inverter | Device Fault | Yes
ALM_INV011_ExternalFanAbnormal | INV011_ExternalFanAbnormal | INV011 | Inverter | External fan abnormal | Yes
ALM_INV011_FanFailure | INV011_FanFailure | INV011 | Inverter | Fan Failure | Yes
ALM_INV011_Faulty | INV011_Faulty | INV011 | Inverter | Faulty | Yes
ALM_INV011_FaultyMonitoringUnit | INV011_FaultyMonitoringUnit | INV011 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV011_FaultyPowerCollector | INV011_FaultyPowerCollector | INV011 | Inverter | Faulty Power Collector | Yes
ALM_INV011_GeneralFaultTrip | INV011_GeneralFaultTrip | INV011 | Inverter | General Fault Trip | Yes
ALM_INV011_GridConnectionDeratingInverterInternalCauses | INV011_GridConnectionDeratingInverterInternalCauses | INV011 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV011_GridConnectionDeratingPowerRationing | INV011_GridConnectionDeratingPowerRationing | INV011 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV011_GridLoss | INV011_GridLoss | INV011 | Inverter | Grid Loss | Yes
ALM_INV011_GridOverfrequency | INV011_GridOverfrequency | INV011 | Inverter | Grid Overfrequency | Yes
ALM_INV011_GridOvervoltage | INV011_GridOvervoltage | INV011 | Inverter | Grid Overvoltage | Yes
ALM_INV011_GridTiedOffGridControllerAbnormal | INV011_GridTiedOffGridControllerAbnormal | INV011 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV011_GridUnderfrequency | INV011_GridUnderfrequency | INV011 | Inverter | Grid Underfrequency | Yes
ALM_INV011_GridUndervoltage | INV011_GridUndervoltage | INV011 | Inverter | Grid Undervoltage | Yes
ALM_INV011_GroundFault | INV011_GroundFault | INV011 | Inverter | Ground Fault | Yes
ALM_INV011_HighInputStringVoltageGround | INV011_HighInputStringVoltageGround | INV011 | Inverter | High input string voltage to ground | Yes
ALM_INV011_HighStringInputVoltage | INV011_HighStringInputVoltage | INV011 | Inverter | High string input voltage | Yes
ALM_INV011_InverterTripHistoryAvailable | INV011_InverterTripHistoryAvailable | INV011 | Inverter | Inverter Trip History Available | Yes
ALM_INV011_IslandingDetectionStatus | INV011_IslandingDetectionStatus | INV011 | Inverter | Islanding Detection Status | Yes
ALM_INV011_LicenseExpired | INV011_LicenseExpired | INV011 | Inverter | License Expired | Yes
ALM_INV011_LockingStatus | INV011_LockingStatus | INV011 | Inverter | Locking status | Yes
ALM_INV011_LowInsulationResistance | INV011_LowInsulationResistance | INV011 | Inverter | Low Insulation Resistance | Yes
ALM_INV011_OffGridOutputOverload | INV011_OffGridOutputOverload | INV011 | Inverter | Off-grid output overload | Yes
ALM_INV011_OptimizerFault | INV011_OptimizerFault | INV011 | Inverter | Optimizer fault | Yes
ALM_INV011_OutputDCComponentOverhigh | INV011_OutputDCComponentOverhigh | INV011 | Inverter | Output DC Component Overhigh | Yes
ALM_INV011_OutputOvercurrent | INV011_OutputOvercurrent | INV011 | Inverter | Output Overcurrent | Yes
ALM_INV011_PVStringLoss | INV011_PVStringLoss | INV011 | Inverter | PV String Loss | Yes
ALM_INV011_PassiveIslanding | INV011_PassiveIslanding | INV011 | Inverter | Passive Islanding | Yes
ALM_INV011_PeripheralPortShortCircuit | INV011_PeripheralPortShortCircuit | INV011 | Inverter | Peripheral port short circuit | Yes
ALM_INV011_PhaseWireShortCircuitedPE | INV011_PhaseWireShortCircuitedPE | INV011 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV011_PowerLimitationActiveGridCommand | INV011_PowerLimitationActiveGridCommand | INV011 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV011_StringReverseConnection | INV011_StringReverseConnection | INV011 | Inverter | String Reverse Connection | Yes
ALM_INV011_StringReversePolarity | INV011_StringReversePolarity | INV011 | Inverter | String Reverse Polarity | Yes
ALM_INV011_TransientACOvervoltage | INV011_TransientACOvervoltage | INV011 | Inverter | Transient AC Overvoltage | Yes
ALM_INV011_WarningActive | INV011_WarningActive | INV011 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV012_ACOvervoltage | INV012_ACOvervoltage | INV012 | Inverter | AC Overvoltage | Yes
ALM_INV012_ACUndervoltage | INV012_ACUndervoltage | INV012 | Inverter | AC Undervoltage | Yes
ALM_INV012_AFCISelfCheckFailure | INV012_AFCISelfCheckFailure | INV012 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV012_AbnormalGrounding | INV012_AbnormalGrounding | INV012 | Inverter | Abnormal Grounding | Yes
ALM_INV012_AbnormalPVModuleConfiguration | INV012_AbnormalPVModuleConfiguration | INV012 | Inverter | Abnormal PV module configuration | Yes
ALM_INV012_AbnormalResidualCurrent | INV012_AbnormalResidualCurrent | INV012 | Inverter | Abnormal Residual Current | Yes
ALM_INV012_AbnormalStringPower | INV012_AbnormalStringPower | INV012 | Inverter | Abnormal String Power | Yes
ALM_INV012_ActiveIslanding | INV012_ActiveIslanding | INV012 | Inverter | Active Islanding | Yes
ALM_INV012_BuiltPIDOperationAbnormal | INV012_BuiltPIDOperationAbnormal | INV012 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV012_CabinetOvertemperature | INV012_CabinetOvertemperature | INV012 | Inverter | Cabinet Overtemperature | Yes
ALM_INV012_CommunicationFailure | INV012_CommunicationFailure | INV012 | Inverter | Communication Failure | Yes
ALM_INV012_CommunicationStatus | INV012_CommunicationStatus | INV012 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV012_DCArcFault | INV012_DCArcFault | INV012 | Inverter | DC Arc Fault | Yes
ALM_INV012_DCInsulationFault | INV012_DCInsulationFault | INV012 | Inverter | DC Insulation Fault | Yes
ALM_INV012_DCOvervoltage | INV012_DCOvervoltage | INV012 | Inverter | DC Overvoltage | Yes
ALM_INV012_DeviceFault | INV012_DeviceFault | INV012 | Inverter | Device Fault | Yes
ALM_INV012_ExternalFanAbnormal | INV012_ExternalFanAbnormal | INV012 | Inverter | External fan abnormal | Yes
ALM_INV012_FanFailure | INV012_FanFailure | INV012 | Inverter | Fan Failure | Yes
ALM_INV012_Faulty | INV012_Faulty | INV012 | Inverter | Faulty | Yes
ALM_INV012_FaultyMonitoringUnit | INV012_FaultyMonitoringUnit | INV012 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV012_FaultyPowerCollector | INV012_FaultyPowerCollector | INV012 | Inverter | Faulty Power Collector | Yes
ALM_INV012_GeneralFaultTrip | INV012_GeneralFaultTrip | INV012 | Inverter | General Fault Trip | Yes
ALM_INV012_GridConnectionDeratingInverterInternalCauses | INV012_GridConnectionDeratingInverterInternalCauses | INV012 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV012_GridConnectionDeratingPowerRationing | INV012_GridConnectionDeratingPowerRationing | INV012 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV012_GridLoss | INV012_GridLoss | INV012 | Inverter | Grid Loss | Yes
ALM_INV012_GridOverfrequency | INV012_GridOverfrequency | INV012 | Inverter | Grid Overfrequency | Yes
ALM_INV012_GridOvervoltage | INV012_GridOvervoltage | INV012 | Inverter | Grid Overvoltage | Yes
ALM_INV012_GridTiedOffGridControllerAbnormal | INV012_GridTiedOffGridControllerAbnormal | INV012 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV012_GridUnderfrequency | INV012_GridUnderfrequency | INV012 | Inverter | Grid Underfrequency | Yes
ALM_INV012_GridUndervoltage | INV012_GridUndervoltage | INV012 | Inverter | Grid Undervoltage | Yes
ALM_INV012_GroundFault | INV012_GroundFault | INV012 | Inverter | Ground Fault | Yes
ALM_INV012_HighInputStringVoltageGround | INV012_HighInputStringVoltageGround | INV012 | Inverter | High input string voltage to ground | Yes
ALM_INV012_HighStringInputVoltage | INV012_HighStringInputVoltage | INV012 | Inverter | High string input voltage | Yes
ALM_INV012_InverterTripHistoryAvailable | INV012_InverterTripHistoryAvailable | INV012 | Inverter | Inverter Trip History Available | Yes
ALM_INV012_IslandingDetectionStatus | INV012_IslandingDetectionStatus | INV012 | Inverter | Islanding Detection Status | Yes
ALM_INV012_LicenseExpired | INV012_LicenseExpired | INV012 | Inverter | License Expired | Yes
ALM_INV012_LockingStatus | INV012_LockingStatus | INV012 | Inverter | Locking status | Yes
ALM_INV012_LowInsulationResistance | INV012_LowInsulationResistance | INV012 | Inverter | Low Insulation Resistance | Yes
ALM_INV012_OffGridOutputOverload | INV012_OffGridOutputOverload | INV012 | Inverter | Off-grid output overload | Yes
ALM_INV012_OptimizerFault | INV012_OptimizerFault | INV012 | Inverter | Optimizer fault | Yes
ALM_INV012_OutputDCComponentOverhigh | INV012_OutputDCComponentOverhigh | INV012 | Inverter | Output DC Component Overhigh | Yes
ALM_INV012_OutputOvercurrent | INV012_OutputOvercurrent | INV012 | Inverter | Output Overcurrent | Yes
ALM_INV012_PVStringLoss | INV012_PVStringLoss | INV012 | Inverter | PV String Loss | Yes
ALM_INV012_PassiveIslanding | INV012_PassiveIslanding | INV012 | Inverter | Passive Islanding | Yes
ALM_INV012_PeripheralPortShortCircuit | INV012_PeripheralPortShortCircuit | INV012 | Inverter | Peripheral port short circuit | Yes
ALM_INV012_PhaseWireShortCircuitedPE | INV012_PhaseWireShortCircuitedPE | INV012 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV012_PowerLimitationActiveGridCommand | INV012_PowerLimitationActiveGridCommand | INV012 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV012_StringReverseConnection | INV012_StringReverseConnection | INV012 | Inverter | String Reverse Connection | Yes
ALM_INV012_StringReversePolarity | INV012_StringReversePolarity | INV012 | Inverter | String Reverse Polarity | Yes
ALM_INV012_TransientACOvervoltage | INV012_TransientACOvervoltage | INV012 | Inverter | Transient AC Overvoltage | Yes
ALM_INV012_WarningActive | INV012_WarningActive | INV012 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV013_ACOvervoltage | INV013_ACOvervoltage | INV013 | Inverter | AC Overvoltage | Yes
ALM_INV013_ACUndervoltage | INV013_ACUndervoltage | INV013 | Inverter | AC Undervoltage | Yes
ALM_INV013_AFCISelfCheckFailure | INV013_AFCISelfCheckFailure | INV013 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV013_AbnormalGrounding | INV013_AbnormalGrounding | INV013 | Inverter | Abnormal Grounding | Yes
ALM_INV013_AbnormalPVModuleConfiguration | INV013_AbnormalPVModuleConfiguration | INV013 | Inverter | Abnormal PV module configuration | Yes
ALM_INV013_AbnormalResidualCurrent | INV013_AbnormalResidualCurrent | INV013 | Inverter | Abnormal Residual Current | Yes
ALM_INV013_AbnormalStringPower | INV013_AbnormalStringPower | INV013 | Inverter | Abnormal String Power | Yes
ALM_INV013_ActiveIslanding | INV013_ActiveIslanding | INV013 | Inverter | Active Islanding | Yes
ALM_INV013_BuiltPIDOperationAbnormal | INV013_BuiltPIDOperationAbnormal | INV013 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV013_CabinetOvertemperature | INV013_CabinetOvertemperature | INV013 | Inverter | Cabinet Overtemperature | Yes
ALM_INV013_CommunicationFailure | INV013_CommunicationFailure | INV013 | Inverter | Communication Failure | Yes
ALM_INV013_CommunicationStatus | INV013_CommunicationStatus | INV013 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV013_DCArcFault | INV013_DCArcFault | INV013 | Inverter | DC Arc Fault | Yes
ALM_INV013_DCInsulationFault | INV013_DCInsulationFault | INV013 | Inverter | DC Insulation Fault | Yes
ALM_INV013_DCOvervoltage | INV013_DCOvervoltage | INV013 | Inverter | DC Overvoltage | Yes
ALM_INV013_DeviceFault | INV013_DeviceFault | INV013 | Inverter | Device Fault | Yes
ALM_INV013_ExternalFanAbnormal | INV013_ExternalFanAbnormal | INV013 | Inverter | External fan abnormal | Yes
ALM_INV013_FanFailure | INV013_FanFailure | INV013 | Inverter | Fan Failure | Yes
ALM_INV013_Faulty | INV013_Faulty | INV013 | Inverter | Faulty | Yes
ALM_INV013_FaultyMonitoringUnit | INV013_FaultyMonitoringUnit | INV013 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV013_FaultyPowerCollector | INV013_FaultyPowerCollector | INV013 | Inverter | Faulty Power Collector | Yes
ALM_INV013_GeneralFaultTrip | INV013_GeneralFaultTrip | INV013 | Inverter | General Fault Trip | Yes
ALM_INV013_GridConnectionDeratingInverterInternalCauses | INV013_GridConnectionDeratingInverterInternalCauses | INV013 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV013_GridConnectionDeratingPowerRationing | INV013_GridConnectionDeratingPowerRationing | INV013 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV013_GridLoss | INV013_GridLoss | INV013 | Inverter | Grid Loss | Yes
ALM_INV013_GridOverfrequency | INV013_GridOverfrequency | INV013 | Inverter | Grid Overfrequency | Yes
ALM_INV013_GridOvervoltage | INV013_GridOvervoltage | INV013 | Inverter | Grid Overvoltage | Yes
ALM_INV013_GridTiedOffGridControllerAbnormal | INV013_GridTiedOffGridControllerAbnormal | INV013 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV013_GridUnderfrequency | INV013_GridUnderfrequency | INV013 | Inverter | Grid Underfrequency | Yes
ALM_INV013_GridUndervoltage | INV013_GridUndervoltage | INV013 | Inverter | Grid Undervoltage | Yes
ALM_INV013_GroundFault | INV013_GroundFault | INV013 | Inverter | Ground Fault | Yes
ALM_INV013_HighInputStringVoltageGround | INV013_HighInputStringVoltageGround | INV013 | Inverter | High input string voltage to ground | Yes
ALM_INV013_HighStringInputVoltage | INV013_HighStringInputVoltage | INV013 | Inverter | High string input voltage | Yes
ALM_INV013_InverterTripHistoryAvailable | INV013_InverterTripHistoryAvailable | INV013 | Inverter | Inverter Trip History Available | Yes
ALM_INV013_IslandingDetectionStatus | INV013_IslandingDetectionStatus | INV013 | Inverter | Islanding Detection Status | Yes
ALM_INV013_LicenseExpired | INV013_LicenseExpired | INV013 | Inverter | License Expired | Yes
ALM_INV013_LockingStatus | INV013_LockingStatus | INV013 | Inverter | Locking status | Yes
ALM_INV013_LowInsulationResistance | INV013_LowInsulationResistance | INV013 | Inverter | Low Insulation Resistance | Yes
ALM_INV013_OffGridOutputOverload | INV013_OffGridOutputOverload | INV013 | Inverter | Off-grid output overload | Yes
ALM_INV013_OptimizerFault | INV013_OptimizerFault | INV013 | Inverter | Optimizer fault | Yes
ALM_INV013_OutputDCComponentOverhigh | INV013_OutputDCComponentOverhigh | INV013 | Inverter | Output DC Component Overhigh | Yes
ALM_INV013_OutputOvercurrent | INV013_OutputOvercurrent | INV013 | Inverter | Output Overcurrent | Yes
ALM_INV013_PVStringLoss | INV013_PVStringLoss | INV013 | Inverter | PV String Loss | Yes
ALM_INV013_PassiveIslanding | INV013_PassiveIslanding | INV013 | Inverter | Passive Islanding | Yes
ALM_INV013_PeripheralPortShortCircuit | INV013_PeripheralPortShortCircuit | INV013 | Inverter | Peripheral port short circuit | Yes
ALM_INV013_PhaseWireShortCircuitedPE | INV013_PhaseWireShortCircuitedPE | INV013 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV013_PowerLimitationActiveGridCommand | INV013_PowerLimitationActiveGridCommand | INV013 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV013_StringReverseConnection | INV013_StringReverseConnection | INV013 | Inverter | String Reverse Connection | Yes
ALM_INV013_StringReversePolarity | INV013_StringReversePolarity | INV013 | Inverter | String Reverse Polarity | Yes
ALM_INV013_TransientACOvervoltage | INV013_TransientACOvervoltage | INV013 | Inverter | Transient AC Overvoltage | Yes
ALM_INV013_WarningActive | INV013_WarningActive | INV013 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV014_ACOvervoltage | INV014_ACOvervoltage | INV014 | Inverter | AC Overvoltage | Yes
ALM_INV014_ACUndervoltage | INV014_ACUndervoltage | INV014 | Inverter | AC Undervoltage | Yes
ALM_INV014_AFCISelfCheckFailure | INV014_AFCISelfCheckFailure | INV014 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV014_AbnormalGrounding | INV014_AbnormalGrounding | INV014 | Inverter | Abnormal Grounding | Yes
ALM_INV014_AbnormalPVModuleConfiguration | INV014_AbnormalPVModuleConfiguration | INV014 | Inverter | Abnormal PV module configuration | Yes
ALM_INV014_AbnormalResidualCurrent | INV014_AbnormalResidualCurrent | INV014 | Inverter | Abnormal Residual Current | Yes
ALM_INV014_AbnormalStringPower | INV014_AbnormalStringPower | INV014 | Inverter | Abnormal String Power | Yes
ALM_INV014_ActiveIslanding | INV014_ActiveIslanding | INV014 | Inverter | Active Islanding | Yes
ALM_INV014_BuiltPIDOperationAbnormal | INV014_BuiltPIDOperationAbnormal | INV014 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV014_CabinetOvertemperature | INV014_CabinetOvertemperature | INV014 | Inverter | Cabinet Overtemperature | Yes
ALM_INV014_CommunicationFailure | INV014_CommunicationFailure | INV014 | Inverter | Communication Failure | Yes
ALM_INV014_CommunicationStatus | INV014_CommunicationStatus | INV014 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV014_DCArcFault | INV014_DCArcFault | INV014 | Inverter | DC Arc Fault | Yes
ALM_INV014_DCInsulationFault | INV014_DCInsulationFault | INV014 | Inverter | DC Insulation Fault | Yes
ALM_INV014_DCOvervoltage | INV014_DCOvervoltage | INV014 | Inverter | DC Overvoltage | Yes
ALM_INV014_DeviceFault | INV014_DeviceFault | INV014 | Inverter | Device Fault | Yes
ALM_INV014_ExternalFanAbnormal | INV014_ExternalFanAbnormal | INV014 | Inverter | External fan abnormal | Yes
ALM_INV014_FanFailure | INV014_FanFailure | INV014 | Inverter | Fan Failure | Yes
ALM_INV014_Faulty | INV014_Faulty | INV014 | Inverter | Faulty | Yes
ALM_INV014_FaultyMonitoringUnit | INV014_FaultyMonitoringUnit | INV014 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV014_FaultyPowerCollector | INV014_FaultyPowerCollector | INV014 | Inverter | Faulty Power Collector | Yes
ALM_INV014_GeneralFaultTrip | INV014_GeneralFaultTrip | INV014 | Inverter | General Fault Trip | Yes
ALM_INV014_GridConnectionDeratingInverterInternalCauses | INV014_GridConnectionDeratingInverterInternalCauses | INV014 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV014_GridConnectionDeratingPowerRationing | INV014_GridConnectionDeratingPowerRationing | INV014 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV014_GridLoss | INV014_GridLoss | INV014 | Inverter | Grid Loss | Yes
ALM_INV014_GridOverfrequency | INV014_GridOverfrequency | INV014 | Inverter | Grid Overfrequency | Yes
ALM_INV014_GridOvervoltage | INV014_GridOvervoltage | INV014 | Inverter | Grid Overvoltage | Yes
ALM_INV014_GridTiedOffGridControllerAbnormal | INV014_GridTiedOffGridControllerAbnormal | INV014 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV014_GridUnderfrequency | INV014_GridUnderfrequency | INV014 | Inverter | Grid Underfrequency | Yes
ALM_INV014_GridUndervoltage | INV014_GridUndervoltage | INV014 | Inverter | Grid Undervoltage | Yes
ALM_INV014_GroundFault | INV014_GroundFault | INV014 | Inverter | Ground Fault | Yes
ALM_INV014_HighInputStringVoltageGround | INV014_HighInputStringVoltageGround | INV014 | Inverter | High input string voltage to ground | Yes
ALM_INV014_HighStringInputVoltage | INV014_HighStringInputVoltage | INV014 | Inverter | High string input voltage | Yes
ALM_INV014_InverterTripHistoryAvailable | INV014_InverterTripHistoryAvailable | INV014 | Inverter | Inverter Trip History Available | Yes
ALM_INV014_IslandingDetectionStatus | INV014_IslandingDetectionStatus | INV014 | Inverter | Islanding Detection Status | Yes
ALM_INV014_LicenseExpired | INV014_LicenseExpired | INV014 | Inverter | License Expired | Yes
ALM_INV014_LockingStatus | INV014_LockingStatus | INV014 | Inverter | Locking status | Yes
ALM_INV014_LowInsulationResistance | INV014_LowInsulationResistance | INV014 | Inverter | Low Insulation Resistance | Yes
ALM_INV014_OffGridOutputOverload | INV014_OffGridOutputOverload | INV014 | Inverter | Off-grid output overload | Yes
ALM_INV014_OptimizerFault | INV014_OptimizerFault | INV014 | Inverter | Optimizer fault | Yes
ALM_INV014_OutputDCComponentOverhigh | INV014_OutputDCComponentOverhigh | INV014 | Inverter | Output DC Component Overhigh | Yes
ALM_INV014_OutputOvercurrent | INV014_OutputOvercurrent | INV014 | Inverter | Output Overcurrent | Yes
ALM_INV014_PVStringLoss | INV014_PVStringLoss | INV014 | Inverter | PV String Loss | Yes
ALM_INV014_PassiveIslanding | INV014_PassiveIslanding | INV014 | Inverter | Passive Islanding | Yes
ALM_INV014_PeripheralPortShortCircuit | INV014_PeripheralPortShortCircuit | INV014 | Inverter | Peripheral port short circuit | Yes
ALM_INV014_PhaseWireShortCircuitedPE | INV014_PhaseWireShortCircuitedPE | INV014 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV014_PowerLimitationActiveGridCommand | INV014_PowerLimitationActiveGridCommand | INV014 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV014_StringReverseConnection | INV014_StringReverseConnection | INV014 | Inverter | String Reverse Connection | Yes
ALM_INV014_StringReversePolarity | INV014_StringReversePolarity | INV014 | Inverter | String Reverse Polarity | Yes
ALM_INV014_TransientACOvervoltage | INV014_TransientACOvervoltage | INV014 | Inverter | Transient AC Overvoltage | Yes
ALM_INV014_WarningActive | INV014_WarningActive | INV014 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV015_ACOvervoltage | INV015_ACOvervoltage | INV015 | Inverter | AC Overvoltage | Yes
ALM_INV015_ACUndervoltage | INV015_ACUndervoltage | INV015 | Inverter | AC Undervoltage | Yes
ALM_INV015_AFCISelfCheckFailure | INV015_AFCISelfCheckFailure | INV015 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV015_AbnormalGrounding | INV015_AbnormalGrounding | INV015 | Inverter | Abnormal Grounding | Yes
ALM_INV015_AbnormalPVModuleConfiguration | INV015_AbnormalPVModuleConfiguration | INV015 | Inverter | Abnormal PV module configuration | Yes
ALM_INV015_AbnormalResidualCurrent | INV015_AbnormalResidualCurrent | INV015 | Inverter | Abnormal Residual Current | Yes
ALM_INV015_AbnormalStringPower | INV015_AbnormalStringPower | INV015 | Inverter | Abnormal String Power | Yes
ALM_INV015_ActiveIslanding | INV015_ActiveIslanding | INV015 | Inverter | Active Islanding | Yes
ALM_INV015_BuiltPIDOperationAbnormal | INV015_BuiltPIDOperationAbnormal | INV015 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV015_CabinetOvertemperature | INV015_CabinetOvertemperature | INV015 | Inverter | Cabinet Overtemperature | Yes
ALM_INV015_CommunicationFailure | INV015_CommunicationFailure | INV015 | Inverter | Communication Failure | Yes
ALM_INV015_CommunicationStatus | INV015_CommunicationStatus | INV015 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV015_DCArcFault | INV015_DCArcFault | INV015 | Inverter | DC Arc Fault | Yes
ALM_INV015_DCInsulationFault | INV015_DCInsulationFault | INV015 | Inverter | DC Insulation Fault | Yes
ALM_INV015_DCOvervoltage | INV015_DCOvervoltage | INV015 | Inverter | DC Overvoltage | Yes
ALM_INV015_DeviceFault | INV015_DeviceFault | INV015 | Inverter | Device Fault | Yes
ALM_INV015_ExternalFanAbnormal | INV015_ExternalFanAbnormal | INV015 | Inverter | External fan abnormal | Yes
ALM_INV015_FanFailure | INV015_FanFailure | INV015 | Inverter | Fan Failure | Yes
ALM_INV015_Faulty | INV015_Faulty | INV015 | Inverter | Faulty | Yes
ALM_INV015_FaultyMonitoringUnit | INV015_FaultyMonitoringUnit | INV015 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV015_FaultyPowerCollector | INV015_FaultyPowerCollector | INV015 | Inverter | Faulty Power Collector | Yes
ALM_INV015_GeneralFaultTrip | INV015_GeneralFaultTrip | INV015 | Inverter | General Fault Trip | Yes
ALM_INV015_GridConnectionDeratingInverterInternalCauses | INV015_GridConnectionDeratingInverterInternalCauses | INV015 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV015_GridConnectionDeratingPowerRationing | INV015_GridConnectionDeratingPowerRationing | INV015 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV015_GridLoss | INV015_GridLoss | INV015 | Inverter | Grid Loss | Yes
ALM_INV015_GridOverfrequency | INV015_GridOverfrequency | INV015 | Inverter | Grid Overfrequency | Yes
ALM_INV015_GridOvervoltage | INV015_GridOvervoltage | INV015 | Inverter | Grid Overvoltage | Yes
ALM_INV015_GridTiedOffGridControllerAbnormal | INV015_GridTiedOffGridControllerAbnormal | INV015 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV015_GridUnderfrequency | INV015_GridUnderfrequency | INV015 | Inverter | Grid Underfrequency | Yes
ALM_INV015_GridUndervoltage | INV015_GridUndervoltage | INV015 | Inverter | Grid Undervoltage | Yes
ALM_INV015_GroundFault | INV015_GroundFault | INV015 | Inverter | Ground Fault | Yes
ALM_INV015_HighInputStringVoltageGround | INV015_HighInputStringVoltageGround | INV015 | Inverter | High input string voltage to ground | Yes
ALM_INV015_HighStringInputVoltage | INV015_HighStringInputVoltage | INV015 | Inverter | High string input voltage | Yes
ALM_INV015_InverterTripHistoryAvailable | INV015_InverterTripHistoryAvailable | INV015 | Inverter | Inverter Trip History Available | Yes
ALM_INV015_IslandingDetectionStatus | INV015_IslandingDetectionStatus | INV015 | Inverter | Islanding Detection Status | Yes
ALM_INV015_LicenseExpired | INV015_LicenseExpired | INV015 | Inverter | License Expired | Yes
ALM_INV015_LockingStatus | INV015_LockingStatus | INV015 | Inverter | Locking status | Yes
ALM_INV015_LowInsulationResistance | INV015_LowInsulationResistance | INV015 | Inverter | Low Insulation Resistance | Yes
ALM_INV015_OffGridOutputOverload | INV015_OffGridOutputOverload | INV015 | Inverter | Off-grid output overload | Yes
ALM_INV015_OptimizerFault | INV015_OptimizerFault | INV015 | Inverter | Optimizer fault | Yes
ALM_INV015_OutputDCComponentOverhigh | INV015_OutputDCComponentOverhigh | INV015 | Inverter | Output DC Component Overhigh | Yes
ALM_INV015_OutputOvercurrent | INV015_OutputOvercurrent | INV015 | Inverter | Output Overcurrent | Yes
ALM_INV015_PVStringLoss | INV015_PVStringLoss | INV015 | Inverter | PV String Loss | Yes
ALM_INV015_PassiveIslanding | INV015_PassiveIslanding | INV015 | Inverter | Passive Islanding | Yes
ALM_INV015_PeripheralPortShortCircuit | INV015_PeripheralPortShortCircuit | INV015 | Inverter | Peripheral port short circuit | Yes
ALM_INV015_PhaseWireShortCircuitedPE | INV015_PhaseWireShortCircuitedPE | INV015 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV015_PowerLimitationActiveGridCommand | INV015_PowerLimitationActiveGridCommand | INV015 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV015_StringReverseConnection | INV015_StringReverseConnection | INV015 | Inverter | String Reverse Connection | Yes
ALM_INV015_StringReversePolarity | INV015_StringReversePolarity | INV015 | Inverter | String Reverse Polarity | Yes
ALM_INV015_TransientACOvervoltage | INV015_TransientACOvervoltage | INV015 | Inverter | Transient AC Overvoltage | Yes
ALM_INV015_WarningActive | INV015_WarningActive | INV015 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV016_ACOvervoltage | INV016_ACOvervoltage | INV016 | Inverter | AC Overvoltage | Yes
ALM_INV016_ACUndervoltage | INV016_ACUndervoltage | INV016 | Inverter | AC Undervoltage | Yes
ALM_INV016_AFCISelfCheckFailure | INV016_AFCISelfCheckFailure | INV016 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV016_AbnormalGrounding | INV016_AbnormalGrounding | INV016 | Inverter | Abnormal Grounding | Yes
ALM_INV016_AbnormalPVModuleConfiguration | INV016_AbnormalPVModuleConfiguration | INV016 | Inverter | Abnormal PV module configuration | Yes
ALM_INV016_AbnormalResidualCurrent | INV016_AbnormalResidualCurrent | INV016 | Inverter | Abnormal Residual Current | Yes
ALM_INV016_AbnormalStringPower | INV016_AbnormalStringPower | INV016 | Inverter | Abnormal String Power | Yes
ALM_INV016_ActiveIslanding | INV016_ActiveIslanding | INV016 | Inverter | Active Islanding | Yes
ALM_INV016_BuiltPIDOperationAbnormal | INV016_BuiltPIDOperationAbnormal | INV016 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV016_CabinetOvertemperature | INV016_CabinetOvertemperature | INV016 | Inverter | Cabinet Overtemperature | Yes
ALM_INV016_CommunicationFailure | INV016_CommunicationFailure | INV016 | Inverter | Communication Failure | Yes
ALM_INV016_CommunicationStatus | INV016_CommunicationStatus | INV016 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV016_DCArcFault | INV016_DCArcFault | INV016 | Inverter | DC Arc Fault | Yes
ALM_INV016_DCInsulationFault | INV016_DCInsulationFault | INV016 | Inverter | DC Insulation Fault | Yes
ALM_INV016_DCOvervoltage | INV016_DCOvervoltage | INV016 | Inverter | DC Overvoltage | Yes
ALM_INV016_DeviceFault | INV016_DeviceFault | INV016 | Inverter | Device Fault | Yes
ALM_INV016_ExternalFanAbnormal | INV016_ExternalFanAbnormal | INV016 | Inverter | External fan abnormal | Yes
ALM_INV016_FanFailure | INV016_FanFailure | INV016 | Inverter | Fan Failure | Yes
ALM_INV016_Faulty | INV016_Faulty | INV016 | Inverter | Faulty | Yes
ALM_INV016_FaultyMonitoringUnit | INV016_FaultyMonitoringUnit | INV016 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV016_FaultyPowerCollector | INV016_FaultyPowerCollector | INV016 | Inverter | Faulty Power Collector | Yes
ALM_INV016_GeneralFaultTrip | INV016_GeneralFaultTrip | INV016 | Inverter | General Fault Trip | Yes
ALM_INV016_GridConnectionDeratingInverterInternalCauses | INV016_GridConnectionDeratingInverterInternalCauses | INV016 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV016_GridConnectionDeratingPowerRationing | INV016_GridConnectionDeratingPowerRationing | INV016 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV016_GridLoss | INV016_GridLoss | INV016 | Inverter | Grid Loss | Yes
ALM_INV016_GridOverfrequency | INV016_GridOverfrequency | INV016 | Inverter | Grid Overfrequency | Yes
ALM_INV016_GridOvervoltage | INV016_GridOvervoltage | INV016 | Inverter | Grid Overvoltage | Yes
ALM_INV016_GridTiedOffGridControllerAbnormal | INV016_GridTiedOffGridControllerAbnormal | INV016 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV016_GridUnderfrequency | INV016_GridUnderfrequency | INV016 | Inverter | Grid Underfrequency | Yes
ALM_INV016_GridUndervoltage | INV016_GridUndervoltage | INV016 | Inverter | Grid Undervoltage | Yes
ALM_INV016_GroundFault | INV016_GroundFault | INV016 | Inverter | Ground Fault | Yes
ALM_INV016_HighInputStringVoltageGround | INV016_HighInputStringVoltageGround | INV016 | Inverter | High input string voltage to ground | Yes
ALM_INV016_HighStringInputVoltage | INV016_HighStringInputVoltage | INV016 | Inverter | High string input voltage | Yes
ALM_INV016_InverterTripHistoryAvailable | INV016_InverterTripHistoryAvailable | INV016 | Inverter | Inverter Trip History Available | Yes
ALM_INV016_IslandingDetectionStatus | INV016_IslandingDetectionStatus | INV016 | Inverter | Islanding Detection Status | Yes
ALM_INV016_LicenseExpired | INV016_LicenseExpired | INV016 | Inverter | License Expired | Yes
ALM_INV016_LockingStatus | INV016_LockingStatus | INV016 | Inverter | Locking status | Yes
ALM_INV016_LowInsulationResistance | INV016_LowInsulationResistance | INV016 | Inverter | Low Insulation Resistance | Yes
ALM_INV016_OffGridOutputOverload | INV016_OffGridOutputOverload | INV016 | Inverter | Off-grid output overload | Yes
ALM_INV016_OptimizerFault | INV016_OptimizerFault | INV016 | Inverter | Optimizer fault | Yes
ALM_INV016_OutputDCComponentOverhigh | INV016_OutputDCComponentOverhigh | INV016 | Inverter | Output DC Component Overhigh | Yes
ALM_INV016_OutputOvercurrent | INV016_OutputOvercurrent | INV016 | Inverter | Output Overcurrent | Yes
ALM_INV016_PVStringLoss | INV016_PVStringLoss | INV016 | Inverter | PV String Loss | Yes
ALM_INV016_PassiveIslanding | INV016_PassiveIslanding | INV016 | Inverter | Passive Islanding | Yes
ALM_INV016_PeripheralPortShortCircuit | INV016_PeripheralPortShortCircuit | INV016 | Inverter | Peripheral port short circuit | Yes
ALM_INV016_PhaseWireShortCircuitedPE | INV016_PhaseWireShortCircuitedPE | INV016 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV016_PowerLimitationActiveGridCommand | INV016_PowerLimitationActiveGridCommand | INV016 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV016_StringReverseConnection | INV016_StringReverseConnection | INV016 | Inverter | String Reverse Connection | Yes
ALM_INV016_StringReversePolarity | INV016_StringReversePolarity | INV016 | Inverter | String Reverse Polarity | Yes
ALM_INV016_TransientACOvervoltage | INV016_TransientACOvervoltage | INV016 | Inverter | Transient AC Overvoltage | Yes
ALM_INV016_WarningActive | INV016_WarningActive | INV016 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV017_ACOvervoltage | INV017_ACOvervoltage | INV017 | Inverter | AC Overvoltage | Yes
ALM_INV017_ACUndervoltage | INV017_ACUndervoltage | INV017 | Inverter | AC Undervoltage | Yes
ALM_INV017_AFCISelfCheckFailure | INV017_AFCISelfCheckFailure | INV017 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV017_AbnormalGrounding | INV017_AbnormalGrounding | INV017 | Inverter | Abnormal Grounding | Yes
ALM_INV017_AbnormalPVModuleConfiguration | INV017_AbnormalPVModuleConfiguration | INV017 | Inverter | Abnormal PV module configuration | Yes
ALM_INV017_AbnormalResidualCurrent | INV017_AbnormalResidualCurrent | INV017 | Inverter | Abnormal Residual Current | Yes
ALM_INV017_AbnormalStringPower | INV017_AbnormalStringPower | INV017 | Inverter | Abnormal String Power | Yes
ALM_INV017_ActiveIslanding | INV017_ActiveIslanding | INV017 | Inverter | Active Islanding | Yes
ALM_INV017_BuiltPIDOperationAbnormal | INV017_BuiltPIDOperationAbnormal | INV017 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV017_CabinetOvertemperature | INV017_CabinetOvertemperature | INV017 | Inverter | Cabinet Overtemperature | Yes
ALM_INV017_CommunicationFailure | INV017_CommunicationFailure | INV017 | Inverter | Communication Failure | Yes
ALM_INV017_CommunicationStatus | INV017_CommunicationStatus | INV017 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV017_DCArcFault | INV017_DCArcFault | INV017 | Inverter | DC Arc Fault | Yes
ALM_INV017_DCInsulationFault | INV017_DCInsulationFault | INV017 | Inverter | DC Insulation Fault | Yes
ALM_INV017_DCOvervoltage | INV017_DCOvervoltage | INV017 | Inverter | DC Overvoltage | Yes
ALM_INV017_DeviceFault | INV017_DeviceFault | INV017 | Inverter | Device Fault | Yes
ALM_INV017_ExternalFanAbnormal | INV017_ExternalFanAbnormal | INV017 | Inverter | External fan abnormal | Yes
ALM_INV017_FanFailure | INV017_FanFailure | INV017 | Inverter | Fan Failure | Yes
ALM_INV017_Faulty | INV017_Faulty | INV017 | Inverter | Faulty | Yes
ALM_INV017_FaultyMonitoringUnit | INV017_FaultyMonitoringUnit | INV017 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV017_FaultyPowerCollector | INV017_FaultyPowerCollector | INV017 | Inverter | Faulty Power Collector | Yes
ALM_INV017_GeneralFaultTrip | INV017_GeneralFaultTrip | INV017 | Inverter | General Fault Trip | Yes
ALM_INV017_GridConnectionDeratingInverterInternalCauses | INV017_GridConnectionDeratingInverterInternalCauses | INV017 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV017_GridConnectionDeratingPowerRationing | INV017_GridConnectionDeratingPowerRationing | INV017 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV017_GridLoss | INV017_GridLoss | INV017 | Inverter | Grid Loss | Yes
ALM_INV017_GridOverfrequency | INV017_GridOverfrequency | INV017 | Inverter | Grid Overfrequency | Yes
ALM_INV017_GridOvervoltage | INV017_GridOvervoltage | INV017 | Inverter | Grid Overvoltage | Yes
ALM_INV017_GridTiedOffGridControllerAbnormal | INV017_GridTiedOffGridControllerAbnormal | INV017 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV017_GridUnderfrequency | INV017_GridUnderfrequency | INV017 | Inverter | Grid Underfrequency | Yes
ALM_INV017_GridUndervoltage | INV017_GridUndervoltage | INV017 | Inverter | Grid Undervoltage | Yes
ALM_INV017_GroundFault | INV017_GroundFault | INV017 | Inverter | Ground Fault | Yes
ALM_INV017_HighInputStringVoltageGround | INV017_HighInputStringVoltageGround | INV017 | Inverter | High input string voltage to ground | Yes
ALM_INV017_HighStringInputVoltage | INV017_HighStringInputVoltage | INV017 | Inverter | High string input voltage | Yes
ALM_INV017_InverterTripHistoryAvailable | INV017_InverterTripHistoryAvailable | INV017 | Inverter | Inverter Trip History Available | Yes
ALM_INV017_IslandingDetectionStatus | INV017_IslandingDetectionStatus | INV017 | Inverter | Islanding Detection Status | Yes
ALM_INV017_LicenseExpired | INV017_LicenseExpired | INV017 | Inverter | License Expired | Yes
ALM_INV017_LockingStatus | INV017_LockingStatus | INV017 | Inverter | Locking status | Yes
ALM_INV017_LowInsulationResistance | INV017_LowInsulationResistance | INV017 | Inverter | Low Insulation Resistance | Yes
ALM_INV017_OffGridOutputOverload | INV017_OffGridOutputOverload | INV017 | Inverter | Off-grid output overload | Yes
ALM_INV017_OptimizerFault | INV017_OptimizerFault | INV017 | Inverter | Optimizer fault | Yes
ALM_INV017_OutputDCComponentOverhigh | INV017_OutputDCComponentOverhigh | INV017 | Inverter | Output DC Component Overhigh | Yes
ALM_INV017_OutputOvercurrent | INV017_OutputOvercurrent | INV017 | Inverter | Output Overcurrent | Yes
ALM_INV017_PVStringLoss | INV017_PVStringLoss | INV017 | Inverter | PV String Loss | Yes
ALM_INV017_PassiveIslanding | INV017_PassiveIslanding | INV017 | Inverter | Passive Islanding | Yes
ALM_INV017_PeripheralPortShortCircuit | INV017_PeripheralPortShortCircuit | INV017 | Inverter | Peripheral port short circuit | Yes
ALM_INV017_PhaseWireShortCircuitedPE | INV017_PhaseWireShortCircuitedPE | INV017 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV017_PowerLimitationActiveGridCommand | INV017_PowerLimitationActiveGridCommand | INV017 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV017_StringReverseConnection | INV017_StringReverseConnection | INV017 | Inverter | String Reverse Connection | Yes
ALM_INV017_StringReversePolarity | INV017_StringReversePolarity | INV017 | Inverter | String Reverse Polarity | Yes
ALM_INV017_TransientACOvervoltage | INV017_TransientACOvervoltage | INV017 | Inverter | Transient AC Overvoltage | Yes
ALM_INV017_WarningActive | INV017_WarningActive | INV017 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV018_ACOvervoltage | INV018_ACOvervoltage | INV018 | Inverter | AC Overvoltage | Yes
ALM_INV018_ACUndervoltage | INV018_ACUndervoltage | INV018 | Inverter | AC Undervoltage | Yes
ALM_INV018_AFCISelfCheckFailure | INV018_AFCISelfCheckFailure | INV018 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV018_AbnormalGrounding | INV018_AbnormalGrounding | INV018 | Inverter | Abnormal Grounding | Yes
ALM_INV018_AbnormalPVModuleConfiguration | INV018_AbnormalPVModuleConfiguration | INV018 | Inverter | Abnormal PV module configuration | Yes
ALM_INV018_AbnormalResidualCurrent | INV018_AbnormalResidualCurrent | INV018 | Inverter | Abnormal Residual Current | Yes
ALM_INV018_AbnormalStringPower | INV018_AbnormalStringPower | INV018 | Inverter | Abnormal String Power | Yes
ALM_INV018_ActiveIslanding | INV018_ActiveIslanding | INV018 | Inverter | Active Islanding | Yes
ALM_INV018_BuiltPIDOperationAbnormal | INV018_BuiltPIDOperationAbnormal | INV018 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV018_CabinetOvertemperature | INV018_CabinetOvertemperature | INV018 | Inverter | Cabinet Overtemperature | Yes
ALM_INV018_CommunicationFailure | INV018_CommunicationFailure | INV018 | Inverter | Communication Failure | Yes
ALM_INV018_CommunicationStatus | INV018_CommunicationStatus | INV018 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV018_DCArcFault | INV018_DCArcFault | INV018 | Inverter | DC Arc Fault | Yes
ALM_INV018_DCInsulationFault | INV018_DCInsulationFault | INV018 | Inverter | DC Insulation Fault | Yes
ALM_INV018_DCOvervoltage | INV018_DCOvervoltage | INV018 | Inverter | DC Overvoltage | Yes
ALM_INV018_DeviceFault | INV018_DeviceFault | INV018 | Inverter | Device Fault | Yes
ALM_INV018_ExternalFanAbnormal | INV018_ExternalFanAbnormal | INV018 | Inverter | External fan abnormal | Yes
ALM_INV018_FanFailure | INV018_FanFailure | INV018 | Inverter | Fan Failure | Yes
ALM_INV018_Faulty | INV018_Faulty | INV018 | Inverter | Faulty | Yes
ALM_INV018_FaultyMonitoringUnit | INV018_FaultyMonitoringUnit | INV018 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV018_FaultyPowerCollector | INV018_FaultyPowerCollector | INV018 | Inverter | Faulty Power Collector | Yes
ALM_INV018_GeneralFaultTrip | INV018_GeneralFaultTrip | INV018 | Inverter | General Fault Trip | Yes
ALM_INV018_GridConnectionDeratingInverterInternalCauses | INV018_GridConnectionDeratingInverterInternalCauses | INV018 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV018_GridConnectionDeratingPowerRationing | INV018_GridConnectionDeratingPowerRationing | INV018 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV018_GridLoss | INV018_GridLoss | INV018 | Inverter | Grid Loss | Yes
ALM_INV018_GridOverfrequency | INV018_GridOverfrequency | INV018 | Inverter | Grid Overfrequency | Yes
ALM_INV018_GridOvervoltage | INV018_GridOvervoltage | INV018 | Inverter | Grid Overvoltage | Yes
ALM_INV018_GridTiedOffGridControllerAbnormal | INV018_GridTiedOffGridControllerAbnormal | INV018 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV018_GridUnderfrequency | INV018_GridUnderfrequency | INV018 | Inverter | Grid Underfrequency | Yes
ALM_INV018_GridUndervoltage | INV018_GridUndervoltage | INV018 | Inverter | Grid Undervoltage | Yes
ALM_INV018_GroundFault | INV018_GroundFault | INV018 | Inverter | Ground Fault | Yes
ALM_INV018_HighInputStringVoltageGround | INV018_HighInputStringVoltageGround | INV018 | Inverter | High input string voltage to ground | Yes
ALM_INV018_HighStringInputVoltage | INV018_HighStringInputVoltage | INV018 | Inverter | High string input voltage | Yes
ALM_INV018_InverterTripHistoryAvailable | INV018_InverterTripHistoryAvailable | INV018 | Inverter | Inverter Trip History Available | Yes
ALM_INV018_IslandingDetectionStatus | INV018_IslandingDetectionStatus | INV018 | Inverter | Islanding Detection Status | Yes
ALM_INV018_LicenseExpired | INV018_LicenseExpired | INV018 | Inverter | License Expired | Yes
ALM_INV018_LockingStatus | INV018_LockingStatus | INV018 | Inverter | Locking status | Yes
ALM_INV018_LowInsulationResistance | INV018_LowInsulationResistance | INV018 | Inverter | Low Insulation Resistance | Yes
ALM_INV018_OffGridOutputOverload | INV018_OffGridOutputOverload | INV018 | Inverter | Off-grid output overload | Yes
ALM_INV018_OptimizerFault | INV018_OptimizerFault | INV018 | Inverter | Optimizer fault | Yes
ALM_INV018_OutputDCComponentOverhigh | INV018_OutputDCComponentOverhigh | INV018 | Inverter | Output DC Component Overhigh | Yes
ALM_INV018_OutputOvercurrent | INV018_OutputOvercurrent | INV018 | Inverter | Output Overcurrent | Yes
ALM_INV018_PVStringLoss | INV018_PVStringLoss | INV018 | Inverter | PV String Loss | Yes
ALM_INV018_PassiveIslanding | INV018_PassiveIslanding | INV018 | Inverter | Passive Islanding | Yes
ALM_INV018_PeripheralPortShortCircuit | INV018_PeripheralPortShortCircuit | INV018 | Inverter | Peripheral port short circuit | Yes
ALM_INV018_PhaseWireShortCircuitedPE | INV018_PhaseWireShortCircuitedPE | INV018 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV018_PowerLimitationActiveGridCommand | INV018_PowerLimitationActiveGridCommand | INV018 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV018_StringReverseConnection | INV018_StringReverseConnection | INV018 | Inverter | String Reverse Connection | Yes
ALM_INV018_StringReversePolarity | INV018_StringReversePolarity | INV018 | Inverter | String Reverse Polarity | Yes
ALM_INV018_TransientACOvervoltage | INV018_TransientACOvervoltage | INV018 | Inverter | Transient AC Overvoltage | Yes
ALM_INV018_WarningActive | INV018_WarningActive | INV018 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV019_ACOvervoltage | INV019_ACOvervoltage | INV019 | Inverter | AC Overvoltage | Yes
ALM_INV019_ACUndervoltage | INV019_ACUndervoltage | INV019 | Inverter | AC Undervoltage | Yes
ALM_INV019_AFCISelfCheckFailure | INV019_AFCISelfCheckFailure | INV019 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV019_AbnormalGrounding | INV019_AbnormalGrounding | INV019 | Inverter | Abnormal Grounding | Yes
ALM_INV019_AbnormalPVModuleConfiguration | INV019_AbnormalPVModuleConfiguration | INV019 | Inverter | Abnormal PV module configuration | Yes
ALM_INV019_AbnormalResidualCurrent | INV019_AbnormalResidualCurrent | INV019 | Inverter | Abnormal Residual Current | Yes
ALM_INV019_AbnormalStringPower | INV019_AbnormalStringPower | INV019 | Inverter | Abnormal String Power | Yes
ALM_INV019_ActiveIslanding | INV019_ActiveIslanding | INV019 | Inverter | Active Islanding | Yes
ALM_INV019_BuiltPIDOperationAbnormal | INV019_BuiltPIDOperationAbnormal | INV019 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV019_CabinetOvertemperature | INV019_CabinetOvertemperature | INV019 | Inverter | Cabinet Overtemperature | Yes
ALM_INV019_CommunicationFailure | INV019_CommunicationFailure | INV019 | Inverter | Communication Failure | Yes
ALM_INV019_CommunicationStatus | INV019_CommunicationStatus | INV019 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV019_DCArcFault | INV019_DCArcFault | INV019 | Inverter | DC Arc Fault | Yes
ALM_INV019_DCInsulationFault | INV019_DCInsulationFault | INV019 | Inverter | DC Insulation Fault | Yes
ALM_INV019_DCOvervoltage | INV019_DCOvervoltage | INV019 | Inverter | DC Overvoltage | Yes
ALM_INV019_DeviceFault | INV019_DeviceFault | INV019 | Inverter | Device Fault | Yes
ALM_INV019_ExternalFanAbnormal | INV019_ExternalFanAbnormal | INV019 | Inverter | External fan abnormal | Yes
ALM_INV019_FanFailure | INV019_FanFailure | INV019 | Inverter | Fan Failure | Yes
ALM_INV019_Faulty | INV019_Faulty | INV019 | Inverter | Faulty | Yes
ALM_INV019_FaultyMonitoringUnit | INV019_FaultyMonitoringUnit | INV019 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV019_FaultyPowerCollector | INV019_FaultyPowerCollector | INV019 | Inverter | Faulty Power Collector | Yes
ALM_INV019_GeneralFaultTrip | INV019_GeneralFaultTrip | INV019 | Inverter | General Fault Trip | Yes
ALM_INV019_GridConnectionDeratingInverterInternalCauses | INV019_GridConnectionDeratingInverterInternalCauses | INV019 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV019_GridConnectionDeratingPowerRationing | INV019_GridConnectionDeratingPowerRationing | INV019 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV019_GridLoss | INV019_GridLoss | INV019 | Inverter | Grid Loss | Yes
ALM_INV019_GridOverfrequency | INV019_GridOverfrequency | INV019 | Inverter | Grid Overfrequency | Yes
ALM_INV019_GridOvervoltage | INV019_GridOvervoltage | INV019 | Inverter | Grid Overvoltage | Yes
ALM_INV019_GridTiedOffGridControllerAbnormal | INV019_GridTiedOffGridControllerAbnormal | INV019 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV019_GridUnderfrequency | INV019_GridUnderfrequency | INV019 | Inverter | Grid Underfrequency | Yes
ALM_INV019_GridUndervoltage | INV019_GridUndervoltage | INV019 | Inverter | Grid Undervoltage | Yes
ALM_INV019_GroundFault | INV019_GroundFault | INV019 | Inverter | Ground Fault | Yes
ALM_INV019_HighInputStringVoltageGround | INV019_HighInputStringVoltageGround | INV019 | Inverter | High input string voltage to ground | Yes
ALM_INV019_HighStringInputVoltage | INV019_HighStringInputVoltage | INV019 | Inverter | High string input voltage | Yes
ALM_INV019_InverterTripHistoryAvailable | INV019_InverterTripHistoryAvailable | INV019 | Inverter | Inverter Trip History Available | Yes
ALM_INV019_IslandingDetectionStatus | INV019_IslandingDetectionStatus | INV019 | Inverter | Islanding Detection Status | Yes
ALM_INV019_LicenseExpired | INV019_LicenseExpired | INV019 | Inverter | License Expired | Yes
ALM_INV019_LockingStatus | INV019_LockingStatus | INV019 | Inverter | Locking status | Yes
ALM_INV019_LowInsulationResistance | INV019_LowInsulationResistance | INV019 | Inverter | Low Insulation Resistance | Yes
ALM_INV019_OffGridOutputOverload | INV019_OffGridOutputOverload | INV019 | Inverter | Off-grid output overload | Yes
ALM_INV019_OptimizerFault | INV019_OptimizerFault | INV019 | Inverter | Optimizer fault | Yes
ALM_INV019_OutputDCComponentOverhigh | INV019_OutputDCComponentOverhigh | INV019 | Inverter | Output DC Component Overhigh | Yes
ALM_INV019_OutputOvercurrent | INV019_OutputOvercurrent | INV019 | Inverter | Output Overcurrent | Yes
ALM_INV019_PVStringLoss | INV019_PVStringLoss | INV019 | Inverter | PV String Loss | Yes
ALM_INV019_PassiveIslanding | INV019_PassiveIslanding | INV019 | Inverter | Passive Islanding | Yes
ALM_INV019_PeripheralPortShortCircuit | INV019_PeripheralPortShortCircuit | INV019 | Inverter | Peripheral port short circuit | Yes
ALM_INV019_PhaseWireShortCircuitedPE | INV019_PhaseWireShortCircuitedPE | INV019 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV019_PowerLimitationActiveGridCommand | INV019_PowerLimitationActiveGridCommand | INV019 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV019_StringReverseConnection | INV019_StringReverseConnection | INV019 | Inverter | String Reverse Connection | Yes
ALM_INV019_StringReversePolarity | INV019_StringReversePolarity | INV019 | Inverter | String Reverse Polarity | Yes
ALM_INV019_TransientACOvervoltage | INV019_TransientACOvervoltage | INV019 | Inverter | Transient AC Overvoltage | Yes
ALM_INV019_WarningActive | INV019_WarningActive | INV019 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV020_ACOvervoltage | INV020_ACOvervoltage | INV020 | Inverter | AC Overvoltage | Yes
ALM_INV020_ACUndervoltage | INV020_ACUndervoltage | INV020 | Inverter | AC Undervoltage | Yes
ALM_INV020_AFCISelfCheckFailure | INV020_AFCISelfCheckFailure | INV020 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV020_AbnormalGrounding | INV020_AbnormalGrounding | INV020 | Inverter | Abnormal Grounding | Yes
ALM_INV020_AbnormalPVModuleConfiguration | INV020_AbnormalPVModuleConfiguration | INV020 | Inverter | Abnormal PV module configuration | Yes
ALM_INV020_AbnormalResidualCurrent | INV020_AbnormalResidualCurrent | INV020 | Inverter | Abnormal Residual Current | Yes
ALM_INV020_AbnormalStringPower | INV020_AbnormalStringPower | INV020 | Inverter | Abnormal String Power | Yes
ALM_INV020_ActiveIslanding | INV020_ActiveIslanding | INV020 | Inverter | Active Islanding | Yes
ALM_INV020_BuiltPIDOperationAbnormal | INV020_BuiltPIDOperationAbnormal | INV020 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV020_CabinetOvertemperature | INV020_CabinetOvertemperature | INV020 | Inverter | Cabinet Overtemperature | Yes
ALM_INV020_CommunicationFailure | INV020_CommunicationFailure | INV020 | Inverter | Communication Failure | Yes
ALM_INV020_CommunicationStatus | INV020_CommunicationStatus | INV020 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV020_DCArcFault | INV020_DCArcFault | INV020 | Inverter | DC Arc Fault | Yes
ALM_INV020_DCInsulationFault | INV020_DCInsulationFault | INV020 | Inverter | DC Insulation Fault | Yes
ALM_INV020_DCOvervoltage | INV020_DCOvervoltage | INV020 | Inverter | DC Overvoltage | Yes
ALM_INV020_DeviceFault | INV020_DeviceFault | INV020 | Inverter | Device Fault | Yes
ALM_INV020_ExternalFanAbnormal | INV020_ExternalFanAbnormal | INV020 | Inverter | External fan abnormal | Yes
ALM_INV020_FanFailure | INV020_FanFailure | INV020 | Inverter | Fan Failure | Yes
ALM_INV020_Faulty | INV020_Faulty | INV020 | Inverter | Faulty | Yes
ALM_INV020_FaultyMonitoringUnit | INV020_FaultyMonitoringUnit | INV020 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV020_FaultyPowerCollector | INV020_FaultyPowerCollector | INV020 | Inverter | Faulty Power Collector | Yes
ALM_INV020_GeneralFaultTrip | INV020_GeneralFaultTrip | INV020 | Inverter | General Fault Trip | Yes
ALM_INV020_GridConnectionDeratingInverterInternalCauses | INV020_GridConnectionDeratingInverterInternalCauses | INV020 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV020_GridConnectionDeratingPowerRationing | INV020_GridConnectionDeratingPowerRationing | INV020 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV020_GridLoss | INV020_GridLoss | INV020 | Inverter | Grid Loss | Yes
ALM_INV020_GridOverfrequency | INV020_GridOverfrequency | INV020 | Inverter | Grid Overfrequency | Yes
ALM_INV020_GridOvervoltage | INV020_GridOvervoltage | INV020 | Inverter | Grid Overvoltage | Yes
ALM_INV020_GridTiedOffGridControllerAbnormal | INV020_GridTiedOffGridControllerAbnormal | INV020 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV020_GridUnderfrequency | INV020_GridUnderfrequency | INV020 | Inverter | Grid Underfrequency | Yes
ALM_INV020_GridUndervoltage | INV020_GridUndervoltage | INV020 | Inverter | Grid Undervoltage | Yes
ALM_INV020_GroundFault | INV020_GroundFault | INV020 | Inverter | Ground Fault | Yes
ALM_INV020_HighInputStringVoltageGround | INV020_HighInputStringVoltageGround | INV020 | Inverter | High input string voltage to ground | Yes
ALM_INV020_HighStringInputVoltage | INV020_HighStringInputVoltage | INV020 | Inverter | High string input voltage | Yes
ALM_INV020_InverterTripHistoryAvailable | INV020_InverterTripHistoryAvailable | INV020 | Inverter | Inverter Trip History Available | Yes
ALM_INV020_IslandingDetectionStatus | INV020_IslandingDetectionStatus | INV020 | Inverter | Islanding Detection Status | Yes
ALM_INV020_LicenseExpired | INV020_LicenseExpired | INV020 | Inverter | License Expired | Yes
ALM_INV020_LockingStatus | INV020_LockingStatus | INV020 | Inverter | Locking status | Yes
ALM_INV020_LowInsulationResistance | INV020_LowInsulationResistance | INV020 | Inverter | Low Insulation Resistance | Yes
ALM_INV020_OffGridOutputOverload | INV020_OffGridOutputOverload | INV020 | Inverter | Off-grid output overload | Yes
ALM_INV020_OptimizerFault | INV020_OptimizerFault | INV020 | Inverter | Optimizer fault | Yes
ALM_INV020_OutputDCComponentOverhigh | INV020_OutputDCComponentOverhigh | INV020 | Inverter | Output DC Component Overhigh | Yes
ALM_INV020_OutputOvercurrent | INV020_OutputOvercurrent | INV020 | Inverter | Output Overcurrent | Yes
ALM_INV020_PVStringLoss | INV020_PVStringLoss | INV020 | Inverter | PV String Loss | Yes
ALM_INV020_PassiveIslanding | INV020_PassiveIslanding | INV020 | Inverter | Passive Islanding | Yes
ALM_INV020_PeripheralPortShortCircuit | INV020_PeripheralPortShortCircuit | INV020 | Inverter | Peripheral port short circuit | Yes
ALM_INV020_PhaseWireShortCircuitedPE | INV020_PhaseWireShortCircuitedPE | INV020 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV020_PowerLimitationActiveGridCommand | INV020_PowerLimitationActiveGridCommand | INV020 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV020_StringReverseConnection | INV020_StringReverseConnection | INV020 | Inverter | String Reverse Connection | Yes
ALM_INV020_StringReversePolarity | INV020_StringReversePolarity | INV020 | Inverter | String Reverse Polarity | Yes
ALM_INV020_TransientACOvervoltage | INV020_TransientACOvervoltage | INV020 | Inverter | Transient AC Overvoltage | Yes
ALM_INV020_WarningActive | INV020_WarningActive | INV020 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV021_ACOvervoltage | INV021_ACOvervoltage | INV021 | Inverter | AC Overvoltage | Yes
ALM_INV021_ACUndervoltage | INV021_ACUndervoltage | INV021 | Inverter | AC Undervoltage | Yes
ALM_INV021_AFCISelfCheckFailure | INV021_AFCISelfCheckFailure | INV021 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV021_AbnormalGrounding | INV021_AbnormalGrounding | INV021 | Inverter | Abnormal Grounding | Yes
ALM_INV021_AbnormalPVModuleConfiguration | INV021_AbnormalPVModuleConfiguration | INV021 | Inverter | Abnormal PV module configuration | Yes
ALM_INV021_AbnormalResidualCurrent | INV021_AbnormalResidualCurrent | INV021 | Inverter | Abnormal Residual Current | Yes
ALM_INV021_AbnormalStringPower | INV021_AbnormalStringPower | INV021 | Inverter | Abnormal String Power | Yes
ALM_INV021_ActiveIslanding | INV021_ActiveIslanding | INV021 | Inverter | Active Islanding | Yes
ALM_INV021_BuiltPIDOperationAbnormal | INV021_BuiltPIDOperationAbnormal | INV021 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV021_CabinetOvertemperature | INV021_CabinetOvertemperature | INV021 | Inverter | Cabinet Overtemperature | Yes
ALM_INV021_CommunicationFailure | INV021_CommunicationFailure | INV021 | Inverter | Communication Failure | Yes
ALM_INV021_CommunicationStatus | INV021_CommunicationStatus | INV021 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV021_DCArcFault | INV021_DCArcFault | INV021 | Inverter | DC Arc Fault | Yes
ALM_INV021_DCInsulationFault | INV021_DCInsulationFault | INV021 | Inverter | DC Insulation Fault | Yes
ALM_INV021_DCOvervoltage | INV021_DCOvervoltage | INV021 | Inverter | DC Overvoltage | Yes
ALM_INV021_DeviceFault | INV021_DeviceFault | INV021 | Inverter | Device Fault | Yes
ALM_INV021_ExternalFanAbnormal | INV021_ExternalFanAbnormal | INV021 | Inverter | External fan abnormal | Yes
ALM_INV021_FanFailure | INV021_FanFailure | INV021 | Inverter | Fan Failure | Yes
ALM_INV021_Faulty | INV021_Faulty | INV021 | Inverter | Faulty | Yes
ALM_INV021_FaultyMonitoringUnit | INV021_FaultyMonitoringUnit | INV021 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV021_FaultyPowerCollector | INV021_FaultyPowerCollector | INV021 | Inverter | Faulty Power Collector | Yes
ALM_INV021_GeneralFaultTrip | INV021_GeneralFaultTrip | INV021 | Inverter | General Fault Trip | Yes
ALM_INV021_GridConnectionDeratingInverterInternalCauses | INV021_GridConnectionDeratingInverterInternalCauses | INV021 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV021_GridConnectionDeratingPowerRationing | INV021_GridConnectionDeratingPowerRationing | INV021 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV021_GridLoss | INV021_GridLoss | INV021 | Inverter | Grid Loss | Yes
ALM_INV021_GridOverfrequency | INV021_GridOverfrequency | INV021 | Inverter | Grid Overfrequency | Yes
ALM_INV021_GridOvervoltage | INV021_GridOvervoltage | INV021 | Inverter | Grid Overvoltage | Yes
ALM_INV021_GridTiedOffGridControllerAbnormal | INV021_GridTiedOffGridControllerAbnormal | INV021 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV021_GridUnderfrequency | INV021_GridUnderfrequency | INV021 | Inverter | Grid Underfrequency | Yes
ALM_INV021_GridUndervoltage | INV021_GridUndervoltage | INV021 | Inverter | Grid Undervoltage | Yes
ALM_INV021_GroundFault | INV021_GroundFault | INV021 | Inverter | Ground Fault | Yes
ALM_INV021_HighInputStringVoltageGround | INV021_HighInputStringVoltageGround | INV021 | Inverter | High input string voltage to ground | Yes
ALM_INV021_HighStringInputVoltage | INV021_HighStringInputVoltage | INV021 | Inverter | High string input voltage | Yes
ALM_INV021_InverterTripHistoryAvailable | INV021_InverterTripHistoryAvailable | INV021 | Inverter | Inverter Trip History Available | Yes
ALM_INV021_IslandingDetectionStatus | INV021_IslandingDetectionStatus | INV021 | Inverter | Islanding Detection Status | Yes
ALM_INV021_LicenseExpired | INV021_LicenseExpired | INV021 | Inverter | License Expired | Yes
ALM_INV021_LockingStatus | INV021_LockingStatus | INV021 | Inverter | Locking status | Yes
ALM_INV021_LowInsulationResistance | INV021_LowInsulationResistance | INV021 | Inverter | Low Insulation Resistance | Yes
ALM_INV021_OffGridOutputOverload | INV021_OffGridOutputOverload | INV021 | Inverter | Off-grid output overload | Yes
ALM_INV021_OptimizerFault | INV021_OptimizerFault | INV021 | Inverter | Optimizer fault | Yes
ALM_INV021_OutputDCComponentOverhigh | INV021_OutputDCComponentOverhigh | INV021 | Inverter | Output DC Component Overhigh | Yes
ALM_INV021_OutputOvercurrent | INV021_OutputOvercurrent | INV021 | Inverter | Output Overcurrent | Yes
ALM_INV021_PVStringLoss | INV021_PVStringLoss | INV021 | Inverter | PV String Loss | Yes
ALM_INV021_PassiveIslanding | INV021_PassiveIslanding | INV021 | Inverter | Passive Islanding | Yes
ALM_INV021_PeripheralPortShortCircuit | INV021_PeripheralPortShortCircuit | INV021 | Inverter | Peripheral port short circuit | Yes
ALM_INV021_PhaseWireShortCircuitedPE | INV021_PhaseWireShortCircuitedPE | INV021 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV021_PowerLimitationActiveGridCommand | INV021_PowerLimitationActiveGridCommand | INV021 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV021_StringReverseConnection | INV021_StringReverseConnection | INV021 | Inverter | String Reverse Connection | Yes
ALM_INV021_StringReversePolarity | INV021_StringReversePolarity | INV021 | Inverter | String Reverse Polarity | Yes
ALM_INV021_TransientACOvervoltage | INV021_TransientACOvervoltage | INV021 | Inverter | Transient AC Overvoltage | Yes
ALM_INV021_WarningActive | INV021_WarningActive | INV021 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV022_ACOvervoltage | INV022_ACOvervoltage | INV022 | Inverter | AC Overvoltage | Yes
ALM_INV022_ACUndervoltage | INV022_ACUndervoltage | INV022 | Inverter | AC Undervoltage | Yes
ALM_INV022_AFCISelfCheckFailure | INV022_AFCISelfCheckFailure | INV022 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV022_AbnormalGrounding | INV022_AbnormalGrounding | INV022 | Inverter | Abnormal Grounding | Yes
ALM_INV022_AbnormalPVModuleConfiguration | INV022_AbnormalPVModuleConfiguration | INV022 | Inverter | Abnormal PV module configuration | Yes
ALM_INV022_AbnormalResidualCurrent | INV022_AbnormalResidualCurrent | INV022 | Inverter | Abnormal Residual Current | Yes
ALM_INV022_AbnormalStringPower | INV022_AbnormalStringPower | INV022 | Inverter | Abnormal String Power | Yes
ALM_INV022_ActiveIslanding | INV022_ActiveIslanding | INV022 | Inverter | Active Islanding | Yes
ALM_INV022_BuiltPIDOperationAbnormal | INV022_BuiltPIDOperationAbnormal | INV022 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV022_CabinetOvertemperature | INV022_CabinetOvertemperature | INV022 | Inverter | Cabinet Overtemperature | Yes
ALM_INV022_CommunicationFailure | INV022_CommunicationFailure | INV022 | Inverter | Communication Failure | Yes
ALM_INV022_CommunicationStatus | INV022_CommunicationStatus | INV022 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV022_DCArcFault | INV022_DCArcFault | INV022 | Inverter | DC Arc Fault | Yes
ALM_INV022_DCInsulationFault | INV022_DCInsulationFault | INV022 | Inverter | DC Insulation Fault | Yes
ALM_INV022_DCOvervoltage | INV022_DCOvervoltage | INV022 | Inverter | DC Overvoltage | Yes
ALM_INV022_DeviceFault | INV022_DeviceFault | INV022 | Inverter | Device Fault | Yes
ALM_INV022_ExternalFanAbnormal | INV022_ExternalFanAbnormal | INV022 | Inverter | External fan abnormal | Yes
ALM_INV022_FanFailure | INV022_FanFailure | INV022 | Inverter | Fan Failure | Yes
ALM_INV022_Faulty | INV022_Faulty | INV022 | Inverter | Faulty | Yes
ALM_INV022_FaultyMonitoringUnit | INV022_FaultyMonitoringUnit | INV022 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV022_FaultyPowerCollector | INV022_FaultyPowerCollector | INV022 | Inverter | Faulty Power Collector | Yes
ALM_INV022_GeneralFaultTrip | INV022_GeneralFaultTrip | INV022 | Inverter | General Fault Trip | Yes
ALM_INV022_GridConnectionDeratingInverterInternalCauses | INV022_GridConnectionDeratingInverterInternalCauses | INV022 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV022_GridConnectionDeratingPowerRationing | INV022_GridConnectionDeratingPowerRationing | INV022 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV022_GridLoss | INV022_GridLoss | INV022 | Inverter | Grid Loss | Yes
ALM_INV022_GridOverfrequency | INV022_GridOverfrequency | INV022 | Inverter | Grid Overfrequency | Yes
ALM_INV022_GridOvervoltage | INV022_GridOvervoltage | INV022 | Inverter | Grid Overvoltage | Yes
ALM_INV022_GridTiedOffGridControllerAbnormal | INV022_GridTiedOffGridControllerAbnormal | INV022 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV022_GridUnderfrequency | INV022_GridUnderfrequency | INV022 | Inverter | Grid Underfrequency | Yes
ALM_INV022_GridUndervoltage | INV022_GridUndervoltage | INV022 | Inverter | Grid Undervoltage | Yes
ALM_INV022_GroundFault | INV022_GroundFault | INV022 | Inverter | Ground Fault | Yes
ALM_INV022_HighInputStringVoltageGround | INV022_HighInputStringVoltageGround | INV022 | Inverter | High input string voltage to ground | Yes
ALM_INV022_HighStringInputVoltage | INV022_HighStringInputVoltage | INV022 | Inverter | High string input voltage | Yes
ALM_INV022_InverterTripHistoryAvailable | INV022_InverterTripHistoryAvailable | INV022 | Inverter | Inverter Trip History Available | Yes
ALM_INV022_IslandingDetectionStatus | INV022_IslandingDetectionStatus | INV022 | Inverter | Islanding Detection Status | Yes
ALM_INV022_LicenseExpired | INV022_LicenseExpired | INV022 | Inverter | License Expired | Yes
ALM_INV022_LockingStatus | INV022_LockingStatus | INV022 | Inverter | Locking status | Yes
ALM_INV022_LowInsulationResistance | INV022_LowInsulationResistance | INV022 | Inverter | Low Insulation Resistance | Yes
ALM_INV022_OffGridOutputOverload | INV022_OffGridOutputOverload | INV022 | Inverter | Off-grid output overload | Yes
ALM_INV022_OptimizerFault | INV022_OptimizerFault | INV022 | Inverter | Optimizer fault | Yes
ALM_INV022_OutputDCComponentOverhigh | INV022_OutputDCComponentOverhigh | INV022 | Inverter | Output DC Component Overhigh | Yes
ALM_INV022_OutputOvercurrent | INV022_OutputOvercurrent | INV022 | Inverter | Output Overcurrent | Yes
ALM_INV022_PVStringLoss | INV022_PVStringLoss | INV022 | Inverter | PV String Loss | Yes
ALM_INV022_PassiveIslanding | INV022_PassiveIslanding | INV022 | Inverter | Passive Islanding | Yes
ALM_INV022_PeripheralPortShortCircuit | INV022_PeripheralPortShortCircuit | INV022 | Inverter | Peripheral port short circuit | Yes
ALM_INV022_PhaseWireShortCircuitedPE | INV022_PhaseWireShortCircuitedPE | INV022 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV022_PowerLimitationActiveGridCommand | INV022_PowerLimitationActiveGridCommand | INV022 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV022_StringReverseConnection | INV022_StringReverseConnection | INV022 | Inverter | String Reverse Connection | Yes
ALM_INV022_StringReversePolarity | INV022_StringReversePolarity | INV022 | Inverter | String Reverse Polarity | Yes
ALM_INV022_TransientACOvervoltage | INV022_TransientACOvervoltage | INV022 | Inverter | Transient AC Overvoltage | Yes
ALM_INV022_WarningActive | INV022_WarningActive | INV022 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV023_ACOvervoltage | INV023_ACOvervoltage | INV023 | Inverter | AC Overvoltage | Yes
ALM_INV023_ACUndervoltage | INV023_ACUndervoltage | INV023 | Inverter | AC Undervoltage | Yes
ALM_INV023_AFCISelfCheckFailure | INV023_AFCISelfCheckFailure | INV023 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV023_AbnormalGrounding | INV023_AbnormalGrounding | INV023 | Inverter | Abnormal Grounding | Yes
ALM_INV023_AbnormalPVModuleConfiguration | INV023_AbnormalPVModuleConfiguration | INV023 | Inverter | Abnormal PV module configuration | Yes
ALM_INV023_AbnormalResidualCurrent | INV023_AbnormalResidualCurrent | INV023 | Inverter | Abnormal Residual Current | Yes
ALM_INV023_AbnormalStringPower | INV023_AbnormalStringPower | INV023 | Inverter | Abnormal String Power | Yes
ALM_INV023_ActiveIslanding | INV023_ActiveIslanding | INV023 | Inverter | Active Islanding | Yes
ALM_INV023_BuiltPIDOperationAbnormal | INV023_BuiltPIDOperationAbnormal | INV023 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV023_CabinetOvertemperature | INV023_CabinetOvertemperature | INV023 | Inverter | Cabinet Overtemperature | Yes
ALM_INV023_CommunicationFailure | INV023_CommunicationFailure | INV023 | Inverter | Communication Failure | Yes
ALM_INV023_CommunicationStatus | INV023_CommunicationStatus | INV023 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV023_DCArcFault | INV023_DCArcFault | INV023 | Inverter | DC Arc Fault | Yes
ALM_INV023_DCInsulationFault | INV023_DCInsulationFault | INV023 | Inverter | DC Insulation Fault | Yes
ALM_INV023_DCOvervoltage | INV023_DCOvervoltage | INV023 | Inverter | DC Overvoltage | Yes
ALM_INV023_DeviceFault | INV023_DeviceFault | INV023 | Inverter | Device Fault | Yes
ALM_INV023_ExternalFanAbnormal | INV023_ExternalFanAbnormal | INV023 | Inverter | External fan abnormal | Yes
ALM_INV023_FanFailure | INV023_FanFailure | INV023 | Inverter | Fan Failure | Yes
ALM_INV023_Faulty | INV023_Faulty | INV023 | Inverter | Faulty | Yes
ALM_INV023_FaultyMonitoringUnit | INV023_FaultyMonitoringUnit | INV023 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV023_FaultyPowerCollector | INV023_FaultyPowerCollector | INV023 | Inverter | Faulty Power Collector | Yes
ALM_INV023_GeneralFaultTrip | INV023_GeneralFaultTrip | INV023 | Inverter | General Fault Trip | Yes
ALM_INV023_GridConnectionDeratingInverterInternalCauses | INV023_GridConnectionDeratingInverterInternalCauses | INV023 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV023_GridConnectionDeratingPowerRationing | INV023_GridConnectionDeratingPowerRationing | INV023 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV023_GridLoss | INV023_GridLoss | INV023 | Inverter | Grid Loss | Yes
ALM_INV023_GridOverfrequency | INV023_GridOverfrequency | INV023 | Inverter | Grid Overfrequency | Yes
ALM_INV023_GridOvervoltage | INV023_GridOvervoltage | INV023 | Inverter | Grid Overvoltage | Yes
ALM_INV023_GridTiedOffGridControllerAbnormal | INV023_GridTiedOffGridControllerAbnormal | INV023 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV023_GridUnderfrequency | INV023_GridUnderfrequency | INV023 | Inverter | Grid Underfrequency | Yes
ALM_INV023_GridUndervoltage | INV023_GridUndervoltage | INV023 | Inverter | Grid Undervoltage | Yes
ALM_INV023_GroundFault | INV023_GroundFault | INV023 | Inverter | Ground Fault | Yes
ALM_INV023_HighInputStringVoltageGround | INV023_HighInputStringVoltageGround | INV023 | Inverter | High input string voltage to ground | Yes
ALM_INV023_HighStringInputVoltage | INV023_HighStringInputVoltage | INV023 | Inverter | High string input voltage | Yes
ALM_INV023_InverterTripHistoryAvailable | INV023_InverterTripHistoryAvailable | INV023 | Inverter | Inverter Trip History Available | Yes
ALM_INV023_IslandingDetectionStatus | INV023_IslandingDetectionStatus | INV023 | Inverter | Islanding Detection Status | Yes
ALM_INV023_LicenseExpired | INV023_LicenseExpired | INV023 | Inverter | License Expired | Yes
ALM_INV023_LockingStatus | INV023_LockingStatus | INV023 | Inverter | Locking status | Yes
ALM_INV023_LowInsulationResistance | INV023_LowInsulationResistance | INV023 | Inverter | Low Insulation Resistance | Yes
ALM_INV023_OffGridOutputOverload | INV023_OffGridOutputOverload | INV023 | Inverter | Off-grid output overload | Yes
ALM_INV023_OptimizerFault | INV023_OptimizerFault | INV023 | Inverter | Optimizer fault | Yes
ALM_INV023_OutputDCComponentOverhigh | INV023_OutputDCComponentOverhigh | INV023 | Inverter | Output DC Component Overhigh | Yes
ALM_INV023_OutputOvercurrent | INV023_OutputOvercurrent | INV023 | Inverter | Output Overcurrent | Yes
ALM_INV023_PVStringLoss | INV023_PVStringLoss | INV023 | Inverter | PV String Loss | Yes
ALM_INV023_PassiveIslanding | INV023_PassiveIslanding | INV023 | Inverter | Passive Islanding | Yes
ALM_INV023_PeripheralPortShortCircuit | INV023_PeripheralPortShortCircuit | INV023 | Inverter | Peripheral port short circuit | Yes
ALM_INV023_PhaseWireShortCircuitedPE | INV023_PhaseWireShortCircuitedPE | INV023 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV023_PowerLimitationActiveGridCommand | INV023_PowerLimitationActiveGridCommand | INV023 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV023_StringReverseConnection | INV023_StringReverseConnection | INV023 | Inverter | String Reverse Connection | Yes
ALM_INV023_StringReversePolarity | INV023_StringReversePolarity | INV023 | Inverter | String Reverse Polarity | Yes
ALM_INV023_TransientACOvervoltage | INV023_TransientACOvervoltage | INV023 | Inverter | Transient AC Overvoltage | Yes
ALM_INV023_WarningActive | INV023_WarningActive | INV023 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV024_ACOvervoltage | INV024_ACOvervoltage | INV024 | Inverter | AC Overvoltage | Yes
ALM_INV024_ACUndervoltage | INV024_ACUndervoltage | INV024 | Inverter | AC Undervoltage | Yes
ALM_INV024_AFCISelfCheckFailure | INV024_AFCISelfCheckFailure | INV024 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV024_AbnormalGrounding | INV024_AbnormalGrounding | INV024 | Inverter | Abnormal Grounding | Yes
ALM_INV024_AbnormalPVModuleConfiguration | INV024_AbnormalPVModuleConfiguration | INV024 | Inverter | Abnormal PV module configuration | Yes
ALM_INV024_AbnormalResidualCurrent | INV024_AbnormalResidualCurrent | INV024 | Inverter | Abnormal Residual Current | Yes
ALM_INV024_AbnormalStringPower | INV024_AbnormalStringPower | INV024 | Inverter | Abnormal String Power | Yes
ALM_INV024_ActiveIslanding | INV024_ActiveIslanding | INV024 | Inverter | Active Islanding | Yes
ALM_INV024_BuiltPIDOperationAbnormal | INV024_BuiltPIDOperationAbnormal | INV024 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV024_CabinetOvertemperature | INV024_CabinetOvertemperature | INV024 | Inverter | Cabinet Overtemperature | Yes
ALM_INV024_CommunicationFailure | INV024_CommunicationFailure | INV024 | Inverter | Communication Failure | Yes
ALM_INV024_CommunicationStatus | INV024_CommunicationStatus | INV024 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV024_DCArcFault | INV024_DCArcFault | INV024 | Inverter | DC Arc Fault | Yes
ALM_INV024_DCInsulationFault | INV024_DCInsulationFault | INV024 | Inverter | DC Insulation Fault | Yes
ALM_INV024_DCOvervoltage | INV024_DCOvervoltage | INV024 | Inverter | DC Overvoltage | Yes
ALM_INV024_DeviceFault | INV024_DeviceFault | INV024 | Inverter | Device Fault | Yes
ALM_INV024_ExternalFanAbnormal | INV024_ExternalFanAbnormal | INV024 | Inverter | External fan abnormal | Yes
ALM_INV024_FanFailure | INV024_FanFailure | INV024 | Inverter | Fan Failure | Yes
ALM_INV024_Faulty | INV024_Faulty | INV024 | Inverter | Faulty | Yes
ALM_INV024_FaultyMonitoringUnit | INV024_FaultyMonitoringUnit | INV024 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV024_FaultyPowerCollector | INV024_FaultyPowerCollector | INV024 | Inverter | Faulty Power Collector | Yes
ALM_INV024_GeneralFaultTrip | INV024_GeneralFaultTrip | INV024 | Inverter | General Fault Trip | Yes
ALM_INV024_GridConnectionDeratingInverterInternalCauses | INV024_GridConnectionDeratingInverterInternalCauses | INV024 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV024_GridConnectionDeratingPowerRationing | INV024_GridConnectionDeratingPowerRationing | INV024 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV024_GridLoss | INV024_GridLoss | INV024 | Inverter | Grid Loss | Yes
ALM_INV024_GridOverfrequency | INV024_GridOverfrequency | INV024 | Inverter | Grid Overfrequency | Yes
ALM_INV024_GridOvervoltage | INV024_GridOvervoltage | INV024 | Inverter | Grid Overvoltage | Yes
ALM_INV024_GridTiedOffGridControllerAbnormal | INV024_GridTiedOffGridControllerAbnormal | INV024 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV024_GridUnderfrequency | INV024_GridUnderfrequency | INV024 | Inverter | Grid Underfrequency | Yes
ALM_INV024_GridUndervoltage | INV024_GridUndervoltage | INV024 | Inverter | Grid Undervoltage | Yes
ALM_INV024_GroundFault | INV024_GroundFault | INV024 | Inverter | Ground Fault | Yes
ALM_INV024_HighInputStringVoltageGround | INV024_HighInputStringVoltageGround | INV024 | Inverter | High input string voltage to ground | Yes
ALM_INV024_HighStringInputVoltage | INV024_HighStringInputVoltage | INV024 | Inverter | High string input voltage | Yes
ALM_INV024_InverterTripHistoryAvailable | INV024_InverterTripHistoryAvailable | INV024 | Inverter | Inverter Trip History Available | Yes
ALM_INV024_IslandingDetectionStatus | INV024_IslandingDetectionStatus | INV024 | Inverter | Islanding Detection Status | Yes
ALM_INV024_LicenseExpired | INV024_LicenseExpired | INV024 | Inverter | License Expired | Yes
ALM_INV024_LockingStatus | INV024_LockingStatus | INV024 | Inverter | Locking status | Yes
ALM_INV024_LowInsulationResistance | INV024_LowInsulationResistance | INV024 | Inverter | Low Insulation Resistance | Yes
ALM_INV024_OffGridOutputOverload | INV024_OffGridOutputOverload | INV024 | Inverter | Off-grid output overload | Yes
ALM_INV024_OptimizerFault | INV024_OptimizerFault | INV024 | Inverter | Optimizer fault | Yes
ALM_INV024_OutputDCComponentOverhigh | INV024_OutputDCComponentOverhigh | INV024 | Inverter | Output DC Component Overhigh | Yes
ALM_INV024_OutputOvercurrent | INV024_OutputOvercurrent | INV024 | Inverter | Output Overcurrent | Yes
ALM_INV024_PVStringLoss | INV024_PVStringLoss | INV024 | Inverter | PV String Loss | Yes
ALM_INV024_PassiveIslanding | INV024_PassiveIslanding | INV024 | Inverter | Passive Islanding | Yes
ALM_INV024_PeripheralPortShortCircuit | INV024_PeripheralPortShortCircuit | INV024 | Inverter | Peripheral port short circuit | Yes
ALM_INV024_PhaseWireShortCircuitedPE | INV024_PhaseWireShortCircuitedPE | INV024 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV024_PowerLimitationActiveGridCommand | INV024_PowerLimitationActiveGridCommand | INV024 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV024_StringReverseConnection | INV024_StringReverseConnection | INV024 | Inverter | String Reverse Connection | Yes
ALM_INV024_StringReversePolarity | INV024_StringReversePolarity | INV024 | Inverter | String Reverse Polarity | Yes
ALM_INV024_TransientACOvervoltage | INV024_TransientACOvervoltage | INV024 | Inverter | Transient AC Overvoltage | Yes
ALM_INV024_WarningActive | INV024_WarningActive | INV024 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV025_ACOvervoltage | INV025_ACOvervoltage | INV025 | Inverter | AC Overvoltage | Yes
ALM_INV025_ACUndervoltage | INV025_ACUndervoltage | INV025 | Inverter | AC Undervoltage | Yes
ALM_INV025_AFCISelfCheckFailure | INV025_AFCISelfCheckFailure | INV025 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV025_AbnormalGrounding | INV025_AbnormalGrounding | INV025 | Inverter | Abnormal Grounding | Yes
ALM_INV025_AbnormalPVModuleConfiguration | INV025_AbnormalPVModuleConfiguration | INV025 | Inverter | Abnormal PV module configuration | Yes
ALM_INV025_AbnormalResidualCurrent | INV025_AbnormalResidualCurrent | INV025 | Inverter | Abnormal Residual Current | Yes
ALM_INV025_AbnormalStringPower | INV025_AbnormalStringPower | INV025 | Inverter | Abnormal String Power | Yes
ALM_INV025_ActiveIslanding | INV025_ActiveIslanding | INV025 | Inverter | Active Islanding | Yes
ALM_INV025_BuiltPIDOperationAbnormal | INV025_BuiltPIDOperationAbnormal | INV025 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV025_CabinetOvertemperature | INV025_CabinetOvertemperature | INV025 | Inverter | Cabinet Overtemperature | Yes
ALM_INV025_CommunicationFailure | INV025_CommunicationFailure | INV025 | Inverter | Communication Failure | Yes
ALM_INV025_CommunicationStatus | INV025_CommunicationStatus | INV025 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV025_DCArcFault | INV025_DCArcFault | INV025 | Inverter | DC Arc Fault | Yes
ALM_INV025_DCInsulationFault | INV025_DCInsulationFault | INV025 | Inverter | DC Insulation Fault | Yes
ALM_INV025_DCOvervoltage | INV025_DCOvervoltage | INV025 | Inverter | DC Overvoltage | Yes
ALM_INV025_DeviceFault | INV025_DeviceFault | INV025 | Inverter | Device Fault | Yes
ALM_INV025_ExternalFanAbnormal | INV025_ExternalFanAbnormal | INV025 | Inverter | External fan abnormal | Yes
ALM_INV025_FanFailure | INV025_FanFailure | INV025 | Inverter | Fan Failure | Yes
ALM_INV025_Faulty | INV025_Faulty | INV025 | Inverter | Faulty | Yes
ALM_INV025_FaultyMonitoringUnit | INV025_FaultyMonitoringUnit | INV025 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV025_FaultyPowerCollector | INV025_FaultyPowerCollector | INV025 | Inverter | Faulty Power Collector | Yes
ALM_INV025_GeneralFaultTrip | INV025_GeneralFaultTrip | INV025 | Inverter | General Fault Trip | Yes
ALM_INV025_GridConnectionDeratingInverterInternalCauses | INV025_GridConnectionDeratingInverterInternalCauses | INV025 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV025_GridConnectionDeratingPowerRationing | INV025_GridConnectionDeratingPowerRationing | INV025 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV025_GridLoss | INV025_GridLoss | INV025 | Inverter | Grid Loss | Yes
ALM_INV025_GridOverfrequency | INV025_GridOverfrequency | INV025 | Inverter | Grid Overfrequency | Yes
ALM_INV025_GridOvervoltage | INV025_GridOvervoltage | INV025 | Inverter | Grid Overvoltage | Yes
ALM_INV025_GridTiedOffGridControllerAbnormal | INV025_GridTiedOffGridControllerAbnormal | INV025 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV025_GridUnderfrequency | INV025_GridUnderfrequency | INV025 | Inverter | Grid Underfrequency | Yes
ALM_INV025_GridUndervoltage | INV025_GridUndervoltage | INV025 | Inverter | Grid Undervoltage | Yes
ALM_INV025_GroundFault | INV025_GroundFault | INV025 | Inverter | Ground Fault | Yes
ALM_INV025_HighInputStringVoltageGround | INV025_HighInputStringVoltageGround | INV025 | Inverter | High input string voltage to ground | Yes
ALM_INV025_HighStringInputVoltage | INV025_HighStringInputVoltage | INV025 | Inverter | High string input voltage | Yes
ALM_INV025_InverterTripHistoryAvailable | INV025_InverterTripHistoryAvailable | INV025 | Inverter | Inverter Trip History Available | Yes
ALM_INV025_IslandingDetectionStatus | INV025_IslandingDetectionStatus | INV025 | Inverter | Islanding Detection Status | Yes
ALM_INV025_LicenseExpired | INV025_LicenseExpired | INV025 | Inverter | License Expired | Yes
ALM_INV025_LockingStatus | INV025_LockingStatus | INV025 | Inverter | Locking status | Yes
ALM_INV025_LowInsulationResistance | INV025_LowInsulationResistance | INV025 | Inverter | Low Insulation Resistance | Yes
ALM_INV025_OffGridOutputOverload | INV025_OffGridOutputOverload | INV025 | Inverter | Off-grid output overload | Yes
ALM_INV025_OptimizerFault | INV025_OptimizerFault | INV025 | Inverter | Optimizer fault | Yes
ALM_INV025_OutputDCComponentOverhigh | INV025_OutputDCComponentOverhigh | INV025 | Inverter | Output DC Component Overhigh | Yes
ALM_INV025_OutputOvercurrent | INV025_OutputOvercurrent | INV025 | Inverter | Output Overcurrent | Yes
ALM_INV025_PVStringLoss | INV025_PVStringLoss | INV025 | Inverter | PV String Loss | Yes
ALM_INV025_PassiveIslanding | INV025_PassiveIslanding | INV025 | Inverter | Passive Islanding | Yes
ALM_INV025_PeripheralPortShortCircuit | INV025_PeripheralPortShortCircuit | INV025 | Inverter | Peripheral port short circuit | Yes
ALM_INV025_PhaseWireShortCircuitedPE | INV025_PhaseWireShortCircuitedPE | INV025 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV025_PowerLimitationActiveGridCommand | INV025_PowerLimitationActiveGridCommand | INV025 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV025_StringReverseConnection | INV025_StringReverseConnection | INV025 | Inverter | String Reverse Connection | Yes
ALM_INV025_StringReversePolarity | INV025_StringReversePolarity | INV025 | Inverter | String Reverse Polarity | Yes
ALM_INV025_TransientACOvervoltage | INV025_TransientACOvervoltage | INV025 | Inverter | Transient AC Overvoltage | Yes
ALM_INV025_WarningActive | INV025_WarningActive | INV025 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV026_ACOvervoltage | INV026_ACOvervoltage | INV026 | Inverter | AC Overvoltage | Yes
ALM_INV026_ACUndervoltage | INV026_ACUndervoltage | INV026 | Inverter | AC Undervoltage | Yes
ALM_INV026_AFCISelfCheckFailure | INV026_AFCISelfCheckFailure | INV026 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV026_AbnormalGrounding | INV026_AbnormalGrounding | INV026 | Inverter | Abnormal Grounding | Yes
ALM_INV026_AbnormalPVModuleConfiguration | INV026_AbnormalPVModuleConfiguration | INV026 | Inverter | Abnormal PV module configuration | Yes
ALM_INV026_AbnormalResidualCurrent | INV026_AbnormalResidualCurrent | INV026 | Inverter | Abnormal Residual Current | Yes
ALM_INV026_AbnormalStringPower | INV026_AbnormalStringPower | INV026 | Inverter | Abnormal String Power | Yes
ALM_INV026_ActiveIslanding | INV026_ActiveIslanding | INV026 | Inverter | Active Islanding | Yes
ALM_INV026_BuiltPIDOperationAbnormal | INV026_BuiltPIDOperationAbnormal | INV026 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV026_CabinetOvertemperature | INV026_CabinetOvertemperature | INV026 | Inverter | Cabinet Overtemperature | Yes
ALM_INV026_CommunicationFailure | INV026_CommunicationFailure | INV026 | Inverter | Communication Failure | Yes
ALM_INV026_CommunicationStatus | INV026_CommunicationStatus | INV026 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV026_DCArcFault | INV026_DCArcFault | INV026 | Inverter | DC Arc Fault | Yes
ALM_INV026_DCInsulationFault | INV026_DCInsulationFault | INV026 | Inverter | DC Insulation Fault | Yes
ALM_INV026_DCOvervoltage | INV026_DCOvervoltage | INV026 | Inverter | DC Overvoltage | Yes
ALM_INV026_DeviceFault | INV026_DeviceFault | INV026 | Inverter | Device Fault | Yes
ALM_INV026_ExternalFanAbnormal | INV026_ExternalFanAbnormal | INV026 | Inverter | External fan abnormal | Yes
ALM_INV026_FanFailure | INV026_FanFailure | INV026 | Inverter | Fan Failure | Yes
ALM_INV026_Faulty | INV026_Faulty | INV026 | Inverter | Faulty | Yes
ALM_INV026_FaultyMonitoringUnit | INV026_FaultyMonitoringUnit | INV026 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV026_FaultyPowerCollector | INV026_FaultyPowerCollector | INV026 | Inverter | Faulty Power Collector | Yes
ALM_INV026_GeneralFaultTrip | INV026_GeneralFaultTrip | INV026 | Inverter | General Fault Trip | Yes
ALM_INV026_GridConnectionDeratingInverterInternalCauses | INV026_GridConnectionDeratingInverterInternalCauses | INV026 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV026_GridConnectionDeratingPowerRationing | INV026_GridConnectionDeratingPowerRationing | INV026 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV026_GridLoss | INV026_GridLoss | INV026 | Inverter | Grid Loss | Yes
ALM_INV026_GridOverfrequency | INV026_GridOverfrequency | INV026 | Inverter | Grid Overfrequency | Yes
ALM_INV026_GridOvervoltage | INV026_GridOvervoltage | INV026 | Inverter | Grid Overvoltage | Yes
ALM_INV026_GridTiedOffGridControllerAbnormal | INV026_GridTiedOffGridControllerAbnormal | INV026 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV026_GridUnderfrequency | INV026_GridUnderfrequency | INV026 | Inverter | Grid Underfrequency | Yes
ALM_INV026_GridUndervoltage | INV026_GridUndervoltage | INV026 | Inverter | Grid Undervoltage | Yes
ALM_INV026_GroundFault | INV026_GroundFault | INV026 | Inverter | Ground Fault | Yes
ALM_INV026_HighInputStringVoltageGround | INV026_HighInputStringVoltageGround | INV026 | Inverter | High input string voltage to ground | Yes
ALM_INV026_HighStringInputVoltage | INV026_HighStringInputVoltage | INV026 | Inverter | High string input voltage | Yes
ALM_INV026_InverterTripHistoryAvailable | INV026_InverterTripHistoryAvailable | INV026 | Inverter | Inverter Trip History Available | Yes
ALM_INV026_IslandingDetectionStatus | INV026_IslandingDetectionStatus | INV026 | Inverter | Islanding Detection Status | Yes
ALM_INV026_LicenseExpired | INV026_LicenseExpired | INV026 | Inverter | License Expired | Yes
ALM_INV026_LockingStatus | INV026_LockingStatus | INV026 | Inverter | Locking status | Yes
ALM_INV026_LowInsulationResistance | INV026_LowInsulationResistance | INV026 | Inverter | Low Insulation Resistance | Yes
ALM_INV026_OffGridOutputOverload | INV026_OffGridOutputOverload | INV026 | Inverter | Off-grid output overload | Yes
ALM_INV026_OptimizerFault | INV026_OptimizerFault | INV026 | Inverter | Optimizer fault | Yes
ALM_INV026_OutputDCComponentOverhigh | INV026_OutputDCComponentOverhigh | INV026 | Inverter | Output DC Component Overhigh | Yes
ALM_INV026_OutputOvercurrent | INV026_OutputOvercurrent | INV026 | Inverter | Output Overcurrent | Yes
ALM_INV026_PVStringLoss | INV026_PVStringLoss | INV026 | Inverter | PV String Loss | Yes
ALM_INV026_PassiveIslanding | INV026_PassiveIslanding | INV026 | Inverter | Passive Islanding | Yes
ALM_INV026_PeripheralPortShortCircuit | INV026_PeripheralPortShortCircuit | INV026 | Inverter | Peripheral port short circuit | Yes
ALM_INV026_PhaseWireShortCircuitedPE | INV026_PhaseWireShortCircuitedPE | INV026 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV026_PowerLimitationActiveGridCommand | INV026_PowerLimitationActiveGridCommand | INV026 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV026_StringReverseConnection | INV026_StringReverseConnection | INV026 | Inverter | String Reverse Connection | Yes
ALM_INV026_StringReversePolarity | INV026_StringReversePolarity | INV026 | Inverter | String Reverse Polarity | Yes
ALM_INV026_TransientACOvervoltage | INV026_TransientACOvervoltage | INV026 | Inverter | Transient AC Overvoltage | Yes
ALM_INV026_WarningActive | INV026_WarningActive | INV026 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV027_ACOvervoltage | INV027_ACOvervoltage | INV027 | Inverter | AC Overvoltage | Yes
ALM_INV027_ACUndervoltage | INV027_ACUndervoltage | INV027 | Inverter | AC Undervoltage | Yes
ALM_INV027_AFCISelfCheckFailure | INV027_AFCISelfCheckFailure | INV027 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV027_AbnormalGrounding | INV027_AbnormalGrounding | INV027 | Inverter | Abnormal Grounding | Yes
ALM_INV027_AbnormalPVModuleConfiguration | INV027_AbnormalPVModuleConfiguration | INV027 | Inverter | Abnormal PV module configuration | Yes
ALM_INV027_AbnormalResidualCurrent | INV027_AbnormalResidualCurrent | INV027 | Inverter | Abnormal Residual Current | Yes
ALM_INV027_AbnormalStringPower | INV027_AbnormalStringPower | INV027 | Inverter | Abnormal String Power | Yes
ALM_INV027_ActiveIslanding | INV027_ActiveIslanding | INV027 | Inverter | Active Islanding | Yes
ALM_INV027_BuiltPIDOperationAbnormal | INV027_BuiltPIDOperationAbnormal | INV027 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV027_CabinetOvertemperature | INV027_CabinetOvertemperature | INV027 | Inverter | Cabinet Overtemperature | Yes
ALM_INV027_CommunicationFailure | INV027_CommunicationFailure | INV027 | Inverter | Communication Failure | Yes
ALM_INV027_CommunicationStatus | INV027_CommunicationStatus | INV027 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV027_DCArcFault | INV027_DCArcFault | INV027 | Inverter | DC Arc Fault | Yes
ALM_INV027_DCInsulationFault | INV027_DCInsulationFault | INV027 | Inverter | DC Insulation Fault | Yes
ALM_INV027_DCOvervoltage | INV027_DCOvervoltage | INV027 | Inverter | DC Overvoltage | Yes
ALM_INV027_DeviceFault | INV027_DeviceFault | INV027 | Inverter | Device Fault | Yes
ALM_INV027_ExternalFanAbnormal | INV027_ExternalFanAbnormal | INV027 | Inverter | External fan abnormal | Yes
ALM_INV027_FanFailure | INV027_FanFailure | INV027 | Inverter | Fan Failure | Yes
ALM_INV027_Faulty | INV027_Faulty | INV027 | Inverter | Faulty | Yes
ALM_INV027_FaultyMonitoringUnit | INV027_FaultyMonitoringUnit | INV027 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV027_FaultyPowerCollector | INV027_FaultyPowerCollector | INV027 | Inverter | Faulty Power Collector | Yes
ALM_INV027_GeneralFaultTrip | INV027_GeneralFaultTrip | INV027 | Inverter | General Fault Trip | Yes
ALM_INV027_GridConnectionDeratingInverterInternalCauses | INV027_GridConnectionDeratingInverterInternalCauses | INV027 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV027_GridConnectionDeratingPowerRationing | INV027_GridConnectionDeratingPowerRationing | INV027 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV027_GridLoss | INV027_GridLoss | INV027 | Inverter | Grid Loss | Yes
ALM_INV027_GridOverfrequency | INV027_GridOverfrequency | INV027 | Inverter | Grid Overfrequency | Yes
ALM_INV027_GridOvervoltage | INV027_GridOvervoltage | INV027 | Inverter | Grid Overvoltage | Yes
ALM_INV027_GridTiedOffGridControllerAbnormal | INV027_GridTiedOffGridControllerAbnormal | INV027 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV027_GridUnderfrequency | INV027_GridUnderfrequency | INV027 | Inverter | Grid Underfrequency | Yes
ALM_INV027_GridUndervoltage | INV027_GridUndervoltage | INV027 | Inverter | Grid Undervoltage | Yes
ALM_INV027_GroundFault | INV027_GroundFault | INV027 | Inverter | Ground Fault | Yes
ALM_INV027_HighInputStringVoltageGround | INV027_HighInputStringVoltageGround | INV027 | Inverter | High input string voltage to ground | Yes
ALM_INV027_HighStringInputVoltage | INV027_HighStringInputVoltage | INV027 | Inverter | High string input voltage | Yes
ALM_INV027_InverterTripHistoryAvailable | INV027_InverterTripHistoryAvailable | INV027 | Inverter | Inverter Trip History Available | Yes
ALM_INV027_IslandingDetectionStatus | INV027_IslandingDetectionStatus | INV027 | Inverter | Islanding Detection Status | Yes
ALM_INV027_LicenseExpired | INV027_LicenseExpired | INV027 | Inverter | License Expired | Yes
ALM_INV027_LockingStatus | INV027_LockingStatus | INV027 | Inverter | Locking status | Yes
ALM_INV027_LowInsulationResistance | INV027_LowInsulationResistance | INV027 | Inverter | Low Insulation Resistance | Yes
ALM_INV027_OffGridOutputOverload | INV027_OffGridOutputOverload | INV027 | Inverter | Off-grid output overload | Yes
ALM_INV027_OptimizerFault | INV027_OptimizerFault | INV027 | Inverter | Optimizer fault | Yes
ALM_INV027_OutputDCComponentOverhigh | INV027_OutputDCComponentOverhigh | INV027 | Inverter | Output DC Component Overhigh | Yes
ALM_INV027_OutputOvercurrent | INV027_OutputOvercurrent | INV027 | Inverter | Output Overcurrent | Yes
ALM_INV027_PVStringLoss | INV027_PVStringLoss | INV027 | Inverter | PV String Loss | Yes
ALM_INV027_PassiveIslanding | INV027_PassiveIslanding | INV027 | Inverter | Passive Islanding | Yes
ALM_INV027_PeripheralPortShortCircuit | INV027_PeripheralPortShortCircuit | INV027 | Inverter | Peripheral port short circuit | Yes
ALM_INV027_PhaseWireShortCircuitedPE | INV027_PhaseWireShortCircuitedPE | INV027 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV027_PowerLimitationActiveGridCommand | INV027_PowerLimitationActiveGridCommand | INV027 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV027_StringReverseConnection | INV027_StringReverseConnection | INV027 | Inverter | String Reverse Connection | Yes
ALM_INV027_StringReversePolarity | INV027_StringReversePolarity | INV027 | Inverter | String Reverse Polarity | Yes
ALM_INV027_TransientACOvervoltage | INV027_TransientACOvervoltage | INV027 | Inverter | Transient AC Overvoltage | Yes
ALM_INV027_WarningActive | INV027_WarningActive | INV027 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV028_ACOvervoltage | INV028_ACOvervoltage | INV028 | Inverter | AC Overvoltage | Yes
ALM_INV028_ACUndervoltage | INV028_ACUndervoltage | INV028 | Inverter | AC Undervoltage | Yes
ALM_INV028_AFCISelfCheckFailure | INV028_AFCISelfCheckFailure | INV028 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV028_AbnormalGrounding | INV028_AbnormalGrounding | INV028 | Inverter | Abnormal Grounding | Yes
ALM_INV028_AbnormalPVModuleConfiguration | INV028_AbnormalPVModuleConfiguration | INV028 | Inverter | Abnormal PV module configuration | Yes
ALM_INV028_AbnormalResidualCurrent | INV028_AbnormalResidualCurrent | INV028 | Inverter | Abnormal Residual Current | Yes
ALM_INV028_AbnormalStringPower | INV028_AbnormalStringPower | INV028 | Inverter | Abnormal String Power | Yes
ALM_INV028_ActiveIslanding | INV028_ActiveIslanding | INV028 | Inverter | Active Islanding | Yes
ALM_INV028_BuiltPIDOperationAbnormal | INV028_BuiltPIDOperationAbnormal | INV028 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV028_CabinetOvertemperature | INV028_CabinetOvertemperature | INV028 | Inverter | Cabinet Overtemperature | Yes
ALM_INV028_CommunicationFailure | INV028_CommunicationFailure | INV028 | Inverter | Communication Failure | Yes
ALM_INV028_CommunicationStatus | INV028_CommunicationStatus | INV028 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV028_DCArcFault | INV028_DCArcFault | INV028 | Inverter | DC Arc Fault | Yes
ALM_INV028_DCInsulationFault | INV028_DCInsulationFault | INV028 | Inverter | DC Insulation Fault | Yes
ALM_INV028_DCOvervoltage | INV028_DCOvervoltage | INV028 | Inverter | DC Overvoltage | Yes
ALM_INV028_DeviceFault | INV028_DeviceFault | INV028 | Inverter | Device Fault | Yes
ALM_INV028_ExternalFanAbnormal | INV028_ExternalFanAbnormal | INV028 | Inverter | External fan abnormal | Yes
ALM_INV028_FanFailure | INV028_FanFailure | INV028 | Inverter | Fan Failure | Yes
ALM_INV028_Faulty | INV028_Faulty | INV028 | Inverter | Faulty | Yes
ALM_INV028_FaultyMonitoringUnit | INV028_FaultyMonitoringUnit | INV028 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV028_FaultyPowerCollector | INV028_FaultyPowerCollector | INV028 | Inverter | Faulty Power Collector | Yes
ALM_INV028_GeneralFaultTrip | INV028_GeneralFaultTrip | INV028 | Inverter | General Fault Trip | Yes
ALM_INV028_GridConnectionDeratingInverterInternalCauses | INV028_GridConnectionDeratingInverterInternalCauses | INV028 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV028_GridConnectionDeratingPowerRationing | INV028_GridConnectionDeratingPowerRationing | INV028 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV028_GridLoss | INV028_GridLoss | INV028 | Inverter | Grid Loss | Yes
ALM_INV028_GridOverfrequency | INV028_GridOverfrequency | INV028 | Inverter | Grid Overfrequency | Yes
ALM_INV028_GridOvervoltage | INV028_GridOvervoltage | INV028 | Inverter | Grid Overvoltage | Yes
ALM_INV028_GridTiedOffGridControllerAbnormal | INV028_GridTiedOffGridControllerAbnormal | INV028 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV028_GridUnderfrequency | INV028_GridUnderfrequency | INV028 | Inverter | Grid Underfrequency | Yes
ALM_INV028_GridUndervoltage | INV028_GridUndervoltage | INV028 | Inverter | Grid Undervoltage | Yes
ALM_INV028_GroundFault | INV028_GroundFault | INV028 | Inverter | Ground Fault | Yes
ALM_INV028_HighInputStringVoltageGround | INV028_HighInputStringVoltageGround | INV028 | Inverter | High input string voltage to ground | Yes
ALM_INV028_HighStringInputVoltage | INV028_HighStringInputVoltage | INV028 | Inverter | High string input voltage | Yes
ALM_INV028_InverterTripHistoryAvailable | INV028_InverterTripHistoryAvailable | INV028 | Inverter | Inverter Trip History Available | Yes
ALM_INV028_IslandingDetectionStatus | INV028_IslandingDetectionStatus | INV028 | Inverter | Islanding Detection Status | Yes
ALM_INV028_LicenseExpired | INV028_LicenseExpired | INV028 | Inverter | License Expired | Yes
ALM_INV028_LockingStatus | INV028_LockingStatus | INV028 | Inverter | Locking status | Yes
ALM_INV028_LowInsulationResistance | INV028_LowInsulationResistance | INV028 | Inverter | Low Insulation Resistance | Yes
ALM_INV028_OffGridOutputOverload | INV028_OffGridOutputOverload | INV028 | Inverter | Off-grid output overload | Yes
ALM_INV028_OptimizerFault | INV028_OptimizerFault | INV028 | Inverter | Optimizer fault | Yes
ALM_INV028_OutputDCComponentOverhigh | INV028_OutputDCComponentOverhigh | INV028 | Inverter | Output DC Component Overhigh | Yes
ALM_INV028_OutputOvercurrent | INV028_OutputOvercurrent | INV028 | Inverter | Output Overcurrent | Yes
ALM_INV028_PVStringLoss | INV028_PVStringLoss | INV028 | Inverter | PV String Loss | Yes
ALM_INV028_PassiveIslanding | INV028_PassiveIslanding | INV028 | Inverter | Passive Islanding | Yes
ALM_INV028_PeripheralPortShortCircuit | INV028_PeripheralPortShortCircuit | INV028 | Inverter | Peripheral port short circuit | Yes
ALM_INV028_PhaseWireShortCircuitedPE | INV028_PhaseWireShortCircuitedPE | INV028 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV028_PowerLimitationActiveGridCommand | INV028_PowerLimitationActiveGridCommand | INV028 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV028_StringReverseConnection | INV028_StringReverseConnection | INV028 | Inverter | String Reverse Connection | Yes
ALM_INV028_StringReversePolarity | INV028_StringReversePolarity | INV028 | Inverter | String Reverse Polarity | Yes
ALM_INV028_TransientACOvervoltage | INV028_TransientACOvervoltage | INV028 | Inverter | Transient AC Overvoltage | Yes
ALM_INV028_WarningActive | INV028_WarningActive | INV028 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV029_ACOvervoltage | INV029_ACOvervoltage | INV029 | Inverter | AC Overvoltage | Yes
ALM_INV029_ACUndervoltage | INV029_ACUndervoltage | INV029 | Inverter | AC Undervoltage | Yes
ALM_INV029_AFCISelfCheckFailure | INV029_AFCISelfCheckFailure | INV029 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV029_AbnormalGrounding | INV029_AbnormalGrounding | INV029 | Inverter | Abnormal Grounding | Yes
ALM_INV029_AbnormalPVModuleConfiguration | INV029_AbnormalPVModuleConfiguration | INV029 | Inverter | Abnormal PV module configuration | Yes
ALM_INV029_AbnormalResidualCurrent | INV029_AbnormalResidualCurrent | INV029 | Inverter | Abnormal Residual Current | Yes
ALM_INV029_AbnormalStringPower | INV029_AbnormalStringPower | INV029 | Inverter | Abnormal String Power | Yes
ALM_INV029_ActiveIslanding | INV029_ActiveIslanding | INV029 | Inverter | Active Islanding | Yes
ALM_INV029_BuiltPIDOperationAbnormal | INV029_BuiltPIDOperationAbnormal | INV029 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV029_CabinetOvertemperature | INV029_CabinetOvertemperature | INV029 | Inverter | Cabinet Overtemperature | Yes
ALM_INV029_CommunicationFailure | INV029_CommunicationFailure | INV029 | Inverter | Communication Failure | Yes
ALM_INV029_CommunicationStatus | INV029_CommunicationStatus | INV029 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV029_DCArcFault | INV029_DCArcFault | INV029 | Inverter | DC Arc Fault | Yes
ALM_INV029_DCInsulationFault | INV029_DCInsulationFault | INV029 | Inverter | DC Insulation Fault | Yes
ALM_INV029_DCOvervoltage | INV029_DCOvervoltage | INV029 | Inverter | DC Overvoltage | Yes
ALM_INV029_DeviceFault | INV029_DeviceFault | INV029 | Inverter | Device Fault | Yes
ALM_INV029_ExternalFanAbnormal | INV029_ExternalFanAbnormal | INV029 | Inverter | External fan abnormal | Yes
ALM_INV029_FanFailure | INV029_FanFailure | INV029 | Inverter | Fan Failure | Yes
ALM_INV029_Faulty | INV029_Faulty | INV029 | Inverter | Faulty | Yes
ALM_INV029_FaultyMonitoringUnit | INV029_FaultyMonitoringUnit | INV029 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV029_FaultyPowerCollector | INV029_FaultyPowerCollector | INV029 | Inverter | Faulty Power Collector | Yes
ALM_INV029_GeneralFaultTrip | INV029_GeneralFaultTrip | INV029 | Inverter | General Fault Trip | Yes
ALM_INV029_GridConnectionDeratingInverterInternalCauses | INV029_GridConnectionDeratingInverterInternalCauses | INV029 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV029_GridConnectionDeratingPowerRationing | INV029_GridConnectionDeratingPowerRationing | INV029 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV029_GridLoss | INV029_GridLoss | INV029 | Inverter | Grid Loss | Yes
ALM_INV029_GridOverfrequency | INV029_GridOverfrequency | INV029 | Inverter | Grid Overfrequency | Yes
ALM_INV029_GridOvervoltage | INV029_GridOvervoltage | INV029 | Inverter | Grid Overvoltage | Yes
ALM_INV029_GridTiedOffGridControllerAbnormal | INV029_GridTiedOffGridControllerAbnormal | INV029 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV029_GridUnderfrequency | INV029_GridUnderfrequency | INV029 | Inverter | Grid Underfrequency | Yes
ALM_INV029_GridUndervoltage | INV029_GridUndervoltage | INV029 | Inverter | Grid Undervoltage | Yes
ALM_INV029_GroundFault | INV029_GroundFault | INV029 | Inverter | Ground Fault | Yes
ALM_INV029_HighInputStringVoltageGround | INV029_HighInputStringVoltageGround | INV029 | Inverter | High input string voltage to ground | Yes
ALM_INV029_HighStringInputVoltage | INV029_HighStringInputVoltage | INV029 | Inverter | High string input voltage | Yes
ALM_INV029_InverterTripHistoryAvailable | INV029_InverterTripHistoryAvailable | INV029 | Inverter | Inverter Trip History Available | Yes
ALM_INV029_IslandingDetectionStatus | INV029_IslandingDetectionStatus | INV029 | Inverter | Islanding Detection Status | Yes
ALM_INV029_LicenseExpired | INV029_LicenseExpired | INV029 | Inverter | License Expired | Yes
ALM_INV029_LockingStatus | INV029_LockingStatus | INV029 | Inverter | Locking status | Yes
ALM_INV029_LowInsulationResistance | INV029_LowInsulationResistance | INV029 | Inverter | Low Insulation Resistance | Yes
ALM_INV029_OffGridOutputOverload | INV029_OffGridOutputOverload | INV029 | Inverter | Off-grid output overload | Yes
ALM_INV029_OptimizerFault | INV029_OptimizerFault | INV029 | Inverter | Optimizer fault | Yes
ALM_INV029_OutputDCComponentOverhigh | INV029_OutputDCComponentOverhigh | INV029 | Inverter | Output DC Component Overhigh | Yes
ALM_INV029_OutputOvercurrent | INV029_OutputOvercurrent | INV029 | Inverter | Output Overcurrent | Yes
ALM_INV029_PVStringLoss | INV029_PVStringLoss | INV029 | Inverter | PV String Loss | Yes
ALM_INV029_PassiveIslanding | INV029_PassiveIslanding | INV029 | Inverter | Passive Islanding | Yes
ALM_INV029_PeripheralPortShortCircuit | INV029_PeripheralPortShortCircuit | INV029 | Inverter | Peripheral port short circuit | Yes
ALM_INV029_PhaseWireShortCircuitedPE | INV029_PhaseWireShortCircuitedPE | INV029 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV029_PowerLimitationActiveGridCommand | INV029_PowerLimitationActiveGridCommand | INV029 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV029_StringReverseConnection | INV029_StringReverseConnection | INV029 | Inverter | String Reverse Connection | Yes
ALM_INV029_StringReversePolarity | INV029_StringReversePolarity | INV029 | Inverter | String Reverse Polarity | Yes
ALM_INV029_TransientACOvervoltage | INV029_TransientACOvervoltage | INV029 | Inverter | Transient AC Overvoltage | Yes
ALM_INV029_WarningActive | INV029_WarningActive | INV029 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV030_ACOvervoltage | INV030_ACOvervoltage | INV030 | Inverter | AC Overvoltage | Yes
ALM_INV030_ACUndervoltage | INV030_ACUndervoltage | INV030 | Inverter | AC Undervoltage | Yes
ALM_INV030_AFCISelfCheckFailure | INV030_AFCISelfCheckFailure | INV030 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV030_AbnormalGrounding | INV030_AbnormalGrounding | INV030 | Inverter | Abnormal Grounding | Yes
ALM_INV030_AbnormalPVModuleConfiguration | INV030_AbnormalPVModuleConfiguration | INV030 | Inverter | Abnormal PV module configuration | Yes
ALM_INV030_AbnormalResidualCurrent | INV030_AbnormalResidualCurrent | INV030 | Inverter | Abnormal Residual Current | Yes
ALM_INV030_AbnormalStringPower | INV030_AbnormalStringPower | INV030 | Inverter | Abnormal String Power | Yes
ALM_INV030_ActiveIslanding | INV030_ActiveIslanding | INV030 | Inverter | Active Islanding | Yes
ALM_INV030_BuiltPIDOperationAbnormal | INV030_BuiltPIDOperationAbnormal | INV030 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV030_CabinetOvertemperature | INV030_CabinetOvertemperature | INV030 | Inverter | Cabinet Overtemperature | Yes
ALM_INV030_CommunicationFailure | INV030_CommunicationFailure | INV030 | Inverter | Communication Failure | Yes
ALM_INV030_CommunicationStatus | INV030_CommunicationStatus | INV030 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV030_DCArcFault | INV030_DCArcFault | INV030 | Inverter | DC Arc Fault | Yes
ALM_INV030_DCInsulationFault | INV030_DCInsulationFault | INV030 | Inverter | DC Insulation Fault | Yes
ALM_INV030_DCOvervoltage | INV030_DCOvervoltage | INV030 | Inverter | DC Overvoltage | Yes
ALM_INV030_DeviceFault | INV030_DeviceFault | INV030 | Inverter | Device Fault | Yes
ALM_INV030_ExternalFanAbnormal | INV030_ExternalFanAbnormal | INV030 | Inverter | External fan abnormal | Yes
ALM_INV030_FanFailure | INV030_FanFailure | INV030 | Inverter | Fan Failure | Yes
ALM_INV030_Faulty | INV030_Faulty | INV030 | Inverter | Faulty | Yes
ALM_INV030_FaultyMonitoringUnit | INV030_FaultyMonitoringUnit | INV030 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV030_FaultyPowerCollector | INV030_FaultyPowerCollector | INV030 | Inverter | Faulty Power Collector | Yes
ALM_INV030_GeneralFaultTrip | INV030_GeneralFaultTrip | INV030 | Inverter | General Fault Trip | Yes
ALM_INV030_GridConnectionDeratingInverterInternalCauses | INV030_GridConnectionDeratingInverterInternalCauses | INV030 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV030_GridConnectionDeratingPowerRationing | INV030_GridConnectionDeratingPowerRationing | INV030 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV030_GridLoss | INV030_GridLoss | INV030 | Inverter | Grid Loss | Yes
ALM_INV030_GridOverfrequency | INV030_GridOverfrequency | INV030 | Inverter | Grid Overfrequency | Yes
ALM_INV030_GridOvervoltage | INV030_GridOvervoltage | INV030 | Inverter | Grid Overvoltage | Yes
ALM_INV030_GridTiedOffGridControllerAbnormal | INV030_GridTiedOffGridControllerAbnormal | INV030 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV030_GridUnderfrequency | INV030_GridUnderfrequency | INV030 | Inverter | Grid Underfrequency | Yes
ALM_INV030_GridUndervoltage | INV030_GridUndervoltage | INV030 | Inverter | Grid Undervoltage | Yes
ALM_INV030_GroundFault | INV030_GroundFault | INV030 | Inverter | Ground Fault | Yes
ALM_INV030_HighInputStringVoltageGround | INV030_HighInputStringVoltageGround | INV030 | Inverter | High input string voltage to ground | Yes
ALM_INV030_HighStringInputVoltage | INV030_HighStringInputVoltage | INV030 | Inverter | High string input voltage | Yes
ALM_INV030_InverterTripHistoryAvailable | INV030_InverterTripHistoryAvailable | INV030 | Inverter | Inverter Trip History Available | Yes
ALM_INV030_IslandingDetectionStatus | INV030_IslandingDetectionStatus | INV030 | Inverter | Islanding Detection Status | Yes
ALM_INV030_LicenseExpired | INV030_LicenseExpired | INV030 | Inverter | License Expired | Yes
ALM_INV030_LockingStatus | INV030_LockingStatus | INV030 | Inverter | Locking status | Yes
ALM_INV030_LowInsulationResistance | INV030_LowInsulationResistance | INV030 | Inverter | Low Insulation Resistance | Yes
ALM_INV030_OffGridOutputOverload | INV030_OffGridOutputOverload | INV030 | Inverter | Off-grid output overload | Yes
ALM_INV030_OptimizerFault | INV030_OptimizerFault | INV030 | Inverter | Optimizer fault | Yes
ALM_INV030_OutputDCComponentOverhigh | INV030_OutputDCComponentOverhigh | INV030 | Inverter | Output DC Component Overhigh | Yes
ALM_INV030_OutputOvercurrent | INV030_OutputOvercurrent | INV030 | Inverter | Output Overcurrent | Yes
ALM_INV030_PVStringLoss | INV030_PVStringLoss | INV030 | Inverter | PV String Loss | Yes
ALM_INV030_PassiveIslanding | INV030_PassiveIslanding | INV030 | Inverter | Passive Islanding | Yes
ALM_INV030_PeripheralPortShortCircuit | INV030_PeripheralPortShortCircuit | INV030 | Inverter | Peripheral port short circuit | Yes
ALM_INV030_PhaseWireShortCircuitedPE | INV030_PhaseWireShortCircuitedPE | INV030 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV030_PowerLimitationActiveGridCommand | INV030_PowerLimitationActiveGridCommand | INV030 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV030_StringReverseConnection | INV030_StringReverseConnection | INV030 | Inverter | String Reverse Connection | Yes
ALM_INV030_StringReversePolarity | INV030_StringReversePolarity | INV030 | Inverter | String Reverse Polarity | Yes
ALM_INV030_TransientACOvervoltage | INV030_TransientACOvervoltage | INV030 | Inverter | Transient AC Overvoltage | Yes
ALM_INV030_WarningActive | INV030_WarningActive | INV030 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV031_ACOvervoltage | INV031_ACOvervoltage | INV031 | Inverter | AC Overvoltage | Yes
ALM_INV031_ACUndervoltage | INV031_ACUndervoltage | INV031 | Inverter | AC Undervoltage | Yes
ALM_INV031_AFCISelfCheckFailure | INV031_AFCISelfCheckFailure | INV031 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV031_AbnormalGrounding | INV031_AbnormalGrounding | INV031 | Inverter | Abnormal Grounding | Yes
ALM_INV031_AbnormalPVModuleConfiguration | INV031_AbnormalPVModuleConfiguration | INV031 | Inverter | Abnormal PV module configuration | Yes
ALM_INV031_AbnormalResidualCurrent | INV031_AbnormalResidualCurrent | INV031 | Inverter | Abnormal Residual Current | Yes
ALM_INV031_AbnormalStringPower | INV031_AbnormalStringPower | INV031 | Inverter | Abnormal String Power | Yes
ALM_INV031_ActiveIslanding | INV031_ActiveIslanding | INV031 | Inverter | Active Islanding | Yes
ALM_INV031_BuiltPIDOperationAbnormal | INV031_BuiltPIDOperationAbnormal | INV031 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV031_CabinetOvertemperature | INV031_CabinetOvertemperature | INV031 | Inverter | Cabinet Overtemperature | Yes
ALM_INV031_CommunicationFailure | INV031_CommunicationFailure | INV031 | Inverter | Communication Failure | Yes
ALM_INV031_CommunicationStatus | INV031_CommunicationStatus | INV031 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV031_DCArcFault | INV031_DCArcFault | INV031 | Inverter | DC Arc Fault | Yes
ALM_INV031_DCInsulationFault | INV031_DCInsulationFault | INV031 | Inverter | DC Insulation Fault | Yes
ALM_INV031_DCOvervoltage | INV031_DCOvervoltage | INV031 | Inverter | DC Overvoltage | Yes
ALM_INV031_DeviceFault | INV031_DeviceFault | INV031 | Inverter | Device Fault | Yes
ALM_INV031_ExternalFanAbnormal | INV031_ExternalFanAbnormal | INV031 | Inverter | External fan abnormal | Yes
ALM_INV031_FanFailure | INV031_FanFailure | INV031 | Inverter | Fan Failure | Yes
ALM_INV031_Faulty | INV031_Faulty | INV031 | Inverter | Faulty | Yes
ALM_INV031_FaultyMonitoringUnit | INV031_FaultyMonitoringUnit | INV031 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV031_FaultyPowerCollector | INV031_FaultyPowerCollector | INV031 | Inverter | Faulty Power Collector | Yes
ALM_INV031_GeneralFaultTrip | INV031_GeneralFaultTrip | INV031 | Inverter | General Fault Trip | Yes
ALM_INV031_GridConnectionDeratingInverterInternalCauses | INV031_GridConnectionDeratingInverterInternalCauses | INV031 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV031_GridConnectionDeratingPowerRationing | INV031_GridConnectionDeratingPowerRationing | INV031 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV031_GridLoss | INV031_GridLoss | INV031 | Inverter | Grid Loss | Yes
ALM_INV031_GridOverfrequency | INV031_GridOverfrequency | INV031 | Inverter | Grid Overfrequency | Yes
ALM_INV031_GridOvervoltage | INV031_GridOvervoltage | INV031 | Inverter | Grid Overvoltage | Yes
ALM_INV031_GridTiedOffGridControllerAbnormal | INV031_GridTiedOffGridControllerAbnormal | INV031 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV031_GridUnderfrequency | INV031_GridUnderfrequency | INV031 | Inverter | Grid Underfrequency | Yes
ALM_INV031_GridUndervoltage | INV031_GridUndervoltage | INV031 | Inverter | Grid Undervoltage | Yes
ALM_INV031_GroundFault | INV031_GroundFault | INV031 | Inverter | Ground Fault | Yes
ALM_INV031_HighInputStringVoltageGround | INV031_HighInputStringVoltageGround | INV031 | Inverter | High input string voltage to ground | Yes
ALM_INV031_HighStringInputVoltage | INV031_HighStringInputVoltage | INV031 | Inverter | High string input voltage | Yes
ALM_INV031_InverterTripHistoryAvailable | INV031_InverterTripHistoryAvailable | INV031 | Inverter | Inverter Trip History Available | Yes
ALM_INV031_IslandingDetectionStatus | INV031_IslandingDetectionStatus | INV031 | Inverter | Islanding Detection Status | Yes
ALM_INV031_LicenseExpired | INV031_LicenseExpired | INV031 | Inverter | License Expired | Yes
ALM_INV031_LockingStatus | INV031_LockingStatus | INV031 | Inverter | Locking status | Yes
ALM_INV031_LowInsulationResistance | INV031_LowInsulationResistance | INV031 | Inverter | Low Insulation Resistance | Yes
ALM_INV031_OffGridOutputOverload | INV031_OffGridOutputOverload | INV031 | Inverter | Off-grid output overload | Yes
ALM_INV031_OptimizerFault | INV031_OptimizerFault | INV031 | Inverter | Optimizer fault | Yes
ALM_INV031_OutputDCComponentOverhigh | INV031_OutputDCComponentOverhigh | INV031 | Inverter | Output DC Component Overhigh | Yes
ALM_INV031_OutputOvercurrent | INV031_OutputOvercurrent | INV031 | Inverter | Output Overcurrent | Yes
ALM_INV031_PVStringLoss | INV031_PVStringLoss | INV031 | Inverter | PV String Loss | Yes
ALM_INV031_PassiveIslanding | INV031_PassiveIslanding | INV031 | Inverter | Passive Islanding | Yes
ALM_INV031_PeripheralPortShortCircuit | INV031_PeripheralPortShortCircuit | INV031 | Inverter | Peripheral port short circuit | Yes
ALM_INV031_PhaseWireShortCircuitedPE | INV031_PhaseWireShortCircuitedPE | INV031 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV031_PowerLimitationActiveGridCommand | INV031_PowerLimitationActiveGridCommand | INV031 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV031_StringReverseConnection | INV031_StringReverseConnection | INV031 | Inverter | String Reverse Connection | Yes
ALM_INV031_StringReversePolarity | INV031_StringReversePolarity | INV031 | Inverter | String Reverse Polarity | Yes
ALM_INV031_TransientACOvervoltage | INV031_TransientACOvervoltage | INV031 | Inverter | Transient AC Overvoltage | Yes
ALM_INV031_WarningActive | INV031_WarningActive | INV031 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV032_ACOvervoltage | INV032_ACOvervoltage | INV032 | Inverter | AC Overvoltage | Yes
ALM_INV032_ACUndervoltage | INV032_ACUndervoltage | INV032 | Inverter | AC Undervoltage | Yes
ALM_INV032_AFCISelfCheckFailure | INV032_AFCISelfCheckFailure | INV032 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV032_AbnormalGrounding | INV032_AbnormalGrounding | INV032 | Inverter | Abnormal Grounding | Yes
ALM_INV032_AbnormalPVModuleConfiguration | INV032_AbnormalPVModuleConfiguration | INV032 | Inverter | Abnormal PV module configuration | Yes
ALM_INV032_AbnormalResidualCurrent | INV032_AbnormalResidualCurrent | INV032 | Inverter | Abnormal Residual Current | Yes
ALM_INV032_AbnormalStringPower | INV032_AbnormalStringPower | INV032 | Inverter | Abnormal String Power | Yes
ALM_INV032_ActiveIslanding | INV032_ActiveIslanding | INV032 | Inverter | Active Islanding | Yes
ALM_INV032_BuiltPIDOperationAbnormal | INV032_BuiltPIDOperationAbnormal | INV032 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV032_CabinetOvertemperature | INV032_CabinetOvertemperature | INV032 | Inverter | Cabinet Overtemperature | Yes
ALM_INV032_CommunicationFailure | INV032_CommunicationFailure | INV032 | Inverter | Communication Failure | Yes
ALM_INV032_CommunicationStatus | INV032_CommunicationStatus | INV032 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV032_DCArcFault | INV032_DCArcFault | INV032 | Inverter | DC Arc Fault | Yes
ALM_INV032_DCInsulationFault | INV032_DCInsulationFault | INV032 | Inverter | DC Insulation Fault | Yes
ALM_INV032_DCOvervoltage | INV032_DCOvervoltage | INV032 | Inverter | DC Overvoltage | Yes
ALM_INV032_DeviceFault | INV032_DeviceFault | INV032 | Inverter | Device Fault | Yes
ALM_INV032_ExternalFanAbnormal | INV032_ExternalFanAbnormal | INV032 | Inverter | External fan abnormal | Yes
ALM_INV032_FanFailure | INV032_FanFailure | INV032 | Inverter | Fan Failure | Yes
ALM_INV032_Faulty | INV032_Faulty | INV032 | Inverter | Faulty | Yes
ALM_INV032_FaultyMonitoringUnit | INV032_FaultyMonitoringUnit | INV032 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV032_FaultyPowerCollector | INV032_FaultyPowerCollector | INV032 | Inverter | Faulty Power Collector | Yes
ALM_INV032_GeneralFaultTrip | INV032_GeneralFaultTrip | INV032 | Inverter | General Fault Trip | Yes
ALM_INV032_GridConnectionDeratingInverterInternalCauses | INV032_GridConnectionDeratingInverterInternalCauses | INV032 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV032_GridConnectionDeratingPowerRationing | INV032_GridConnectionDeratingPowerRationing | INV032 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV032_GridLoss | INV032_GridLoss | INV032 | Inverter | Grid Loss | Yes
ALM_INV032_GridOverfrequency | INV032_GridOverfrequency | INV032 | Inverter | Grid Overfrequency | Yes
ALM_INV032_GridOvervoltage | INV032_GridOvervoltage | INV032 | Inverter | Grid Overvoltage | Yes
ALM_INV032_GridTiedOffGridControllerAbnormal | INV032_GridTiedOffGridControllerAbnormal | INV032 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV032_GridUnderfrequency | INV032_GridUnderfrequency | INV032 | Inverter | Grid Underfrequency | Yes
ALM_INV032_GridUndervoltage | INV032_GridUndervoltage | INV032 | Inverter | Grid Undervoltage | Yes
ALM_INV032_GroundFault | INV032_GroundFault | INV032 | Inverter | Ground Fault | Yes
ALM_INV032_HighInputStringVoltageGround | INV032_HighInputStringVoltageGround | INV032 | Inverter | High input string voltage to ground | Yes
ALM_INV032_HighStringInputVoltage | INV032_HighStringInputVoltage | INV032 | Inverter | High string input voltage | Yes
ALM_INV032_InverterTripHistoryAvailable | INV032_InverterTripHistoryAvailable | INV032 | Inverter | Inverter Trip History Available | Yes
ALM_INV032_IslandingDetectionStatus | INV032_IslandingDetectionStatus | INV032 | Inverter | Islanding Detection Status | Yes
ALM_INV032_LicenseExpired | INV032_LicenseExpired | INV032 | Inverter | License Expired | Yes
ALM_INV032_LockingStatus | INV032_LockingStatus | INV032 | Inverter | Locking status | Yes
ALM_INV032_LowInsulationResistance | INV032_LowInsulationResistance | INV032 | Inverter | Low Insulation Resistance | Yes
ALM_INV032_OffGridOutputOverload | INV032_OffGridOutputOverload | INV032 | Inverter | Off-grid output overload | Yes
ALM_INV032_OptimizerFault | INV032_OptimizerFault | INV032 | Inverter | Optimizer fault | Yes
ALM_INV032_OutputDCComponentOverhigh | INV032_OutputDCComponentOverhigh | INV032 | Inverter | Output DC Component Overhigh | Yes
ALM_INV032_OutputOvercurrent | INV032_OutputOvercurrent | INV032 | Inverter | Output Overcurrent | Yes
ALM_INV032_PVStringLoss | INV032_PVStringLoss | INV032 | Inverter | PV String Loss | Yes
ALM_INV032_PassiveIslanding | INV032_PassiveIslanding | INV032 | Inverter | Passive Islanding | Yes
ALM_INV032_PeripheralPortShortCircuit | INV032_PeripheralPortShortCircuit | INV032 | Inverter | Peripheral port short circuit | Yes
ALM_INV032_PhaseWireShortCircuitedPE | INV032_PhaseWireShortCircuitedPE | INV032 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV032_PowerLimitationActiveGridCommand | INV032_PowerLimitationActiveGridCommand | INV032 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV032_StringReverseConnection | INV032_StringReverseConnection | INV032 | Inverter | String Reverse Connection | Yes
ALM_INV032_StringReversePolarity | INV032_StringReversePolarity | INV032 | Inverter | String Reverse Polarity | Yes
ALM_INV032_TransientACOvervoltage | INV032_TransientACOvervoltage | INV032 | Inverter | Transient AC Overvoltage | Yes
ALM_INV032_WarningActive | INV032_WarningActive | INV032 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV033_ACOvervoltage | INV033_ACOvervoltage | INV033 | Inverter | AC Overvoltage | Yes
ALM_INV033_ACUndervoltage | INV033_ACUndervoltage | INV033 | Inverter | AC Undervoltage | Yes
ALM_INV033_AFCISelfCheckFailure | INV033_AFCISelfCheckFailure | INV033 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV033_AbnormalGrounding | INV033_AbnormalGrounding | INV033 | Inverter | Abnormal Grounding | Yes
ALM_INV033_AbnormalPVModuleConfiguration | INV033_AbnormalPVModuleConfiguration | INV033 | Inverter | Abnormal PV module configuration | Yes
ALM_INV033_AbnormalResidualCurrent | INV033_AbnormalResidualCurrent | INV033 | Inverter | Abnormal Residual Current | Yes
ALM_INV033_AbnormalStringPower | INV033_AbnormalStringPower | INV033 | Inverter | Abnormal String Power | Yes
ALM_INV033_ActiveIslanding | INV033_ActiveIslanding | INV033 | Inverter | Active Islanding | Yes
ALM_INV033_BuiltPIDOperationAbnormal | INV033_BuiltPIDOperationAbnormal | INV033 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV033_CabinetOvertemperature | INV033_CabinetOvertemperature | INV033 | Inverter | Cabinet Overtemperature | Yes
ALM_INV033_CommunicationFailure | INV033_CommunicationFailure | INV033 | Inverter | Communication Failure | Yes
ALM_INV033_CommunicationStatus | INV033_CommunicationStatus | INV033 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV033_DCArcFault | INV033_DCArcFault | INV033 | Inverter | DC Arc Fault | Yes
ALM_INV033_DCInsulationFault | INV033_DCInsulationFault | INV033 | Inverter | DC Insulation Fault | Yes
ALM_INV033_DCOvervoltage | INV033_DCOvervoltage | INV033 | Inverter | DC Overvoltage | Yes
ALM_INV033_DeviceFault | INV033_DeviceFault | INV033 | Inverter | Device Fault | Yes
ALM_INV033_ExternalFanAbnormal | INV033_ExternalFanAbnormal | INV033 | Inverter | External fan abnormal | Yes
ALM_INV033_FanFailure | INV033_FanFailure | INV033 | Inverter | Fan Failure | Yes
ALM_INV033_Faulty | INV033_Faulty | INV033 | Inverter | Faulty | Yes
ALM_INV033_FaultyMonitoringUnit | INV033_FaultyMonitoringUnit | INV033 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV033_FaultyPowerCollector | INV033_FaultyPowerCollector | INV033 | Inverter | Faulty Power Collector | Yes
ALM_INV033_GeneralFaultTrip | INV033_GeneralFaultTrip | INV033 | Inverter | General Fault Trip | Yes
ALM_INV033_GridConnectionDeratingInverterInternalCauses | INV033_GridConnectionDeratingInverterInternalCauses | INV033 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV033_GridConnectionDeratingPowerRationing | INV033_GridConnectionDeratingPowerRationing | INV033 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV033_GridLoss | INV033_GridLoss | INV033 | Inverter | Grid Loss | Yes
ALM_INV033_GridOverfrequency | INV033_GridOverfrequency | INV033 | Inverter | Grid Overfrequency | Yes
ALM_INV033_GridOvervoltage | INV033_GridOvervoltage | INV033 | Inverter | Grid Overvoltage | Yes
ALM_INV033_GridTiedOffGridControllerAbnormal | INV033_GridTiedOffGridControllerAbnormal | INV033 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV033_GridUnderfrequency | INV033_GridUnderfrequency | INV033 | Inverter | Grid Underfrequency | Yes
ALM_INV033_GridUndervoltage | INV033_GridUndervoltage | INV033 | Inverter | Grid Undervoltage | Yes
ALM_INV033_GroundFault | INV033_GroundFault | INV033 | Inverter | Ground Fault | Yes
ALM_INV033_HighInputStringVoltageGround | INV033_HighInputStringVoltageGround | INV033 | Inverter | High input string voltage to ground | Yes
ALM_INV033_HighStringInputVoltage | INV033_HighStringInputVoltage | INV033 | Inverter | High string input voltage | Yes
ALM_INV033_InverterTripHistoryAvailable | INV033_InverterTripHistoryAvailable | INV033 | Inverter | Inverter Trip History Available | Yes
ALM_INV033_IslandingDetectionStatus | INV033_IslandingDetectionStatus | INV033 | Inverter | Islanding Detection Status | Yes
ALM_INV033_LicenseExpired | INV033_LicenseExpired | INV033 | Inverter | License Expired | Yes
ALM_INV033_LockingStatus | INV033_LockingStatus | INV033 | Inverter | Locking status | Yes
ALM_INV033_LowInsulationResistance | INV033_LowInsulationResistance | INV033 | Inverter | Low Insulation Resistance | Yes
ALM_INV033_OffGridOutputOverload | INV033_OffGridOutputOverload | INV033 | Inverter | Off-grid output overload | Yes
ALM_INV033_OptimizerFault | INV033_OptimizerFault | INV033 | Inverter | Optimizer fault | Yes
ALM_INV033_OutputDCComponentOverhigh | INV033_OutputDCComponentOverhigh | INV033 | Inverter | Output DC Component Overhigh | Yes
ALM_INV033_OutputOvercurrent | INV033_OutputOvercurrent | INV033 | Inverter | Output Overcurrent | Yes
ALM_INV033_PVStringLoss | INV033_PVStringLoss | INV033 | Inverter | PV String Loss | Yes
ALM_INV033_PassiveIslanding | INV033_PassiveIslanding | INV033 | Inverter | Passive Islanding | Yes
ALM_INV033_PeripheralPortShortCircuit | INV033_PeripheralPortShortCircuit | INV033 | Inverter | Peripheral port short circuit | Yes
ALM_INV033_PhaseWireShortCircuitedPE | INV033_PhaseWireShortCircuitedPE | INV033 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV033_PowerLimitationActiveGridCommand | INV033_PowerLimitationActiveGridCommand | INV033 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV033_StringReverseConnection | INV033_StringReverseConnection | INV033 | Inverter | String Reverse Connection | Yes
ALM_INV033_StringReversePolarity | INV033_StringReversePolarity | INV033 | Inverter | String Reverse Polarity | Yes
ALM_INV033_TransientACOvervoltage | INV033_TransientACOvervoltage | INV033 | Inverter | Transient AC Overvoltage | Yes
ALM_INV033_WarningActive | INV033_WarningActive | INV033 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV034_ACOvervoltage | INV034_ACOvervoltage | INV034 | Inverter | AC Overvoltage | Yes
ALM_INV034_ACUndervoltage | INV034_ACUndervoltage | INV034 | Inverter | AC Undervoltage | Yes
ALM_INV034_AFCISelfCheckFailure | INV034_AFCISelfCheckFailure | INV034 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV034_AbnormalGrounding | INV034_AbnormalGrounding | INV034 | Inverter | Abnormal Grounding | Yes
ALM_INV034_AbnormalPVModuleConfiguration | INV034_AbnormalPVModuleConfiguration | INV034 | Inverter | Abnormal PV module configuration | Yes
ALM_INV034_AbnormalResidualCurrent | INV034_AbnormalResidualCurrent | INV034 | Inverter | Abnormal Residual Current | Yes
ALM_INV034_AbnormalStringPower | INV034_AbnormalStringPower | INV034 | Inverter | Abnormal String Power | Yes
ALM_INV034_ActiveIslanding | INV034_ActiveIslanding | INV034 | Inverter | Active Islanding | Yes
ALM_INV034_BuiltPIDOperationAbnormal | INV034_BuiltPIDOperationAbnormal | INV034 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV034_CabinetOvertemperature | INV034_CabinetOvertemperature | INV034 | Inverter | Cabinet Overtemperature | Yes
ALM_INV034_CommunicationFailure | INV034_CommunicationFailure | INV034 | Inverter | Communication Failure | Yes
ALM_INV034_CommunicationStatus | INV034_CommunicationStatus | INV034 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV034_DCArcFault | INV034_DCArcFault | INV034 | Inverter | DC Arc Fault | Yes
ALM_INV034_DCInsulationFault | INV034_DCInsulationFault | INV034 | Inverter | DC Insulation Fault | Yes
ALM_INV034_DCOvervoltage | INV034_DCOvervoltage | INV034 | Inverter | DC Overvoltage | Yes
ALM_INV034_DeviceFault | INV034_DeviceFault | INV034 | Inverter | Device Fault | Yes
ALM_INV034_ExternalFanAbnormal | INV034_ExternalFanAbnormal | INV034 | Inverter | External fan abnormal | Yes
ALM_INV034_FanFailure | INV034_FanFailure | INV034 | Inverter | Fan Failure | Yes
ALM_INV034_Faulty | INV034_Faulty | INV034 | Inverter | Faulty | Yes
ALM_INV034_FaultyMonitoringUnit | INV034_FaultyMonitoringUnit | INV034 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV034_FaultyPowerCollector | INV034_FaultyPowerCollector | INV034 | Inverter | Faulty Power Collector | Yes
ALM_INV034_GeneralFaultTrip | INV034_GeneralFaultTrip | INV034 | Inverter | General Fault Trip | Yes
ALM_INV034_GridConnectionDeratingInverterInternalCauses | INV034_GridConnectionDeratingInverterInternalCauses | INV034 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV034_GridConnectionDeratingPowerRationing | INV034_GridConnectionDeratingPowerRationing | INV034 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV034_GridLoss | INV034_GridLoss | INV034 | Inverter | Grid Loss | Yes
ALM_INV034_GridOverfrequency | INV034_GridOverfrequency | INV034 | Inverter | Grid Overfrequency | Yes
ALM_INV034_GridOvervoltage | INV034_GridOvervoltage | INV034 | Inverter | Grid Overvoltage | Yes
ALM_INV034_GridTiedOffGridControllerAbnormal | INV034_GridTiedOffGridControllerAbnormal | INV034 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV034_GridUnderfrequency | INV034_GridUnderfrequency | INV034 | Inverter | Grid Underfrequency | Yes
ALM_INV034_GridUndervoltage | INV034_GridUndervoltage | INV034 | Inverter | Grid Undervoltage | Yes
ALM_INV034_GroundFault | INV034_GroundFault | INV034 | Inverter | Ground Fault | Yes
ALM_INV034_HighInputStringVoltageGround | INV034_HighInputStringVoltageGround | INV034 | Inverter | High input string voltage to ground | Yes
ALM_INV034_HighStringInputVoltage | INV034_HighStringInputVoltage | INV034 | Inverter | High string input voltage | Yes
ALM_INV034_InverterTripHistoryAvailable | INV034_InverterTripHistoryAvailable | INV034 | Inverter | Inverter Trip History Available | Yes
ALM_INV034_IslandingDetectionStatus | INV034_IslandingDetectionStatus | INV034 | Inverter | Islanding Detection Status | Yes
ALM_INV034_LicenseExpired | INV034_LicenseExpired | INV034 | Inverter | License Expired | Yes
ALM_INV034_LockingStatus | INV034_LockingStatus | INV034 | Inverter | Locking status | Yes
ALM_INV034_LowInsulationResistance | INV034_LowInsulationResistance | INV034 | Inverter | Low Insulation Resistance | Yes
ALM_INV034_OffGridOutputOverload | INV034_OffGridOutputOverload | INV034 | Inverter | Off-grid output overload | Yes
ALM_INV034_OptimizerFault | INV034_OptimizerFault | INV034 | Inverter | Optimizer fault | Yes
ALM_INV034_OutputDCComponentOverhigh | INV034_OutputDCComponentOverhigh | INV034 | Inverter | Output DC Component Overhigh | Yes
ALM_INV034_OutputOvercurrent | INV034_OutputOvercurrent | INV034 | Inverter | Output Overcurrent | Yes
ALM_INV034_PVStringLoss | INV034_PVStringLoss | INV034 | Inverter | PV String Loss | Yes
ALM_INV034_PassiveIslanding | INV034_PassiveIslanding | INV034 | Inverter | Passive Islanding | Yes
ALM_INV034_PeripheralPortShortCircuit | INV034_PeripheralPortShortCircuit | INV034 | Inverter | Peripheral port short circuit | Yes
ALM_INV034_PhaseWireShortCircuitedPE | INV034_PhaseWireShortCircuitedPE | INV034 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV034_PowerLimitationActiveGridCommand | INV034_PowerLimitationActiveGridCommand | INV034 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV034_StringReverseConnection | INV034_StringReverseConnection | INV034 | Inverter | String Reverse Connection | Yes
ALM_INV034_StringReversePolarity | INV034_StringReversePolarity | INV034 | Inverter | String Reverse Polarity | Yes
ALM_INV034_TransientACOvervoltage | INV034_TransientACOvervoltage | INV034 | Inverter | Transient AC Overvoltage | Yes
ALM_INV034_WarningActive | INV034_WarningActive | INV034 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV035_ACOvervoltage | INV035_ACOvervoltage | INV035 | Inverter | AC Overvoltage | Yes
ALM_INV035_ACUndervoltage | INV035_ACUndervoltage | INV035 | Inverter | AC Undervoltage | Yes
ALM_INV035_AFCISelfCheckFailure | INV035_AFCISelfCheckFailure | INV035 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV035_AbnormalGrounding | INV035_AbnormalGrounding | INV035 | Inverter | Abnormal Grounding | Yes
ALM_INV035_AbnormalPVModuleConfiguration | INV035_AbnormalPVModuleConfiguration | INV035 | Inverter | Abnormal PV module configuration | Yes
ALM_INV035_AbnormalResidualCurrent | INV035_AbnormalResidualCurrent | INV035 | Inverter | Abnormal Residual Current | Yes
ALM_INV035_AbnormalStringPower | INV035_AbnormalStringPower | INV035 | Inverter | Abnormal String Power | Yes
ALM_INV035_ActiveIslanding | INV035_ActiveIslanding | INV035 | Inverter | Active Islanding | Yes
ALM_INV035_BuiltPIDOperationAbnormal | INV035_BuiltPIDOperationAbnormal | INV035 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV035_CabinetOvertemperature | INV035_CabinetOvertemperature | INV035 | Inverter | Cabinet Overtemperature | Yes
ALM_INV035_CommunicationFailure | INV035_CommunicationFailure | INV035 | Inverter | Communication Failure | Yes
ALM_INV035_CommunicationStatus | INV035_CommunicationStatus | INV035 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV035_DCArcFault | INV035_DCArcFault | INV035 | Inverter | DC Arc Fault | Yes
ALM_INV035_DCInsulationFault | INV035_DCInsulationFault | INV035 | Inverter | DC Insulation Fault | Yes
ALM_INV035_DCOvervoltage | INV035_DCOvervoltage | INV035 | Inverter | DC Overvoltage | Yes
ALM_INV035_DeviceFault | INV035_DeviceFault | INV035 | Inverter | Device Fault | Yes
ALM_INV035_ExternalFanAbnormal | INV035_ExternalFanAbnormal | INV035 | Inverter | External fan abnormal | Yes
ALM_INV035_FanFailure | INV035_FanFailure | INV035 | Inverter | Fan Failure | Yes
ALM_INV035_Faulty | INV035_Faulty | INV035 | Inverter | Faulty | Yes
ALM_INV035_FaultyMonitoringUnit | INV035_FaultyMonitoringUnit | INV035 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV035_FaultyPowerCollector | INV035_FaultyPowerCollector | INV035 | Inverter | Faulty Power Collector | Yes
ALM_INV035_GeneralFaultTrip | INV035_GeneralFaultTrip | INV035 | Inverter | General Fault Trip | Yes
ALM_INV035_GridConnectionDeratingInverterInternalCauses | INV035_GridConnectionDeratingInverterInternalCauses | INV035 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV035_GridConnectionDeratingPowerRationing | INV035_GridConnectionDeratingPowerRationing | INV035 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV035_GridLoss | INV035_GridLoss | INV035 | Inverter | Grid Loss | Yes
ALM_INV035_GridOverfrequency | INV035_GridOverfrequency | INV035 | Inverter | Grid Overfrequency | Yes
ALM_INV035_GridOvervoltage | INV035_GridOvervoltage | INV035 | Inverter | Grid Overvoltage | Yes
ALM_INV035_GridTiedOffGridControllerAbnormal | INV035_GridTiedOffGridControllerAbnormal | INV035 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV035_GridUnderfrequency | INV035_GridUnderfrequency | INV035 | Inverter | Grid Underfrequency | Yes
ALM_INV035_GridUndervoltage | INV035_GridUndervoltage | INV035 | Inverter | Grid Undervoltage | Yes
ALM_INV035_GroundFault | INV035_GroundFault | INV035 | Inverter | Ground Fault | Yes
ALM_INV035_HighInputStringVoltageGround | INV035_HighInputStringVoltageGround | INV035 | Inverter | High input string voltage to ground | Yes
ALM_INV035_HighStringInputVoltage | INV035_HighStringInputVoltage | INV035 | Inverter | High string input voltage | Yes
ALM_INV035_InverterTripHistoryAvailable | INV035_InverterTripHistoryAvailable | INV035 | Inverter | Inverter Trip History Available | Yes
ALM_INV035_IslandingDetectionStatus | INV035_IslandingDetectionStatus | INV035 | Inverter | Islanding Detection Status | Yes
ALM_INV035_LicenseExpired | INV035_LicenseExpired | INV035 | Inverter | License Expired | Yes
ALM_INV035_LockingStatus | INV035_LockingStatus | INV035 | Inverter | Locking status | Yes
ALM_INV035_LowInsulationResistance | INV035_LowInsulationResistance | INV035 | Inverter | Low Insulation Resistance | Yes
ALM_INV035_OffGridOutputOverload | INV035_OffGridOutputOverload | INV035 | Inverter | Off-grid output overload | Yes
ALM_INV035_OptimizerFault | INV035_OptimizerFault | INV035 | Inverter | Optimizer fault | Yes
ALM_INV035_OutputDCComponentOverhigh | INV035_OutputDCComponentOverhigh | INV035 | Inverter | Output DC Component Overhigh | Yes
ALM_INV035_OutputOvercurrent | INV035_OutputOvercurrent | INV035 | Inverter | Output Overcurrent | Yes
ALM_INV035_PVStringLoss | INV035_PVStringLoss | INV035 | Inverter | PV String Loss | Yes
ALM_INV035_PassiveIslanding | INV035_PassiveIslanding | INV035 | Inverter | Passive Islanding | Yes
ALM_INV035_PeripheralPortShortCircuit | INV035_PeripheralPortShortCircuit | INV035 | Inverter | Peripheral port short circuit | Yes
ALM_INV035_PhaseWireShortCircuitedPE | INV035_PhaseWireShortCircuitedPE | INV035 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV035_PowerLimitationActiveGridCommand | INV035_PowerLimitationActiveGridCommand | INV035 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV035_StringReverseConnection | INV035_StringReverseConnection | INV035 | Inverter | String Reverse Connection | Yes
ALM_INV035_StringReversePolarity | INV035_StringReversePolarity | INV035 | Inverter | String Reverse Polarity | Yes
ALM_INV035_TransientACOvervoltage | INV035_TransientACOvervoltage | INV035 | Inverter | Transient AC Overvoltage | Yes
ALM_INV035_WarningActive | INV035_WarningActive | INV035 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV036_ACOvervoltage | INV036_ACOvervoltage | INV036 | Inverter | AC Overvoltage | Yes
ALM_INV036_ACUndervoltage | INV036_ACUndervoltage | INV036 | Inverter | AC Undervoltage | Yes
ALM_INV036_AFCISelfCheckFailure | INV036_AFCISelfCheckFailure | INV036 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV036_AbnormalGrounding | INV036_AbnormalGrounding | INV036 | Inverter | Abnormal Grounding | Yes
ALM_INV036_AbnormalPVModuleConfiguration | INV036_AbnormalPVModuleConfiguration | INV036 | Inverter | Abnormal PV module configuration | Yes
ALM_INV036_AbnormalResidualCurrent | INV036_AbnormalResidualCurrent | INV036 | Inverter | Abnormal Residual Current | Yes
ALM_INV036_AbnormalStringPower | INV036_AbnormalStringPower | INV036 | Inverter | Abnormal String Power | Yes
ALM_INV036_ActiveIslanding | INV036_ActiveIslanding | INV036 | Inverter | Active Islanding | Yes
ALM_INV036_BuiltPIDOperationAbnormal | INV036_BuiltPIDOperationAbnormal | INV036 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV036_CabinetOvertemperature | INV036_CabinetOvertemperature | INV036 | Inverter | Cabinet Overtemperature | Yes
ALM_INV036_CommunicationFailure | INV036_CommunicationFailure | INV036 | Inverter | Communication Failure | Yes
ALM_INV036_CommunicationStatus | INV036_CommunicationStatus | INV036 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV036_DCArcFault | INV036_DCArcFault | INV036 | Inverter | DC Arc Fault | Yes
ALM_INV036_DCInsulationFault | INV036_DCInsulationFault | INV036 | Inverter | DC Insulation Fault | Yes
ALM_INV036_DCOvervoltage | INV036_DCOvervoltage | INV036 | Inverter | DC Overvoltage | Yes
ALM_INV036_DeviceFault | INV036_DeviceFault | INV036 | Inverter | Device Fault | Yes
ALM_INV036_ExternalFanAbnormal | INV036_ExternalFanAbnormal | INV036 | Inverter | External fan abnormal | Yes
ALM_INV036_FanFailure | INV036_FanFailure | INV036 | Inverter | Fan Failure | Yes
ALM_INV036_Faulty | INV036_Faulty | INV036 | Inverter | Faulty | Yes
ALM_INV036_FaultyMonitoringUnit | INV036_FaultyMonitoringUnit | INV036 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV036_FaultyPowerCollector | INV036_FaultyPowerCollector | INV036 | Inverter | Faulty Power Collector | Yes
ALM_INV036_GeneralFaultTrip | INV036_GeneralFaultTrip | INV036 | Inverter | General Fault Trip | Yes
ALM_INV036_GridConnectionDeratingInverterInternalCauses | INV036_GridConnectionDeratingInverterInternalCauses | INV036 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV036_GridConnectionDeratingPowerRationing | INV036_GridConnectionDeratingPowerRationing | INV036 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV036_GridLoss | INV036_GridLoss | INV036 | Inverter | Grid Loss | Yes
ALM_INV036_GridOverfrequency | INV036_GridOverfrequency | INV036 | Inverter | Grid Overfrequency | Yes
ALM_INV036_GridOvervoltage | INV036_GridOvervoltage | INV036 | Inverter | Grid Overvoltage | Yes
ALM_INV036_GridTiedOffGridControllerAbnormal | INV036_GridTiedOffGridControllerAbnormal | INV036 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV036_GridUnderfrequency | INV036_GridUnderfrequency | INV036 | Inverter | Grid Underfrequency | Yes
ALM_INV036_GridUndervoltage | INV036_GridUndervoltage | INV036 | Inverter | Grid Undervoltage | Yes
ALM_INV036_GroundFault | INV036_GroundFault | INV036 | Inverter | Ground Fault | Yes
ALM_INV036_HighInputStringVoltageGround | INV036_HighInputStringVoltageGround | INV036 | Inverter | High input string voltage to ground | Yes
ALM_INV036_HighStringInputVoltage | INV036_HighStringInputVoltage | INV036 | Inverter | High string input voltage | Yes
ALM_INV036_InverterTripHistoryAvailable | INV036_InverterTripHistoryAvailable | INV036 | Inverter | Inverter Trip History Available | Yes
ALM_INV036_IslandingDetectionStatus | INV036_IslandingDetectionStatus | INV036 | Inverter | Islanding Detection Status | Yes
ALM_INV036_LicenseExpired | INV036_LicenseExpired | INV036 | Inverter | License Expired | Yes
ALM_INV036_LockingStatus | INV036_LockingStatus | INV036 | Inverter | Locking status | Yes
ALM_INV036_LowInsulationResistance | INV036_LowInsulationResistance | INV036 | Inverter | Low Insulation Resistance | Yes
ALM_INV036_OffGridOutputOverload | INV036_OffGridOutputOverload | INV036 | Inverter | Off-grid output overload | Yes
ALM_INV036_OptimizerFault | INV036_OptimizerFault | INV036 | Inverter | Optimizer fault | Yes
ALM_INV036_OutputDCComponentOverhigh | INV036_OutputDCComponentOverhigh | INV036 | Inverter | Output DC Component Overhigh | Yes
ALM_INV036_OutputOvercurrent | INV036_OutputOvercurrent | INV036 | Inverter | Output Overcurrent | Yes
ALM_INV036_PVStringLoss | INV036_PVStringLoss | INV036 | Inverter | PV String Loss | Yes
ALM_INV036_PassiveIslanding | INV036_PassiveIslanding | INV036 | Inverter | Passive Islanding | Yes
ALM_INV036_PeripheralPortShortCircuit | INV036_PeripheralPortShortCircuit | INV036 | Inverter | Peripheral port short circuit | Yes
ALM_INV036_PhaseWireShortCircuitedPE | INV036_PhaseWireShortCircuitedPE | INV036 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV036_PowerLimitationActiveGridCommand | INV036_PowerLimitationActiveGridCommand | INV036 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV036_StringReverseConnection | INV036_StringReverseConnection | INV036 | Inverter | String Reverse Connection | Yes
ALM_INV036_StringReversePolarity | INV036_StringReversePolarity | INV036 | Inverter | String Reverse Polarity | Yes
ALM_INV036_TransientACOvervoltage | INV036_TransientACOvervoltage | INV036 | Inverter | Transient AC Overvoltage | Yes
ALM_INV036_WarningActive | INV036_WarningActive | INV036 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV037_ACOvervoltage | INV037_ACOvervoltage | INV037 | Inverter | AC Overvoltage | Yes
ALM_INV037_ACUndervoltage | INV037_ACUndervoltage | INV037 | Inverter | AC Undervoltage | Yes
ALM_INV037_AFCISelfCheckFailure | INV037_AFCISelfCheckFailure | INV037 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV037_AbnormalGrounding | INV037_AbnormalGrounding | INV037 | Inverter | Abnormal Grounding | Yes
ALM_INV037_AbnormalPVModuleConfiguration | INV037_AbnormalPVModuleConfiguration | INV037 | Inverter | Abnormal PV module configuration | Yes
ALM_INV037_AbnormalResidualCurrent | INV037_AbnormalResidualCurrent | INV037 | Inverter | Abnormal Residual Current | Yes
ALM_INV037_AbnormalStringPower | INV037_AbnormalStringPower | INV037 | Inverter | Abnormal String Power | Yes
ALM_INV037_ActiveIslanding | INV037_ActiveIslanding | INV037 | Inverter | Active Islanding | Yes
ALM_INV037_BuiltPIDOperationAbnormal | INV037_BuiltPIDOperationAbnormal | INV037 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV037_CabinetOvertemperature | INV037_CabinetOvertemperature | INV037 | Inverter | Cabinet Overtemperature | Yes
ALM_INV037_CommunicationFailure | INV037_CommunicationFailure | INV037 | Inverter | Communication Failure | Yes
ALM_INV037_CommunicationStatus | INV037_CommunicationStatus | INV037 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV037_DCArcFault | INV037_DCArcFault | INV037 | Inverter | DC Arc Fault | Yes
ALM_INV037_DCInsulationFault | INV037_DCInsulationFault | INV037 | Inverter | DC Insulation Fault | Yes
ALM_INV037_DCOvervoltage | INV037_DCOvervoltage | INV037 | Inverter | DC Overvoltage | Yes
ALM_INV037_DeviceFault | INV037_DeviceFault | INV037 | Inverter | Device Fault | Yes
ALM_INV037_ExternalFanAbnormal | INV037_ExternalFanAbnormal | INV037 | Inverter | External fan abnormal | Yes
ALM_INV037_FanFailure | INV037_FanFailure | INV037 | Inverter | Fan Failure | Yes
ALM_INV037_Faulty | INV037_Faulty | INV037 | Inverter | Faulty | Yes
ALM_INV037_FaultyMonitoringUnit | INV037_FaultyMonitoringUnit | INV037 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV037_FaultyPowerCollector | INV037_FaultyPowerCollector | INV037 | Inverter | Faulty Power Collector | Yes
ALM_INV037_GeneralFaultTrip | INV037_GeneralFaultTrip | INV037 | Inverter | General Fault Trip | Yes
ALM_INV037_GridConnectionDeratingInverterInternalCauses | INV037_GridConnectionDeratingInverterInternalCauses | INV037 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV037_GridConnectionDeratingPowerRationing | INV037_GridConnectionDeratingPowerRationing | INV037 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV037_GridLoss | INV037_GridLoss | INV037 | Inverter | Grid Loss | Yes
ALM_INV037_GridOverfrequency | INV037_GridOverfrequency | INV037 | Inverter | Grid Overfrequency | Yes
ALM_INV037_GridOvervoltage | INV037_GridOvervoltage | INV037 | Inverter | Grid Overvoltage | Yes
ALM_INV037_GridTiedOffGridControllerAbnormal | INV037_GridTiedOffGridControllerAbnormal | INV037 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV037_GridUnderfrequency | INV037_GridUnderfrequency | INV037 | Inverter | Grid Underfrequency | Yes
ALM_INV037_GridUndervoltage | INV037_GridUndervoltage | INV037 | Inverter | Grid Undervoltage | Yes
ALM_INV037_GroundFault | INV037_GroundFault | INV037 | Inverter | Ground Fault | Yes
ALM_INV037_HighInputStringVoltageGround | INV037_HighInputStringVoltageGround | INV037 | Inverter | High input string voltage to ground | Yes
ALM_INV037_HighStringInputVoltage | INV037_HighStringInputVoltage | INV037 | Inverter | High string input voltage | Yes
ALM_INV037_InverterTripHistoryAvailable | INV037_InverterTripHistoryAvailable | INV037 | Inverter | Inverter Trip History Available | Yes
ALM_INV037_IslandingDetectionStatus | INV037_IslandingDetectionStatus | INV037 | Inverter | Islanding Detection Status | Yes
ALM_INV037_LicenseExpired | INV037_LicenseExpired | INV037 | Inverter | License Expired | Yes
ALM_INV037_LockingStatus | INV037_LockingStatus | INV037 | Inverter | Locking status | Yes
ALM_INV037_LowInsulationResistance | INV037_LowInsulationResistance | INV037 | Inverter | Low Insulation Resistance | Yes
ALM_INV037_OffGridOutputOverload | INV037_OffGridOutputOverload | INV037 | Inverter | Off-grid output overload | Yes
ALM_INV037_OptimizerFault | INV037_OptimizerFault | INV037 | Inverter | Optimizer fault | Yes
ALM_INV037_OutputDCComponentOverhigh | INV037_OutputDCComponentOverhigh | INV037 | Inverter | Output DC Component Overhigh | Yes
ALM_INV037_OutputOvercurrent | INV037_OutputOvercurrent | INV037 | Inverter | Output Overcurrent | Yes
ALM_INV037_PVStringLoss | INV037_PVStringLoss | INV037 | Inverter | PV String Loss | Yes
ALM_INV037_PassiveIslanding | INV037_PassiveIslanding | INV037 | Inverter | Passive Islanding | Yes
ALM_INV037_PeripheralPortShortCircuit | INV037_PeripheralPortShortCircuit | INV037 | Inverter | Peripheral port short circuit | Yes
ALM_INV037_PhaseWireShortCircuitedPE | INV037_PhaseWireShortCircuitedPE | INV037 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV037_PowerLimitationActiveGridCommand | INV037_PowerLimitationActiveGridCommand | INV037 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV037_StringReverseConnection | INV037_StringReverseConnection | INV037 | Inverter | String Reverse Connection | Yes
ALM_INV037_StringReversePolarity | INV037_StringReversePolarity | INV037 | Inverter | String Reverse Polarity | Yes
ALM_INV037_TransientACOvervoltage | INV037_TransientACOvervoltage | INV037 | Inverter | Transient AC Overvoltage | Yes
ALM_INV037_WarningActive | INV037_WarningActive | INV037 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV038_ACOvervoltage | INV038_ACOvervoltage | INV038 | Inverter | AC Overvoltage | Yes
ALM_INV038_ACUndervoltage | INV038_ACUndervoltage | INV038 | Inverter | AC Undervoltage | Yes
ALM_INV038_AFCISelfCheckFailure | INV038_AFCISelfCheckFailure | INV038 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV038_AbnormalGrounding | INV038_AbnormalGrounding | INV038 | Inverter | Abnormal Grounding | Yes
ALM_INV038_AbnormalPVModuleConfiguration | INV038_AbnormalPVModuleConfiguration | INV038 | Inverter | Abnormal PV module configuration | Yes
ALM_INV038_AbnormalResidualCurrent | INV038_AbnormalResidualCurrent | INV038 | Inverter | Abnormal Residual Current | Yes
ALM_INV038_AbnormalStringPower | INV038_AbnormalStringPower | INV038 | Inverter | Abnormal String Power | Yes
ALM_INV038_ActiveIslanding | INV038_ActiveIslanding | INV038 | Inverter | Active Islanding | Yes
ALM_INV038_BuiltPIDOperationAbnormal | INV038_BuiltPIDOperationAbnormal | INV038 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV038_CabinetOvertemperature | INV038_CabinetOvertemperature | INV038 | Inverter | Cabinet Overtemperature | Yes
ALM_INV038_CommunicationFailure | INV038_CommunicationFailure | INV038 | Inverter | Communication Failure | Yes
ALM_INV038_CommunicationStatus | INV038_CommunicationStatus | INV038 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV038_DCArcFault | INV038_DCArcFault | INV038 | Inverter | DC Arc Fault | Yes
ALM_INV038_DCInsulationFault | INV038_DCInsulationFault | INV038 | Inverter | DC Insulation Fault | Yes
ALM_INV038_DCOvervoltage | INV038_DCOvervoltage | INV038 | Inverter | DC Overvoltage | Yes
ALM_INV038_DeviceFault | INV038_DeviceFault | INV038 | Inverter | Device Fault | Yes
ALM_INV038_ExternalFanAbnormal | INV038_ExternalFanAbnormal | INV038 | Inverter | External fan abnormal | Yes
ALM_INV038_FanFailure | INV038_FanFailure | INV038 | Inverter | Fan Failure | Yes
ALM_INV038_Faulty | INV038_Faulty | INV038 | Inverter | Faulty | Yes
ALM_INV038_FaultyMonitoringUnit | INV038_FaultyMonitoringUnit | INV038 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV038_FaultyPowerCollector | INV038_FaultyPowerCollector | INV038 | Inverter | Faulty Power Collector | Yes
ALM_INV038_GeneralFaultTrip | INV038_GeneralFaultTrip | INV038 | Inverter | General Fault Trip | Yes
ALM_INV038_GridConnectionDeratingInverterInternalCauses | INV038_GridConnectionDeratingInverterInternalCauses | INV038 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV038_GridConnectionDeratingPowerRationing | INV038_GridConnectionDeratingPowerRationing | INV038 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV038_GridLoss | INV038_GridLoss | INV038 | Inverter | Grid Loss | Yes
ALM_INV038_GridOverfrequency | INV038_GridOverfrequency | INV038 | Inverter | Grid Overfrequency | Yes
ALM_INV038_GridOvervoltage | INV038_GridOvervoltage | INV038 | Inverter | Grid Overvoltage | Yes
ALM_INV038_GridTiedOffGridControllerAbnormal | INV038_GridTiedOffGridControllerAbnormal | INV038 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV038_GridUnderfrequency | INV038_GridUnderfrequency | INV038 | Inverter | Grid Underfrequency | Yes
ALM_INV038_GridUndervoltage | INV038_GridUndervoltage | INV038 | Inverter | Grid Undervoltage | Yes
ALM_INV038_GroundFault | INV038_GroundFault | INV038 | Inverter | Ground Fault | Yes
ALM_INV038_HighInputStringVoltageGround | INV038_HighInputStringVoltageGround | INV038 | Inverter | High input string voltage to ground | Yes
ALM_INV038_HighStringInputVoltage | INV038_HighStringInputVoltage | INV038 | Inverter | High string input voltage | Yes
ALM_INV038_InverterTripHistoryAvailable | INV038_InverterTripHistoryAvailable | INV038 | Inverter | Inverter Trip History Available | Yes
ALM_INV038_IslandingDetectionStatus | INV038_IslandingDetectionStatus | INV038 | Inverter | Islanding Detection Status | Yes
ALM_INV038_LicenseExpired | INV038_LicenseExpired | INV038 | Inverter | License Expired | Yes
ALM_INV038_LockingStatus | INV038_LockingStatus | INV038 | Inverter | Locking status | Yes
ALM_INV038_LowInsulationResistance | INV038_LowInsulationResistance | INV038 | Inverter | Low Insulation Resistance | Yes
ALM_INV038_OffGridOutputOverload | INV038_OffGridOutputOverload | INV038 | Inverter | Off-grid output overload | Yes
ALM_INV038_OptimizerFault | INV038_OptimizerFault | INV038 | Inverter | Optimizer fault | Yes
ALM_INV038_OutputDCComponentOverhigh | INV038_OutputDCComponentOverhigh | INV038 | Inverter | Output DC Component Overhigh | Yes
ALM_INV038_OutputOvercurrent | INV038_OutputOvercurrent | INV038 | Inverter | Output Overcurrent | Yes
ALM_INV038_PVStringLoss | INV038_PVStringLoss | INV038 | Inverter | PV String Loss | Yes
ALM_INV038_PassiveIslanding | INV038_PassiveIslanding | INV038 | Inverter | Passive Islanding | Yes
ALM_INV038_PeripheralPortShortCircuit | INV038_PeripheralPortShortCircuit | INV038 | Inverter | Peripheral port short circuit | Yes
ALM_INV038_PhaseWireShortCircuitedPE | INV038_PhaseWireShortCircuitedPE | INV038 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV038_PowerLimitationActiveGridCommand | INV038_PowerLimitationActiveGridCommand | INV038 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV038_StringReverseConnection | INV038_StringReverseConnection | INV038 | Inverter | String Reverse Connection | Yes
ALM_INV038_StringReversePolarity | INV038_StringReversePolarity | INV038 | Inverter | String Reverse Polarity | Yes
ALM_INV038_TransientACOvervoltage | INV038_TransientACOvervoltage | INV038 | Inverter | Transient AC Overvoltage | Yes
ALM_INV038_WarningActive | INV038_WarningActive | INV038 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV039_ACOvervoltage | INV039_ACOvervoltage | INV039 | Inverter | AC Overvoltage | Yes
ALM_INV039_ACUndervoltage | INV039_ACUndervoltage | INV039 | Inverter | AC Undervoltage | Yes
ALM_INV039_AFCISelfCheckFailure | INV039_AFCISelfCheckFailure | INV039 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV039_AbnormalGrounding | INV039_AbnormalGrounding | INV039 | Inverter | Abnormal Grounding | Yes
ALM_INV039_AbnormalPVModuleConfiguration | INV039_AbnormalPVModuleConfiguration | INV039 | Inverter | Abnormal PV module configuration | Yes
ALM_INV039_AbnormalResidualCurrent | INV039_AbnormalResidualCurrent | INV039 | Inverter | Abnormal Residual Current | Yes
ALM_INV039_AbnormalStringPower | INV039_AbnormalStringPower | INV039 | Inverter | Abnormal String Power | Yes
ALM_INV039_ActiveIslanding | INV039_ActiveIslanding | INV039 | Inverter | Active Islanding | Yes
ALM_INV039_BuiltPIDOperationAbnormal | INV039_BuiltPIDOperationAbnormal | INV039 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV039_CabinetOvertemperature | INV039_CabinetOvertemperature | INV039 | Inverter | Cabinet Overtemperature | Yes
ALM_INV039_CommunicationFailure | INV039_CommunicationFailure | INV039 | Inverter | Communication Failure | Yes
ALM_INV039_CommunicationStatus | INV039_CommunicationStatus | INV039 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV039_DCArcFault | INV039_DCArcFault | INV039 | Inverter | DC Arc Fault | Yes
ALM_INV039_DCInsulationFault | INV039_DCInsulationFault | INV039 | Inverter | DC Insulation Fault | Yes
ALM_INV039_DCOvervoltage | INV039_DCOvervoltage | INV039 | Inverter | DC Overvoltage | Yes
ALM_INV039_DeviceFault | INV039_DeviceFault | INV039 | Inverter | Device Fault | Yes
ALM_INV039_ExternalFanAbnormal | INV039_ExternalFanAbnormal | INV039 | Inverter | External fan abnormal | Yes
ALM_INV039_FanFailure | INV039_FanFailure | INV039 | Inverter | Fan Failure | Yes
ALM_INV039_Faulty | INV039_Faulty | INV039 | Inverter | Faulty | Yes
ALM_INV039_FaultyMonitoringUnit | INV039_FaultyMonitoringUnit | INV039 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV039_FaultyPowerCollector | INV039_FaultyPowerCollector | INV039 | Inverter | Faulty Power Collector | Yes
ALM_INV039_GeneralFaultTrip | INV039_GeneralFaultTrip | INV039 | Inverter | General Fault Trip | Yes
ALM_INV039_GridConnectionDeratingInverterInternalCauses | INV039_GridConnectionDeratingInverterInternalCauses | INV039 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV039_GridConnectionDeratingPowerRationing | INV039_GridConnectionDeratingPowerRationing | INV039 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV039_GridLoss | INV039_GridLoss | INV039 | Inverter | Grid Loss | Yes
ALM_INV039_GridOverfrequency | INV039_GridOverfrequency | INV039 | Inverter | Grid Overfrequency | Yes
ALM_INV039_GridOvervoltage | INV039_GridOvervoltage | INV039 | Inverter | Grid Overvoltage | Yes
ALM_INV039_GridTiedOffGridControllerAbnormal | INV039_GridTiedOffGridControllerAbnormal | INV039 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV039_GridUnderfrequency | INV039_GridUnderfrequency | INV039 | Inverter | Grid Underfrequency | Yes
ALM_INV039_GridUndervoltage | INV039_GridUndervoltage | INV039 | Inverter | Grid Undervoltage | Yes
ALM_INV039_GroundFault | INV039_GroundFault | INV039 | Inverter | Ground Fault | Yes
ALM_INV039_HighInputStringVoltageGround | INV039_HighInputStringVoltageGround | INV039 | Inverter | High input string voltage to ground | Yes
ALM_INV039_HighStringInputVoltage | INV039_HighStringInputVoltage | INV039 | Inverter | High string input voltage | Yes
ALM_INV039_InverterTripHistoryAvailable | INV039_InverterTripHistoryAvailable | INV039 | Inverter | Inverter Trip History Available | Yes
ALM_INV039_IslandingDetectionStatus | INV039_IslandingDetectionStatus | INV039 | Inverter | Islanding Detection Status | Yes
ALM_INV039_LicenseExpired | INV039_LicenseExpired | INV039 | Inverter | License Expired | Yes
ALM_INV039_LockingStatus | INV039_LockingStatus | INV039 | Inverter | Locking status | Yes
ALM_INV039_LowInsulationResistance | INV039_LowInsulationResistance | INV039 | Inverter | Low Insulation Resistance | Yes
ALM_INV039_OffGridOutputOverload | INV039_OffGridOutputOverload | INV039 | Inverter | Off-grid output overload | Yes
ALM_INV039_OptimizerFault | INV039_OptimizerFault | INV039 | Inverter | Optimizer fault | Yes
ALM_INV039_OutputDCComponentOverhigh | INV039_OutputDCComponentOverhigh | INV039 | Inverter | Output DC Component Overhigh | Yes
ALM_INV039_OutputOvercurrent | INV039_OutputOvercurrent | INV039 | Inverter | Output Overcurrent | Yes
ALM_INV039_PVStringLoss | INV039_PVStringLoss | INV039 | Inverter | PV String Loss | Yes
ALM_INV039_PassiveIslanding | INV039_PassiveIslanding | INV039 | Inverter | Passive Islanding | Yes
ALM_INV039_PeripheralPortShortCircuit | INV039_PeripheralPortShortCircuit | INV039 | Inverter | Peripheral port short circuit | Yes
ALM_INV039_PhaseWireShortCircuitedPE | INV039_PhaseWireShortCircuitedPE | INV039 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV039_PowerLimitationActiveGridCommand | INV039_PowerLimitationActiveGridCommand | INV039 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV039_StringReverseConnection | INV039_StringReverseConnection | INV039 | Inverter | String Reverse Connection | Yes
ALM_INV039_StringReversePolarity | INV039_StringReversePolarity | INV039 | Inverter | String Reverse Polarity | Yes
ALM_INV039_TransientACOvervoltage | INV039_TransientACOvervoltage | INV039 | Inverter | Transient AC Overvoltage | Yes
ALM_INV039_WarningActive | INV039_WarningActive | INV039 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV040_ACOvervoltage | INV040_ACOvervoltage | INV040 | Inverter | AC Overvoltage | Yes
ALM_INV040_ACUndervoltage | INV040_ACUndervoltage | INV040 | Inverter | AC Undervoltage | Yes
ALM_INV040_AFCISelfCheckFailure | INV040_AFCISelfCheckFailure | INV040 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV040_AbnormalGrounding | INV040_AbnormalGrounding | INV040 | Inverter | Abnormal Grounding | Yes
ALM_INV040_AbnormalPVModuleConfiguration | INV040_AbnormalPVModuleConfiguration | INV040 | Inverter | Abnormal PV module configuration | Yes
ALM_INV040_AbnormalResidualCurrent | INV040_AbnormalResidualCurrent | INV040 | Inverter | Abnormal Residual Current | Yes
ALM_INV040_AbnormalStringPower | INV040_AbnormalStringPower | INV040 | Inverter | Abnormal String Power | Yes
ALM_INV040_ActiveIslanding | INV040_ActiveIslanding | INV040 | Inverter | Active Islanding | Yes
ALM_INV040_BuiltPIDOperationAbnormal | INV040_BuiltPIDOperationAbnormal | INV040 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV040_CabinetOvertemperature | INV040_CabinetOvertemperature | INV040 | Inverter | Cabinet Overtemperature | Yes
ALM_INV040_CommunicationFailure | INV040_CommunicationFailure | INV040 | Inverter | Communication Failure | Yes
ALM_INV040_CommunicationStatus | INV040_CommunicationStatus | INV040 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV040_DCArcFault | INV040_DCArcFault | INV040 | Inverter | DC Arc Fault | Yes
ALM_INV040_DCInsulationFault | INV040_DCInsulationFault | INV040 | Inverter | DC Insulation Fault | Yes
ALM_INV040_DCOvervoltage | INV040_DCOvervoltage | INV040 | Inverter | DC Overvoltage | Yes
ALM_INV040_DeviceFault | INV040_DeviceFault | INV040 | Inverter | Device Fault | Yes
ALM_INV040_ExternalFanAbnormal | INV040_ExternalFanAbnormal | INV040 | Inverter | External fan abnormal | Yes
ALM_INV040_FanFailure | INV040_FanFailure | INV040 | Inverter | Fan Failure | Yes
ALM_INV040_Faulty | INV040_Faulty | INV040 | Inverter | Faulty | Yes
ALM_INV040_FaultyMonitoringUnit | INV040_FaultyMonitoringUnit | INV040 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV040_FaultyPowerCollector | INV040_FaultyPowerCollector | INV040 | Inverter | Faulty Power Collector | Yes
ALM_INV040_GeneralFaultTrip | INV040_GeneralFaultTrip | INV040 | Inverter | General Fault Trip | Yes
ALM_INV040_GridConnectionDeratingInverterInternalCauses | INV040_GridConnectionDeratingInverterInternalCauses | INV040 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV040_GridConnectionDeratingPowerRationing | INV040_GridConnectionDeratingPowerRationing | INV040 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV040_GridLoss | INV040_GridLoss | INV040 | Inverter | Grid Loss | Yes
ALM_INV040_GridOverfrequency | INV040_GridOverfrequency | INV040 | Inverter | Grid Overfrequency | Yes
ALM_INV040_GridOvervoltage | INV040_GridOvervoltage | INV040 | Inverter | Grid Overvoltage | Yes
ALM_INV040_GridTiedOffGridControllerAbnormal | INV040_GridTiedOffGridControllerAbnormal | INV040 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV040_GridUnderfrequency | INV040_GridUnderfrequency | INV040 | Inverter | Grid Underfrequency | Yes
ALM_INV040_GridUndervoltage | INV040_GridUndervoltage | INV040 | Inverter | Grid Undervoltage | Yes
ALM_INV040_GroundFault | INV040_GroundFault | INV040 | Inverter | Ground Fault | Yes
ALM_INV040_HighInputStringVoltageGround | INV040_HighInputStringVoltageGround | INV040 | Inverter | High input string voltage to ground | Yes
ALM_INV040_HighStringInputVoltage | INV040_HighStringInputVoltage | INV040 | Inverter | High string input voltage | Yes
ALM_INV040_InverterTripHistoryAvailable | INV040_InverterTripHistoryAvailable | INV040 | Inverter | Inverter Trip History Available | Yes
ALM_INV040_IslandingDetectionStatus | INV040_IslandingDetectionStatus | INV040 | Inverter | Islanding Detection Status | Yes
ALM_INV040_LicenseExpired | INV040_LicenseExpired | INV040 | Inverter | License Expired | Yes
ALM_INV040_LockingStatus | INV040_LockingStatus | INV040 | Inverter | Locking status | Yes
ALM_INV040_LowInsulationResistance | INV040_LowInsulationResistance | INV040 | Inverter | Low Insulation Resistance | Yes
ALM_INV040_OffGridOutputOverload | INV040_OffGridOutputOverload | INV040 | Inverter | Off-grid output overload | Yes
ALM_INV040_OptimizerFault | INV040_OptimizerFault | INV040 | Inverter | Optimizer fault | Yes
ALM_INV040_OutputDCComponentOverhigh | INV040_OutputDCComponentOverhigh | INV040 | Inverter | Output DC Component Overhigh | Yes
ALM_INV040_OutputOvercurrent | INV040_OutputOvercurrent | INV040 | Inverter | Output Overcurrent | Yes
ALM_INV040_PVStringLoss | INV040_PVStringLoss | INV040 | Inverter | PV String Loss | Yes
ALM_INV040_PassiveIslanding | INV040_PassiveIslanding | INV040 | Inverter | Passive Islanding | Yes
ALM_INV040_PeripheralPortShortCircuit | INV040_PeripheralPortShortCircuit | INV040 | Inverter | Peripheral port short circuit | Yes
ALM_INV040_PhaseWireShortCircuitedPE | INV040_PhaseWireShortCircuitedPE | INV040 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV040_PowerLimitationActiveGridCommand | INV040_PowerLimitationActiveGridCommand | INV040 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV040_StringReverseConnection | INV040_StringReverseConnection | INV040 | Inverter | String Reverse Connection | Yes
ALM_INV040_StringReversePolarity | INV040_StringReversePolarity | INV040 | Inverter | String Reverse Polarity | Yes
ALM_INV040_TransientACOvervoltage | INV040_TransientACOvervoltage | INV040 | Inverter | Transient AC Overvoltage | Yes
ALM_INV040_WarningActive | INV040_WarningActive | INV040 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV041_ACOvervoltage | INV041_ACOvervoltage | INV041 | Inverter | AC Overvoltage | Yes
ALM_INV041_ACUndervoltage | INV041_ACUndervoltage | INV041 | Inverter | AC Undervoltage | Yes
ALM_INV041_AFCISelfCheckFailure | INV041_AFCISelfCheckFailure | INV041 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV041_AbnormalGrounding | INV041_AbnormalGrounding | INV041 | Inverter | Abnormal Grounding | Yes
ALM_INV041_AbnormalPVModuleConfiguration | INV041_AbnormalPVModuleConfiguration | INV041 | Inverter | Abnormal PV module configuration | Yes
ALM_INV041_AbnormalResidualCurrent | INV041_AbnormalResidualCurrent | INV041 | Inverter | Abnormal Residual Current | Yes
ALM_INV041_AbnormalStringPower | INV041_AbnormalStringPower | INV041 | Inverter | Abnormal String Power | Yes
ALM_INV041_ActiveIslanding | INV041_ActiveIslanding | INV041 | Inverter | Active Islanding | Yes
ALM_INV041_BuiltPIDOperationAbnormal | INV041_BuiltPIDOperationAbnormal | INV041 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV041_CabinetOvertemperature | INV041_CabinetOvertemperature | INV041 | Inverter | Cabinet Overtemperature | Yes
ALM_INV041_CommunicationFailure | INV041_CommunicationFailure | INV041 | Inverter | Communication Failure | Yes
ALM_INV041_CommunicationStatus | INV041_CommunicationStatus | INV041 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV041_DCArcFault | INV041_DCArcFault | INV041 | Inverter | DC Arc Fault | Yes
ALM_INV041_DCInsulationFault | INV041_DCInsulationFault | INV041 | Inverter | DC Insulation Fault | Yes
ALM_INV041_DCOvervoltage | INV041_DCOvervoltage | INV041 | Inverter | DC Overvoltage | Yes
ALM_INV041_DeviceFault | INV041_DeviceFault | INV041 | Inverter | Device Fault | Yes
ALM_INV041_ExternalFanAbnormal | INV041_ExternalFanAbnormal | INV041 | Inverter | External fan abnormal | Yes
ALM_INV041_FanFailure | INV041_FanFailure | INV041 | Inverter | Fan Failure | Yes
ALM_INV041_Faulty | INV041_Faulty | INV041 | Inverter | Faulty | Yes
ALM_INV041_FaultyMonitoringUnit | INV041_FaultyMonitoringUnit | INV041 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV041_FaultyPowerCollector | INV041_FaultyPowerCollector | INV041 | Inverter | Faulty Power Collector | Yes
ALM_INV041_GeneralFaultTrip | INV041_GeneralFaultTrip | INV041 | Inverter | General Fault Trip | Yes
ALM_INV041_GridConnectionDeratingInverterInternalCauses | INV041_GridConnectionDeratingInverterInternalCauses | INV041 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV041_GridConnectionDeratingPowerRationing | INV041_GridConnectionDeratingPowerRationing | INV041 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV041_GridLoss | INV041_GridLoss | INV041 | Inverter | Grid Loss | Yes
ALM_INV041_GridOverfrequency | INV041_GridOverfrequency | INV041 | Inverter | Grid Overfrequency | Yes
ALM_INV041_GridOvervoltage | INV041_GridOvervoltage | INV041 | Inverter | Grid Overvoltage | Yes
ALM_INV041_GridTiedOffGridControllerAbnormal | INV041_GridTiedOffGridControllerAbnormal | INV041 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV041_GridUnderfrequency | INV041_GridUnderfrequency | INV041 | Inverter | Grid Underfrequency | Yes
ALM_INV041_GridUndervoltage | INV041_GridUndervoltage | INV041 | Inverter | Grid Undervoltage | Yes
ALM_INV041_GroundFault | INV041_GroundFault | INV041 | Inverter | Ground Fault | Yes
ALM_INV041_HighInputStringVoltageGround | INV041_HighInputStringVoltageGround | INV041 | Inverter | High input string voltage to ground | Yes
ALM_INV041_HighStringInputVoltage | INV041_HighStringInputVoltage | INV041 | Inverter | High string input voltage | Yes
ALM_INV041_InverterTripHistoryAvailable | INV041_InverterTripHistoryAvailable | INV041 | Inverter | Inverter Trip History Available | Yes
ALM_INV041_IslandingDetectionStatus | INV041_IslandingDetectionStatus | INV041 | Inverter | Islanding Detection Status | Yes
ALM_INV041_LicenseExpired | INV041_LicenseExpired | INV041 | Inverter | License Expired | Yes
ALM_INV041_LockingStatus | INV041_LockingStatus | INV041 | Inverter | Locking status | Yes
ALM_INV041_LowInsulationResistance | INV041_LowInsulationResistance | INV041 | Inverter | Low Insulation Resistance | Yes
ALM_INV041_OffGridOutputOverload | INV041_OffGridOutputOverload | INV041 | Inverter | Off-grid output overload | Yes
ALM_INV041_OptimizerFault | INV041_OptimizerFault | INV041 | Inverter | Optimizer fault | Yes
ALM_INV041_OutputDCComponentOverhigh | INV041_OutputDCComponentOverhigh | INV041 | Inverter | Output DC Component Overhigh | Yes
ALM_INV041_OutputOvercurrent | INV041_OutputOvercurrent | INV041 | Inverter | Output Overcurrent | Yes
ALM_INV041_PVStringLoss | INV041_PVStringLoss | INV041 | Inverter | PV String Loss | Yes
ALM_INV041_PassiveIslanding | INV041_PassiveIslanding | INV041 | Inverter | Passive Islanding | Yes
ALM_INV041_PeripheralPortShortCircuit | INV041_PeripheralPortShortCircuit | INV041 | Inverter | Peripheral port short circuit | Yes
ALM_INV041_PhaseWireShortCircuitedPE | INV041_PhaseWireShortCircuitedPE | INV041 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV041_PowerLimitationActiveGridCommand | INV041_PowerLimitationActiveGridCommand | INV041 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV041_StringReverseConnection | INV041_StringReverseConnection | INV041 | Inverter | String Reverse Connection | Yes
ALM_INV041_StringReversePolarity | INV041_StringReversePolarity | INV041 | Inverter | String Reverse Polarity | Yes
ALM_INV041_TransientACOvervoltage | INV041_TransientACOvervoltage | INV041 | Inverter | Transient AC Overvoltage | Yes
ALM_INV041_WarningActive | INV041_WarningActive | INV041 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV042_ACOvervoltage | INV042_ACOvervoltage | INV042 | Inverter | AC Overvoltage | Yes
ALM_INV042_ACUndervoltage | INV042_ACUndervoltage | INV042 | Inverter | AC Undervoltage | Yes
ALM_INV042_AFCISelfCheckFailure | INV042_AFCISelfCheckFailure | INV042 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV042_AbnormalGrounding | INV042_AbnormalGrounding | INV042 | Inverter | Abnormal Grounding | Yes
ALM_INV042_AbnormalPVModuleConfiguration | INV042_AbnormalPVModuleConfiguration | INV042 | Inverter | Abnormal PV module configuration | Yes
ALM_INV042_AbnormalResidualCurrent | INV042_AbnormalResidualCurrent | INV042 | Inverter | Abnormal Residual Current | Yes
ALM_INV042_AbnormalStringPower | INV042_AbnormalStringPower | INV042 | Inverter | Abnormal String Power | Yes
ALM_INV042_ActiveIslanding | INV042_ActiveIslanding | INV042 | Inverter | Active Islanding | Yes
ALM_INV042_BuiltPIDOperationAbnormal | INV042_BuiltPIDOperationAbnormal | INV042 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV042_CabinetOvertemperature | INV042_CabinetOvertemperature | INV042 | Inverter | Cabinet Overtemperature | Yes
ALM_INV042_CommunicationFailure | INV042_CommunicationFailure | INV042 | Inverter | Communication Failure | Yes
ALM_INV042_CommunicationStatus | INV042_CommunicationStatus | INV042 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV042_DCArcFault | INV042_DCArcFault | INV042 | Inverter | DC Arc Fault | Yes
ALM_INV042_DCInsulationFault | INV042_DCInsulationFault | INV042 | Inverter | DC Insulation Fault | Yes
ALM_INV042_DCOvervoltage | INV042_DCOvervoltage | INV042 | Inverter | DC Overvoltage | Yes
ALM_INV042_DeviceFault | INV042_DeviceFault | INV042 | Inverter | Device Fault | Yes
ALM_INV042_ExternalFanAbnormal | INV042_ExternalFanAbnormal | INV042 | Inverter | External fan abnormal | Yes
ALM_INV042_FanFailure | INV042_FanFailure | INV042 | Inverter | Fan Failure | Yes
ALM_INV042_Faulty | INV042_Faulty | INV042 | Inverter | Faulty | Yes
ALM_INV042_FaultyMonitoringUnit | INV042_FaultyMonitoringUnit | INV042 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV042_FaultyPowerCollector | INV042_FaultyPowerCollector | INV042 | Inverter | Faulty Power Collector | Yes
ALM_INV042_GeneralFaultTrip | INV042_GeneralFaultTrip | INV042 | Inverter | General Fault Trip | Yes
ALM_INV042_GridConnectionDeratingInverterInternalCauses | INV042_GridConnectionDeratingInverterInternalCauses | INV042 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV042_GridConnectionDeratingPowerRationing | INV042_GridConnectionDeratingPowerRationing | INV042 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV042_GridLoss | INV042_GridLoss | INV042 | Inverter | Grid Loss | Yes
ALM_INV042_GridOverfrequency | INV042_GridOverfrequency | INV042 | Inverter | Grid Overfrequency | Yes
ALM_INV042_GridOvervoltage | INV042_GridOvervoltage | INV042 | Inverter | Grid Overvoltage | Yes
ALM_INV042_GridTiedOffGridControllerAbnormal | INV042_GridTiedOffGridControllerAbnormal | INV042 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV042_GridUnderfrequency | INV042_GridUnderfrequency | INV042 | Inverter | Grid Underfrequency | Yes
ALM_INV042_GridUndervoltage | INV042_GridUndervoltage | INV042 | Inverter | Grid Undervoltage | Yes
ALM_INV042_GroundFault | INV042_GroundFault | INV042 | Inverter | Ground Fault | Yes
ALM_INV042_HighInputStringVoltageGround | INV042_HighInputStringVoltageGround | INV042 | Inverter | High input string voltage to ground | Yes
ALM_INV042_HighStringInputVoltage | INV042_HighStringInputVoltage | INV042 | Inverter | High string input voltage | Yes
ALM_INV042_InverterTripHistoryAvailable | INV042_InverterTripHistoryAvailable | INV042 | Inverter | Inverter Trip History Available | Yes
ALM_INV042_IslandingDetectionStatus | INV042_IslandingDetectionStatus | INV042 | Inverter | Islanding Detection Status | Yes
ALM_INV042_LicenseExpired | INV042_LicenseExpired | INV042 | Inverter | License Expired | Yes
ALM_INV042_LockingStatus | INV042_LockingStatus | INV042 | Inverter | Locking status | Yes
ALM_INV042_LowInsulationResistance | INV042_LowInsulationResistance | INV042 | Inverter | Low Insulation Resistance | Yes
ALM_INV042_OffGridOutputOverload | INV042_OffGridOutputOverload | INV042 | Inverter | Off-grid output overload | Yes
ALM_INV042_OptimizerFault | INV042_OptimizerFault | INV042 | Inverter | Optimizer fault | Yes
ALM_INV042_OutputDCComponentOverhigh | INV042_OutputDCComponentOverhigh | INV042 | Inverter | Output DC Component Overhigh | Yes
ALM_INV042_OutputOvercurrent | INV042_OutputOvercurrent | INV042 | Inverter | Output Overcurrent | Yes
ALM_INV042_PVStringLoss | INV042_PVStringLoss | INV042 | Inverter | PV String Loss | Yes
ALM_INV042_PassiveIslanding | INV042_PassiveIslanding | INV042 | Inverter | Passive Islanding | Yes
ALM_INV042_PeripheralPortShortCircuit | INV042_PeripheralPortShortCircuit | INV042 | Inverter | Peripheral port short circuit | Yes
ALM_INV042_PhaseWireShortCircuitedPE | INV042_PhaseWireShortCircuitedPE | INV042 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV042_PowerLimitationActiveGridCommand | INV042_PowerLimitationActiveGridCommand | INV042 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV042_StringReverseConnection | INV042_StringReverseConnection | INV042 | Inverter | String Reverse Connection | Yes
ALM_INV042_StringReversePolarity | INV042_StringReversePolarity | INV042 | Inverter | String Reverse Polarity | Yes
ALM_INV042_TransientACOvervoltage | INV042_TransientACOvervoltage | INV042 | Inverter | Transient AC Overvoltage | Yes
ALM_INV042_WarningActive | INV042_WarningActive | INV042 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV043_ACOvervoltage | INV043_ACOvervoltage | INV043 | Inverter | AC Overvoltage | Yes
ALM_INV043_ACUndervoltage | INV043_ACUndervoltage | INV043 | Inverter | AC Undervoltage | Yes
ALM_INV043_AFCISelfCheckFailure | INV043_AFCISelfCheckFailure | INV043 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV043_AbnormalGrounding | INV043_AbnormalGrounding | INV043 | Inverter | Abnormal Grounding | Yes
ALM_INV043_AbnormalPVModuleConfiguration | INV043_AbnormalPVModuleConfiguration | INV043 | Inverter | Abnormal PV module configuration | Yes
ALM_INV043_AbnormalResidualCurrent | INV043_AbnormalResidualCurrent | INV043 | Inverter | Abnormal Residual Current | Yes
ALM_INV043_AbnormalStringPower | INV043_AbnormalStringPower | INV043 | Inverter | Abnormal String Power | Yes
ALM_INV043_ActiveIslanding | INV043_ActiveIslanding | INV043 | Inverter | Active Islanding | Yes
ALM_INV043_BuiltPIDOperationAbnormal | INV043_BuiltPIDOperationAbnormal | INV043 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV043_CabinetOvertemperature | INV043_CabinetOvertemperature | INV043 | Inverter | Cabinet Overtemperature | Yes
ALM_INV043_CommunicationFailure | INV043_CommunicationFailure | INV043 | Inverter | Communication Failure | Yes
ALM_INV043_CommunicationStatus | INV043_CommunicationStatus | INV043 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV043_DCArcFault | INV043_DCArcFault | INV043 | Inverter | DC Arc Fault | Yes
ALM_INV043_DCInsulationFault | INV043_DCInsulationFault | INV043 | Inverter | DC Insulation Fault | Yes
ALM_INV043_DCOvervoltage | INV043_DCOvervoltage | INV043 | Inverter | DC Overvoltage | Yes
ALM_INV043_DeviceFault | INV043_DeviceFault | INV043 | Inverter | Device Fault | Yes
ALM_INV043_ExternalFanAbnormal | INV043_ExternalFanAbnormal | INV043 | Inverter | External fan abnormal | Yes
ALM_INV043_FanFailure | INV043_FanFailure | INV043 | Inverter | Fan Failure | Yes
ALM_INV043_Faulty | INV043_Faulty | INV043 | Inverter | Faulty | Yes
ALM_INV043_FaultyMonitoringUnit | INV043_FaultyMonitoringUnit | INV043 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV043_FaultyPowerCollector | INV043_FaultyPowerCollector | INV043 | Inverter | Faulty Power Collector | Yes
ALM_INV043_GeneralFaultTrip | INV043_GeneralFaultTrip | INV043 | Inverter | General Fault Trip | Yes
ALM_INV043_GridConnectionDeratingInverterInternalCauses | INV043_GridConnectionDeratingInverterInternalCauses | INV043 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV043_GridConnectionDeratingPowerRationing | INV043_GridConnectionDeratingPowerRationing | INV043 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV043_GridLoss | INV043_GridLoss | INV043 | Inverter | Grid Loss | Yes
ALM_INV043_GridOverfrequency | INV043_GridOverfrequency | INV043 | Inverter | Grid Overfrequency | Yes
ALM_INV043_GridOvervoltage | INV043_GridOvervoltage | INV043 | Inverter | Grid Overvoltage | Yes
ALM_INV043_GridTiedOffGridControllerAbnormal | INV043_GridTiedOffGridControllerAbnormal | INV043 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV043_GridUnderfrequency | INV043_GridUnderfrequency | INV043 | Inverter | Grid Underfrequency | Yes
ALM_INV043_GridUndervoltage | INV043_GridUndervoltage | INV043 | Inverter | Grid Undervoltage | Yes
ALM_INV043_GroundFault | INV043_GroundFault | INV043 | Inverter | Ground Fault | Yes
ALM_INV043_HighInputStringVoltageGround | INV043_HighInputStringVoltageGround | INV043 | Inverter | High input string voltage to ground | Yes
ALM_INV043_HighStringInputVoltage | INV043_HighStringInputVoltage | INV043 | Inverter | High string input voltage | Yes
ALM_INV043_InverterTripHistoryAvailable | INV043_InverterTripHistoryAvailable | INV043 | Inverter | Inverter Trip History Available | Yes
ALM_INV043_IslandingDetectionStatus | INV043_IslandingDetectionStatus | INV043 | Inverter | Islanding Detection Status | Yes
ALM_INV043_LicenseExpired | INV043_LicenseExpired | INV043 | Inverter | License Expired | Yes
ALM_INV043_LockingStatus | INV043_LockingStatus | INV043 | Inverter | Locking status | Yes
ALM_INV043_LowInsulationResistance | INV043_LowInsulationResistance | INV043 | Inverter | Low Insulation Resistance | Yes
ALM_INV043_OffGridOutputOverload | INV043_OffGridOutputOverload | INV043 | Inverter | Off-grid output overload | Yes
ALM_INV043_OptimizerFault | INV043_OptimizerFault | INV043 | Inverter | Optimizer fault | Yes
ALM_INV043_OutputDCComponentOverhigh | INV043_OutputDCComponentOverhigh | INV043 | Inverter | Output DC Component Overhigh | Yes
ALM_INV043_OutputOvercurrent | INV043_OutputOvercurrent | INV043 | Inverter | Output Overcurrent | Yes
ALM_INV043_PVStringLoss | INV043_PVStringLoss | INV043 | Inverter | PV String Loss | Yes
ALM_INV043_PassiveIslanding | INV043_PassiveIslanding | INV043 | Inverter | Passive Islanding | Yes
ALM_INV043_PeripheralPortShortCircuit | INV043_PeripheralPortShortCircuit | INV043 | Inverter | Peripheral port short circuit | Yes
ALM_INV043_PhaseWireShortCircuitedPE | INV043_PhaseWireShortCircuitedPE | INV043 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV043_PowerLimitationActiveGridCommand | INV043_PowerLimitationActiveGridCommand | INV043 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV043_StringReverseConnection | INV043_StringReverseConnection | INV043 | Inverter | String Reverse Connection | Yes
ALM_INV043_StringReversePolarity | INV043_StringReversePolarity | INV043 | Inverter | String Reverse Polarity | Yes
ALM_INV043_TransientACOvervoltage | INV043_TransientACOvervoltage | INV043 | Inverter | Transient AC Overvoltage | Yes
ALM_INV043_WarningActive | INV043_WarningActive | INV043 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV044_ACOvervoltage | INV044_ACOvervoltage | INV044 | Inverter | AC Overvoltage | Yes
ALM_INV044_ACUndervoltage | INV044_ACUndervoltage | INV044 | Inverter | AC Undervoltage | Yes
ALM_INV044_AFCISelfCheckFailure | INV044_AFCISelfCheckFailure | INV044 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV044_AbnormalGrounding | INV044_AbnormalGrounding | INV044 | Inverter | Abnormal Grounding | Yes
ALM_INV044_AbnormalPVModuleConfiguration | INV044_AbnormalPVModuleConfiguration | INV044 | Inverter | Abnormal PV module configuration | Yes
ALM_INV044_AbnormalResidualCurrent | INV044_AbnormalResidualCurrent | INV044 | Inverter | Abnormal Residual Current | Yes
ALM_INV044_AbnormalStringPower | INV044_AbnormalStringPower | INV044 | Inverter | Abnormal String Power | Yes
ALM_INV044_ActiveIslanding | INV044_ActiveIslanding | INV044 | Inverter | Active Islanding | Yes
ALM_INV044_BuiltPIDOperationAbnormal | INV044_BuiltPIDOperationAbnormal | INV044 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV044_CabinetOvertemperature | INV044_CabinetOvertemperature | INV044 | Inverter | Cabinet Overtemperature | Yes
ALM_INV044_CommunicationFailure | INV044_CommunicationFailure | INV044 | Inverter | Communication Failure | Yes
ALM_INV044_CommunicationStatus | INV044_CommunicationStatus | INV044 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV044_DCArcFault | INV044_DCArcFault | INV044 | Inverter | DC Arc Fault | Yes
ALM_INV044_DCInsulationFault | INV044_DCInsulationFault | INV044 | Inverter | DC Insulation Fault | Yes
ALM_INV044_DCOvervoltage | INV044_DCOvervoltage | INV044 | Inverter | DC Overvoltage | Yes
ALM_INV044_DeviceFault | INV044_DeviceFault | INV044 | Inverter | Device Fault | Yes
ALM_INV044_ExternalFanAbnormal | INV044_ExternalFanAbnormal | INV044 | Inverter | External fan abnormal | Yes
ALM_INV044_FanFailure | INV044_FanFailure | INV044 | Inverter | Fan Failure | Yes
ALM_INV044_Faulty | INV044_Faulty | INV044 | Inverter | Faulty | Yes
ALM_INV044_FaultyMonitoringUnit | INV044_FaultyMonitoringUnit | INV044 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV044_FaultyPowerCollector | INV044_FaultyPowerCollector | INV044 | Inverter | Faulty Power Collector | Yes
ALM_INV044_GeneralFaultTrip | INV044_GeneralFaultTrip | INV044 | Inverter | General Fault Trip | Yes
ALM_INV044_GridConnectionDeratingInverterInternalCauses | INV044_GridConnectionDeratingInverterInternalCauses | INV044 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV044_GridConnectionDeratingPowerRationing | INV044_GridConnectionDeratingPowerRationing | INV044 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV044_GridLoss | INV044_GridLoss | INV044 | Inverter | Grid Loss | Yes
ALM_INV044_GridOverfrequency | INV044_GridOverfrequency | INV044 | Inverter | Grid Overfrequency | Yes
ALM_INV044_GridOvervoltage | INV044_GridOvervoltage | INV044 | Inverter | Grid Overvoltage | Yes
ALM_INV044_GridTiedOffGridControllerAbnormal | INV044_GridTiedOffGridControllerAbnormal | INV044 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV044_GridUnderfrequency | INV044_GridUnderfrequency | INV044 | Inverter | Grid Underfrequency | Yes
ALM_INV044_GridUndervoltage | INV044_GridUndervoltage | INV044 | Inverter | Grid Undervoltage | Yes
ALM_INV044_GroundFault | INV044_GroundFault | INV044 | Inverter | Ground Fault | Yes
ALM_INV044_HighInputStringVoltageGround | INV044_HighInputStringVoltageGround | INV044 | Inverter | High input string voltage to ground | Yes
ALM_INV044_HighStringInputVoltage | INV044_HighStringInputVoltage | INV044 | Inverter | High string input voltage | Yes
ALM_INV044_InverterTripHistoryAvailable | INV044_InverterTripHistoryAvailable | INV044 | Inverter | Inverter Trip History Available | Yes
ALM_INV044_IslandingDetectionStatus | INV044_IslandingDetectionStatus | INV044 | Inverter | Islanding Detection Status | Yes
ALM_INV044_LicenseExpired | INV044_LicenseExpired | INV044 | Inverter | License Expired | Yes
ALM_INV044_LockingStatus | INV044_LockingStatus | INV044 | Inverter | Locking status | Yes
ALM_INV044_LowInsulationResistance | INV044_LowInsulationResistance | INV044 | Inverter | Low Insulation Resistance | Yes
ALM_INV044_OffGridOutputOverload | INV044_OffGridOutputOverload | INV044 | Inverter | Off-grid output overload | Yes
ALM_INV044_OptimizerFault | INV044_OptimizerFault | INV044 | Inverter | Optimizer fault | Yes
ALM_INV044_OutputDCComponentOverhigh | INV044_OutputDCComponentOverhigh | INV044 | Inverter | Output DC Component Overhigh | Yes
ALM_INV044_OutputOvercurrent | INV044_OutputOvercurrent | INV044 | Inverter | Output Overcurrent | Yes
ALM_INV044_PVStringLoss | INV044_PVStringLoss | INV044 | Inverter | PV String Loss | Yes
ALM_INV044_PassiveIslanding | INV044_PassiveIslanding | INV044 | Inverter | Passive Islanding | Yes
ALM_INV044_PeripheralPortShortCircuit | INV044_PeripheralPortShortCircuit | INV044 | Inverter | Peripheral port short circuit | Yes
ALM_INV044_PhaseWireShortCircuitedPE | INV044_PhaseWireShortCircuitedPE | INV044 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV044_PowerLimitationActiveGridCommand | INV044_PowerLimitationActiveGridCommand | INV044 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV044_StringReverseConnection | INV044_StringReverseConnection | INV044 | Inverter | String Reverse Connection | Yes
ALM_INV044_StringReversePolarity | INV044_StringReversePolarity | INV044 | Inverter | String Reverse Polarity | Yes
ALM_INV044_TransientACOvervoltage | INV044_TransientACOvervoltage | INV044 | Inverter | Transient AC Overvoltage | Yes
ALM_INV044_WarningActive | INV044_WarningActive | INV044 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV045_ACOvervoltage | INV045_ACOvervoltage | INV045 | Inverter | AC Overvoltage | Yes
ALM_INV045_ACUndervoltage | INV045_ACUndervoltage | INV045 | Inverter | AC Undervoltage | Yes
ALM_INV045_AFCISelfCheckFailure | INV045_AFCISelfCheckFailure | INV045 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV045_AbnormalGrounding | INV045_AbnormalGrounding | INV045 | Inverter | Abnormal Grounding | Yes
ALM_INV045_AbnormalPVModuleConfiguration | INV045_AbnormalPVModuleConfiguration | INV045 | Inverter | Abnormal PV module configuration | Yes
ALM_INV045_AbnormalResidualCurrent | INV045_AbnormalResidualCurrent | INV045 | Inverter | Abnormal Residual Current | Yes
ALM_INV045_AbnormalStringPower | INV045_AbnormalStringPower | INV045 | Inverter | Abnormal String Power | Yes
ALM_INV045_ActiveIslanding | INV045_ActiveIslanding | INV045 | Inverter | Active Islanding | Yes
ALM_INV045_BuiltPIDOperationAbnormal | INV045_BuiltPIDOperationAbnormal | INV045 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV045_CabinetOvertemperature | INV045_CabinetOvertemperature | INV045 | Inverter | Cabinet Overtemperature | Yes
ALM_INV045_CommunicationFailure | INV045_CommunicationFailure | INV045 | Inverter | Communication Failure | Yes
ALM_INV045_CommunicationStatus | INV045_CommunicationStatus | INV045 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV045_DCArcFault | INV045_DCArcFault | INV045 | Inverter | DC Arc Fault | Yes
ALM_INV045_DCInsulationFault | INV045_DCInsulationFault | INV045 | Inverter | DC Insulation Fault | Yes
ALM_INV045_DCOvervoltage | INV045_DCOvervoltage | INV045 | Inverter | DC Overvoltage | Yes
ALM_INV045_DeviceFault | INV045_DeviceFault | INV045 | Inverter | Device Fault | Yes
ALM_INV045_ExternalFanAbnormal | INV045_ExternalFanAbnormal | INV045 | Inverter | External fan abnormal | Yes
ALM_INV045_FanFailure | INV045_FanFailure | INV045 | Inverter | Fan Failure | Yes
ALM_INV045_Faulty | INV045_Faulty | INV045 | Inverter | Faulty | Yes
ALM_INV045_FaultyMonitoringUnit | INV045_FaultyMonitoringUnit | INV045 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV045_FaultyPowerCollector | INV045_FaultyPowerCollector | INV045 | Inverter | Faulty Power Collector | Yes
ALM_INV045_GeneralFaultTrip | INV045_GeneralFaultTrip | INV045 | Inverter | General Fault Trip | Yes
ALM_INV045_GridConnectionDeratingInverterInternalCauses | INV045_GridConnectionDeratingInverterInternalCauses | INV045 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV045_GridConnectionDeratingPowerRationing | INV045_GridConnectionDeratingPowerRationing | INV045 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV045_GridLoss | INV045_GridLoss | INV045 | Inverter | Grid Loss | Yes
ALM_INV045_GridOverfrequency | INV045_GridOverfrequency | INV045 | Inverter | Grid Overfrequency | Yes
ALM_INV045_GridOvervoltage | INV045_GridOvervoltage | INV045 | Inverter | Grid Overvoltage | Yes
ALM_INV045_GridTiedOffGridControllerAbnormal | INV045_GridTiedOffGridControllerAbnormal | INV045 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV045_GridUnderfrequency | INV045_GridUnderfrequency | INV045 | Inverter | Grid Underfrequency | Yes
ALM_INV045_GridUndervoltage | INV045_GridUndervoltage | INV045 | Inverter | Grid Undervoltage | Yes
ALM_INV045_GroundFault | INV045_GroundFault | INV045 | Inverter | Ground Fault | Yes
ALM_INV045_HighInputStringVoltageGround | INV045_HighInputStringVoltageGround | INV045 | Inverter | High input string voltage to ground | Yes
ALM_INV045_HighStringInputVoltage | INV045_HighStringInputVoltage | INV045 | Inverter | High string input voltage | Yes
ALM_INV045_InverterTripHistoryAvailable | INV045_InverterTripHistoryAvailable | INV045 | Inverter | Inverter Trip History Available | Yes
ALM_INV045_IslandingDetectionStatus | INV045_IslandingDetectionStatus | INV045 | Inverter | Islanding Detection Status | Yes
ALM_INV045_LicenseExpired | INV045_LicenseExpired | INV045 | Inverter | License Expired | Yes
ALM_INV045_LockingStatus | INV045_LockingStatus | INV045 | Inverter | Locking status | Yes
ALM_INV045_LowInsulationResistance | INV045_LowInsulationResistance | INV045 | Inverter | Low Insulation Resistance | Yes
ALM_INV045_OffGridOutputOverload | INV045_OffGridOutputOverload | INV045 | Inverter | Off-grid output overload | Yes
ALM_INV045_OptimizerFault | INV045_OptimizerFault | INV045 | Inverter | Optimizer fault | Yes
ALM_INV045_OutputDCComponentOverhigh | INV045_OutputDCComponentOverhigh | INV045 | Inverter | Output DC Component Overhigh | Yes
ALM_INV045_OutputOvercurrent | INV045_OutputOvercurrent | INV045 | Inverter | Output Overcurrent | Yes
ALM_INV045_PVStringLoss | INV045_PVStringLoss | INV045 | Inverter | PV String Loss | Yes
ALM_INV045_PassiveIslanding | INV045_PassiveIslanding | INV045 | Inverter | Passive Islanding | Yes
ALM_INV045_PeripheralPortShortCircuit | INV045_PeripheralPortShortCircuit | INV045 | Inverter | Peripheral port short circuit | Yes
ALM_INV045_PhaseWireShortCircuitedPE | INV045_PhaseWireShortCircuitedPE | INV045 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV045_PowerLimitationActiveGridCommand | INV045_PowerLimitationActiveGridCommand | INV045 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV045_StringReverseConnection | INV045_StringReverseConnection | INV045 | Inverter | String Reverse Connection | Yes
ALM_INV045_StringReversePolarity | INV045_StringReversePolarity | INV045 | Inverter | String Reverse Polarity | Yes
ALM_INV045_TransientACOvervoltage | INV045_TransientACOvervoltage | INV045 | Inverter | Transient AC Overvoltage | Yes
ALM_INV045_WarningActive | INV045_WarningActive | INV045 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV046_ACOvervoltage | INV046_ACOvervoltage | INV046 | Inverter | AC Overvoltage | Yes
ALM_INV046_ACUndervoltage | INV046_ACUndervoltage | INV046 | Inverter | AC Undervoltage | Yes
ALM_INV046_AFCISelfCheckFailure | INV046_AFCISelfCheckFailure | INV046 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV046_AbnormalGrounding | INV046_AbnormalGrounding | INV046 | Inverter | Abnormal Grounding | Yes
ALM_INV046_AbnormalPVModuleConfiguration | INV046_AbnormalPVModuleConfiguration | INV046 | Inverter | Abnormal PV module configuration | Yes
ALM_INV046_AbnormalResidualCurrent | INV046_AbnormalResidualCurrent | INV046 | Inverter | Abnormal Residual Current | Yes
ALM_INV046_AbnormalStringPower | INV046_AbnormalStringPower | INV046 | Inverter | Abnormal String Power | Yes
ALM_INV046_ActiveIslanding | INV046_ActiveIslanding | INV046 | Inverter | Active Islanding | Yes
ALM_INV046_BuiltPIDOperationAbnormal | INV046_BuiltPIDOperationAbnormal | INV046 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV046_CabinetOvertemperature | INV046_CabinetOvertemperature | INV046 | Inverter | Cabinet Overtemperature | Yes
ALM_INV046_CommunicationFailure | INV046_CommunicationFailure | INV046 | Inverter | Communication Failure | Yes
ALM_INV046_CommunicationStatus | INV046_CommunicationStatus | INV046 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV046_DCArcFault | INV046_DCArcFault | INV046 | Inverter | DC Arc Fault | Yes
ALM_INV046_DCInsulationFault | INV046_DCInsulationFault | INV046 | Inverter | DC Insulation Fault | Yes
ALM_INV046_DCOvervoltage | INV046_DCOvervoltage | INV046 | Inverter | DC Overvoltage | Yes
ALM_INV046_DeviceFault | INV046_DeviceFault | INV046 | Inverter | Device Fault | Yes
ALM_INV046_ExternalFanAbnormal | INV046_ExternalFanAbnormal | INV046 | Inverter | External fan abnormal | Yes
ALM_INV046_FanFailure | INV046_FanFailure | INV046 | Inverter | Fan Failure | Yes
ALM_INV046_Faulty | INV046_Faulty | INV046 | Inverter | Faulty | Yes
ALM_INV046_FaultyMonitoringUnit | INV046_FaultyMonitoringUnit | INV046 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV046_FaultyPowerCollector | INV046_FaultyPowerCollector | INV046 | Inverter | Faulty Power Collector | Yes
ALM_INV046_GeneralFaultTrip | INV046_GeneralFaultTrip | INV046 | Inverter | General Fault Trip | Yes
ALM_INV046_GridConnectionDeratingInverterInternalCauses | INV046_GridConnectionDeratingInverterInternalCauses | INV046 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV046_GridConnectionDeratingPowerRationing | INV046_GridConnectionDeratingPowerRationing | INV046 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV046_GridLoss | INV046_GridLoss | INV046 | Inverter | Grid Loss | Yes
ALM_INV046_GridOverfrequency | INV046_GridOverfrequency | INV046 | Inverter | Grid Overfrequency | Yes
ALM_INV046_GridOvervoltage | INV046_GridOvervoltage | INV046 | Inverter | Grid Overvoltage | Yes
ALM_INV046_GridTiedOffGridControllerAbnormal | INV046_GridTiedOffGridControllerAbnormal | INV046 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV046_GridUnderfrequency | INV046_GridUnderfrequency | INV046 | Inverter | Grid Underfrequency | Yes
ALM_INV046_GridUndervoltage | INV046_GridUndervoltage | INV046 | Inverter | Grid Undervoltage | Yes
ALM_INV046_GroundFault | INV046_GroundFault | INV046 | Inverter | Ground Fault | Yes
ALM_INV046_HighInputStringVoltageGround | INV046_HighInputStringVoltageGround | INV046 | Inverter | High input string voltage to ground | Yes
ALM_INV046_HighStringInputVoltage | INV046_HighStringInputVoltage | INV046 | Inverter | High string input voltage | Yes
ALM_INV046_InverterTripHistoryAvailable | INV046_InverterTripHistoryAvailable | INV046 | Inverter | Inverter Trip History Available | Yes
ALM_INV046_IslandingDetectionStatus | INV046_IslandingDetectionStatus | INV046 | Inverter | Islanding Detection Status | Yes
ALM_INV046_LicenseExpired | INV046_LicenseExpired | INV046 | Inverter | License Expired | Yes
ALM_INV046_LockingStatus | INV046_LockingStatus | INV046 | Inverter | Locking status | Yes
ALM_INV046_LowInsulationResistance | INV046_LowInsulationResistance | INV046 | Inverter | Low Insulation Resistance | Yes
ALM_INV046_OffGridOutputOverload | INV046_OffGridOutputOverload | INV046 | Inverter | Off-grid output overload | Yes
ALM_INV046_OptimizerFault | INV046_OptimizerFault | INV046 | Inverter | Optimizer fault | Yes
ALM_INV046_OutputDCComponentOverhigh | INV046_OutputDCComponentOverhigh | INV046 | Inverter | Output DC Component Overhigh | Yes
ALM_INV046_OutputOvercurrent | INV046_OutputOvercurrent | INV046 | Inverter | Output Overcurrent | Yes
ALM_INV046_PVStringLoss | INV046_PVStringLoss | INV046 | Inverter | PV String Loss | Yes
ALM_INV046_PassiveIslanding | INV046_PassiveIslanding | INV046 | Inverter | Passive Islanding | Yes
ALM_INV046_PeripheralPortShortCircuit | INV046_PeripheralPortShortCircuit | INV046 | Inverter | Peripheral port short circuit | Yes
ALM_INV046_PhaseWireShortCircuitedPE | INV046_PhaseWireShortCircuitedPE | INV046 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV046_PowerLimitationActiveGridCommand | INV046_PowerLimitationActiveGridCommand | INV046 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV046_StringReverseConnection | INV046_StringReverseConnection | INV046 | Inverter | String Reverse Connection | Yes
ALM_INV046_StringReversePolarity | INV046_StringReversePolarity | INV046 | Inverter | String Reverse Polarity | Yes
ALM_INV046_TransientACOvervoltage | INV046_TransientACOvervoltage | INV046 | Inverter | Transient AC Overvoltage | Yes
ALM_INV046_WarningActive | INV046_WarningActive | INV046 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV047_ACOvervoltage | INV047_ACOvervoltage | INV047 | Inverter | AC Overvoltage | Yes
ALM_INV047_ACUndervoltage | INV047_ACUndervoltage | INV047 | Inverter | AC Undervoltage | Yes
ALM_INV047_AFCISelfCheckFailure | INV047_AFCISelfCheckFailure | INV047 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV047_AbnormalGrounding | INV047_AbnormalGrounding | INV047 | Inverter | Abnormal Grounding | Yes
ALM_INV047_AbnormalPVModuleConfiguration | INV047_AbnormalPVModuleConfiguration | INV047 | Inverter | Abnormal PV module configuration | Yes
ALM_INV047_AbnormalResidualCurrent | INV047_AbnormalResidualCurrent | INV047 | Inverter | Abnormal Residual Current | Yes
ALM_INV047_AbnormalStringPower | INV047_AbnormalStringPower | INV047 | Inverter | Abnormal String Power | Yes
ALM_INV047_ActiveIslanding | INV047_ActiveIslanding | INV047 | Inverter | Active Islanding | Yes
ALM_INV047_BuiltPIDOperationAbnormal | INV047_BuiltPIDOperationAbnormal | INV047 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV047_CabinetOvertemperature | INV047_CabinetOvertemperature | INV047 | Inverter | Cabinet Overtemperature | Yes
ALM_INV047_CommunicationFailure | INV047_CommunicationFailure | INV047 | Inverter | Communication Failure | Yes
ALM_INV047_CommunicationStatus | INV047_CommunicationStatus | INV047 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV047_DCArcFault | INV047_DCArcFault | INV047 | Inverter | DC Arc Fault | Yes
ALM_INV047_DCInsulationFault | INV047_DCInsulationFault | INV047 | Inverter | DC Insulation Fault | Yes
ALM_INV047_DCOvervoltage | INV047_DCOvervoltage | INV047 | Inverter | DC Overvoltage | Yes
ALM_INV047_DeviceFault | INV047_DeviceFault | INV047 | Inverter | Device Fault | Yes
ALM_INV047_ExternalFanAbnormal | INV047_ExternalFanAbnormal | INV047 | Inverter | External fan abnormal | Yes
ALM_INV047_FanFailure | INV047_FanFailure | INV047 | Inverter | Fan Failure | Yes
ALM_INV047_Faulty | INV047_Faulty | INV047 | Inverter | Faulty | Yes
ALM_INV047_FaultyMonitoringUnit | INV047_FaultyMonitoringUnit | INV047 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV047_FaultyPowerCollector | INV047_FaultyPowerCollector | INV047 | Inverter | Faulty Power Collector | Yes
ALM_INV047_GeneralFaultTrip | INV047_GeneralFaultTrip | INV047 | Inverter | General Fault Trip | Yes
ALM_INV047_GridConnectionDeratingInverterInternalCauses | INV047_GridConnectionDeratingInverterInternalCauses | INV047 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV047_GridConnectionDeratingPowerRationing | INV047_GridConnectionDeratingPowerRationing | INV047 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV047_GridLoss | INV047_GridLoss | INV047 | Inverter | Grid Loss | Yes
ALM_INV047_GridOverfrequency | INV047_GridOverfrequency | INV047 | Inverter | Grid Overfrequency | Yes
ALM_INV047_GridOvervoltage | INV047_GridOvervoltage | INV047 | Inverter | Grid Overvoltage | Yes
ALM_INV047_GridTiedOffGridControllerAbnormal | INV047_GridTiedOffGridControllerAbnormal | INV047 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV047_GridUnderfrequency | INV047_GridUnderfrequency | INV047 | Inverter | Grid Underfrequency | Yes
ALM_INV047_GridUndervoltage | INV047_GridUndervoltage | INV047 | Inverter | Grid Undervoltage | Yes
ALM_INV047_GroundFault | INV047_GroundFault | INV047 | Inverter | Ground Fault | Yes
ALM_INV047_HighInputStringVoltageGround | INV047_HighInputStringVoltageGround | INV047 | Inverter | High input string voltage to ground | Yes
ALM_INV047_HighStringInputVoltage | INV047_HighStringInputVoltage | INV047 | Inverter | High string input voltage | Yes
ALM_INV047_InverterTripHistoryAvailable | INV047_InverterTripHistoryAvailable | INV047 | Inverter | Inverter Trip History Available | Yes
ALM_INV047_IslandingDetectionStatus | INV047_IslandingDetectionStatus | INV047 | Inverter | Islanding Detection Status | Yes
ALM_INV047_LicenseExpired | INV047_LicenseExpired | INV047 | Inverter | License Expired | Yes
ALM_INV047_LockingStatus | INV047_LockingStatus | INV047 | Inverter | Locking status | Yes
ALM_INV047_LowInsulationResistance | INV047_LowInsulationResistance | INV047 | Inverter | Low Insulation Resistance | Yes
ALM_INV047_OffGridOutputOverload | INV047_OffGridOutputOverload | INV047 | Inverter | Off-grid output overload | Yes
ALM_INV047_OptimizerFault | INV047_OptimizerFault | INV047 | Inverter | Optimizer fault | Yes
ALM_INV047_OutputDCComponentOverhigh | INV047_OutputDCComponentOverhigh | INV047 | Inverter | Output DC Component Overhigh | Yes
ALM_INV047_OutputOvercurrent | INV047_OutputOvercurrent | INV047 | Inverter | Output Overcurrent | Yes
ALM_INV047_PVStringLoss | INV047_PVStringLoss | INV047 | Inverter | PV String Loss | Yes
ALM_INV047_PassiveIslanding | INV047_PassiveIslanding | INV047 | Inverter | Passive Islanding | Yes
ALM_INV047_PeripheralPortShortCircuit | INV047_PeripheralPortShortCircuit | INV047 | Inverter | Peripheral port short circuit | Yes
ALM_INV047_PhaseWireShortCircuitedPE | INV047_PhaseWireShortCircuitedPE | INV047 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV047_PowerLimitationActiveGridCommand | INV047_PowerLimitationActiveGridCommand | INV047 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV047_StringReverseConnection | INV047_StringReverseConnection | INV047 | Inverter | String Reverse Connection | Yes
ALM_INV047_StringReversePolarity | INV047_StringReversePolarity | INV047 | Inverter | String Reverse Polarity | Yes
ALM_INV047_TransientACOvervoltage | INV047_TransientACOvervoltage | INV047 | Inverter | Transient AC Overvoltage | Yes
ALM_INV047_WarningActive | INV047_WarningActive | INV047 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV048_ACOvervoltage | INV048_ACOvervoltage | INV048 | Inverter | AC Overvoltage | Yes
ALM_INV048_ACUndervoltage | INV048_ACUndervoltage | INV048 | Inverter | AC Undervoltage | Yes
ALM_INV048_AFCISelfCheckFailure | INV048_AFCISelfCheckFailure | INV048 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV048_AbnormalGrounding | INV048_AbnormalGrounding | INV048 | Inverter | Abnormal Grounding | Yes
ALM_INV048_AbnormalPVModuleConfiguration | INV048_AbnormalPVModuleConfiguration | INV048 | Inverter | Abnormal PV module configuration | Yes
ALM_INV048_AbnormalResidualCurrent | INV048_AbnormalResidualCurrent | INV048 | Inverter | Abnormal Residual Current | Yes
ALM_INV048_AbnormalStringPower | INV048_AbnormalStringPower | INV048 | Inverter | Abnormal String Power | Yes
ALM_INV048_ActiveIslanding | INV048_ActiveIslanding | INV048 | Inverter | Active Islanding | Yes
ALM_INV048_BuiltPIDOperationAbnormal | INV048_BuiltPIDOperationAbnormal | INV048 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV048_CabinetOvertemperature | INV048_CabinetOvertemperature | INV048 | Inverter | Cabinet Overtemperature | Yes
ALM_INV048_CommunicationFailure | INV048_CommunicationFailure | INV048 | Inverter | Communication Failure | Yes
ALM_INV048_CommunicationStatus | INV048_CommunicationStatus | INV048 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV048_DCArcFault | INV048_DCArcFault | INV048 | Inverter | DC Arc Fault | Yes
ALM_INV048_DCInsulationFault | INV048_DCInsulationFault | INV048 | Inverter | DC Insulation Fault | Yes
ALM_INV048_DCOvervoltage | INV048_DCOvervoltage | INV048 | Inverter | DC Overvoltage | Yes
ALM_INV048_DeviceFault | INV048_DeviceFault | INV048 | Inverter | Device Fault | Yes
ALM_INV048_ExternalFanAbnormal | INV048_ExternalFanAbnormal | INV048 | Inverter | External fan abnormal | Yes
ALM_INV048_FanFailure | INV048_FanFailure | INV048 | Inverter | Fan Failure | Yes
ALM_INV048_Faulty | INV048_Faulty | INV048 | Inverter | Faulty | Yes
ALM_INV048_FaultyMonitoringUnit | INV048_FaultyMonitoringUnit | INV048 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV048_FaultyPowerCollector | INV048_FaultyPowerCollector | INV048 | Inverter | Faulty Power Collector | Yes
ALM_INV048_GeneralFaultTrip | INV048_GeneralFaultTrip | INV048 | Inverter | General Fault Trip | Yes
ALM_INV048_GridConnectionDeratingInverterInternalCauses | INV048_GridConnectionDeratingInverterInternalCauses | INV048 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV048_GridConnectionDeratingPowerRationing | INV048_GridConnectionDeratingPowerRationing | INV048 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV048_GridLoss | INV048_GridLoss | INV048 | Inverter | Grid Loss | Yes
ALM_INV048_GridOverfrequency | INV048_GridOverfrequency | INV048 | Inverter | Grid Overfrequency | Yes
ALM_INV048_GridOvervoltage | INV048_GridOvervoltage | INV048 | Inverter | Grid Overvoltage | Yes
ALM_INV048_GridTiedOffGridControllerAbnormal | INV048_GridTiedOffGridControllerAbnormal | INV048 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV048_GridUnderfrequency | INV048_GridUnderfrequency | INV048 | Inverter | Grid Underfrequency | Yes
ALM_INV048_GridUndervoltage | INV048_GridUndervoltage | INV048 | Inverter | Grid Undervoltage | Yes
ALM_INV048_GroundFault | INV048_GroundFault | INV048 | Inverter | Ground Fault | Yes
ALM_INV048_HighInputStringVoltageGround | INV048_HighInputStringVoltageGround | INV048 | Inverter | High input string voltage to ground | Yes
ALM_INV048_HighStringInputVoltage | INV048_HighStringInputVoltage | INV048 | Inverter | High string input voltage | Yes
ALM_INV048_InverterTripHistoryAvailable | INV048_InverterTripHistoryAvailable | INV048 | Inverter | Inverter Trip History Available | Yes
ALM_INV048_IslandingDetectionStatus | INV048_IslandingDetectionStatus | INV048 | Inverter | Islanding Detection Status | Yes
ALM_INV048_LicenseExpired | INV048_LicenseExpired | INV048 | Inverter | License Expired | Yes
ALM_INV048_LockingStatus | INV048_LockingStatus | INV048 | Inverter | Locking status | Yes
ALM_INV048_LowInsulationResistance | INV048_LowInsulationResistance | INV048 | Inverter | Low Insulation Resistance | Yes
ALM_INV048_OffGridOutputOverload | INV048_OffGridOutputOverload | INV048 | Inverter | Off-grid output overload | Yes
ALM_INV048_OptimizerFault | INV048_OptimizerFault | INV048 | Inverter | Optimizer fault | Yes
ALM_INV048_OutputDCComponentOverhigh | INV048_OutputDCComponentOverhigh | INV048 | Inverter | Output DC Component Overhigh | Yes
ALM_INV048_OutputOvercurrent | INV048_OutputOvercurrent | INV048 | Inverter | Output Overcurrent | Yes
ALM_INV048_PVStringLoss | INV048_PVStringLoss | INV048 | Inverter | PV String Loss | Yes
ALM_INV048_PassiveIslanding | INV048_PassiveIslanding | INV048 | Inverter | Passive Islanding | Yes
ALM_INV048_PeripheralPortShortCircuit | INV048_PeripheralPortShortCircuit | INV048 | Inverter | Peripheral port short circuit | Yes
ALM_INV048_PhaseWireShortCircuitedPE | INV048_PhaseWireShortCircuitedPE | INV048 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV048_PowerLimitationActiveGridCommand | INV048_PowerLimitationActiveGridCommand | INV048 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV048_StringReverseConnection | INV048_StringReverseConnection | INV048 | Inverter | String Reverse Connection | Yes
ALM_INV048_StringReversePolarity | INV048_StringReversePolarity | INV048 | Inverter | String Reverse Polarity | Yes
ALM_INV048_TransientACOvervoltage | INV048_TransientACOvervoltage | INV048 | Inverter | Transient AC Overvoltage | Yes
ALM_INV048_WarningActive | INV048_WarningActive | INV048 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV049_ACOvervoltage | INV049_ACOvervoltage | INV049 | Inverter | AC Overvoltage | Yes
ALM_INV049_ACUndervoltage | INV049_ACUndervoltage | INV049 | Inverter | AC Undervoltage | Yes
ALM_INV049_AFCISelfCheckFailure | INV049_AFCISelfCheckFailure | INV049 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV049_AbnormalGrounding | INV049_AbnormalGrounding | INV049 | Inverter | Abnormal Grounding | Yes
ALM_INV049_AbnormalPVModuleConfiguration | INV049_AbnormalPVModuleConfiguration | INV049 | Inverter | Abnormal PV module configuration | Yes
ALM_INV049_AbnormalResidualCurrent | INV049_AbnormalResidualCurrent | INV049 | Inverter | Abnormal Residual Current | Yes
ALM_INV049_AbnormalStringPower | INV049_AbnormalStringPower | INV049 | Inverter | Abnormal String Power | Yes
ALM_INV049_ActiveIslanding | INV049_ActiveIslanding | INV049 | Inverter | Active Islanding | Yes
ALM_INV049_BuiltPIDOperationAbnormal | INV049_BuiltPIDOperationAbnormal | INV049 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV049_CabinetOvertemperature | INV049_CabinetOvertemperature | INV049 | Inverter | Cabinet Overtemperature | Yes
ALM_INV049_CommunicationFailure | INV049_CommunicationFailure | INV049 | Inverter | Communication Failure | Yes
ALM_INV049_CommunicationStatus | INV049_CommunicationStatus | INV049 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV049_DCArcFault | INV049_DCArcFault | INV049 | Inverter | DC Arc Fault | Yes
ALM_INV049_DCInsulationFault | INV049_DCInsulationFault | INV049 | Inverter | DC Insulation Fault | Yes
ALM_INV049_DCOvervoltage | INV049_DCOvervoltage | INV049 | Inverter | DC Overvoltage | Yes
ALM_INV049_DeviceFault | INV049_DeviceFault | INV049 | Inverter | Device Fault | Yes
ALM_INV049_ExternalFanAbnormal | INV049_ExternalFanAbnormal | INV049 | Inverter | External fan abnormal | Yes
ALM_INV049_FanFailure | INV049_FanFailure | INV049 | Inverter | Fan Failure | Yes
ALM_INV049_Faulty | INV049_Faulty | INV049 | Inverter | Faulty | Yes
ALM_INV049_FaultyMonitoringUnit | INV049_FaultyMonitoringUnit | INV049 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV049_FaultyPowerCollector | INV049_FaultyPowerCollector | INV049 | Inverter | Faulty Power Collector | Yes
ALM_INV049_GeneralFaultTrip | INV049_GeneralFaultTrip | INV049 | Inverter | General Fault Trip | Yes
ALM_INV049_GridConnectionDeratingInverterInternalCauses | INV049_GridConnectionDeratingInverterInternalCauses | INV049 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV049_GridConnectionDeratingPowerRationing | INV049_GridConnectionDeratingPowerRationing | INV049 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV049_GridLoss | INV049_GridLoss | INV049 | Inverter | Grid Loss | Yes
ALM_INV049_GridOverfrequency | INV049_GridOverfrequency | INV049 | Inverter | Grid Overfrequency | Yes
ALM_INV049_GridOvervoltage | INV049_GridOvervoltage | INV049 | Inverter | Grid Overvoltage | Yes
ALM_INV049_GridTiedOffGridControllerAbnormal | INV049_GridTiedOffGridControllerAbnormal | INV049 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV049_GridUnderfrequency | INV049_GridUnderfrequency | INV049 | Inverter | Grid Underfrequency | Yes
ALM_INV049_GridUndervoltage | INV049_GridUndervoltage | INV049 | Inverter | Grid Undervoltage | Yes
ALM_INV049_GroundFault | INV049_GroundFault | INV049 | Inverter | Ground Fault | Yes
ALM_INV049_HighInputStringVoltageGround | INV049_HighInputStringVoltageGround | INV049 | Inverter | High input string voltage to ground | Yes
ALM_INV049_HighStringInputVoltage | INV049_HighStringInputVoltage | INV049 | Inverter | High string input voltage | Yes
ALM_INV049_InverterTripHistoryAvailable | INV049_InverterTripHistoryAvailable | INV049 | Inverter | Inverter Trip History Available | Yes
ALM_INV049_IslandingDetectionStatus | INV049_IslandingDetectionStatus | INV049 | Inverter | Islanding Detection Status | Yes
ALM_INV049_LicenseExpired | INV049_LicenseExpired | INV049 | Inverter | License Expired | Yes
ALM_INV049_LockingStatus | INV049_LockingStatus | INV049 | Inverter | Locking status | Yes
ALM_INV049_LowInsulationResistance | INV049_LowInsulationResistance | INV049 | Inverter | Low Insulation Resistance | Yes
ALM_INV049_OffGridOutputOverload | INV049_OffGridOutputOverload | INV049 | Inverter | Off-grid output overload | Yes
ALM_INV049_OptimizerFault | INV049_OptimizerFault | INV049 | Inverter | Optimizer fault | Yes
ALM_INV049_OutputDCComponentOverhigh | INV049_OutputDCComponentOverhigh | INV049 | Inverter | Output DC Component Overhigh | Yes
ALM_INV049_OutputOvercurrent | INV049_OutputOvercurrent | INV049 | Inverter | Output Overcurrent | Yes
ALM_INV049_PVStringLoss | INV049_PVStringLoss | INV049 | Inverter | PV String Loss | Yes
ALM_INV049_PassiveIslanding | INV049_PassiveIslanding | INV049 | Inverter | Passive Islanding | Yes
ALM_INV049_PeripheralPortShortCircuit | INV049_PeripheralPortShortCircuit | INV049 | Inverter | Peripheral port short circuit | Yes
ALM_INV049_PhaseWireShortCircuitedPE | INV049_PhaseWireShortCircuitedPE | INV049 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV049_PowerLimitationActiveGridCommand | INV049_PowerLimitationActiveGridCommand | INV049 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV049_StringReverseConnection | INV049_StringReverseConnection | INV049 | Inverter | String Reverse Connection | Yes
ALM_INV049_StringReversePolarity | INV049_StringReversePolarity | INV049 | Inverter | String Reverse Polarity | Yes
ALM_INV049_TransientACOvervoltage | INV049_TransientACOvervoltage | INV049 | Inverter | Transient AC Overvoltage | Yes
ALM_INV049_WarningActive | INV049_WarningActive | INV049 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV050_ACOvervoltage | INV050_ACOvervoltage | INV050 | Inverter | AC Overvoltage | Yes
ALM_INV050_ACUndervoltage | INV050_ACUndervoltage | INV050 | Inverter | AC Undervoltage | Yes
ALM_INV050_AFCISelfCheckFailure | INV050_AFCISelfCheckFailure | INV050 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV050_AbnormalGrounding | INV050_AbnormalGrounding | INV050 | Inverter | Abnormal Grounding | Yes
ALM_INV050_AbnormalPVModuleConfiguration | INV050_AbnormalPVModuleConfiguration | INV050 | Inverter | Abnormal PV module configuration | Yes
ALM_INV050_AbnormalResidualCurrent | INV050_AbnormalResidualCurrent | INV050 | Inverter | Abnormal Residual Current | Yes
ALM_INV050_AbnormalStringPower | INV050_AbnormalStringPower | INV050 | Inverter | Abnormal String Power | Yes
ALM_INV050_ActiveIslanding | INV050_ActiveIslanding | INV050 | Inverter | Active Islanding | Yes
ALM_INV050_BuiltPIDOperationAbnormal | INV050_BuiltPIDOperationAbnormal | INV050 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV050_CabinetOvertemperature | INV050_CabinetOvertemperature | INV050 | Inverter | Cabinet Overtemperature | Yes
ALM_INV050_CommunicationFailure | INV050_CommunicationFailure | INV050 | Inverter | Communication Failure | Yes
ALM_INV050_CommunicationStatus | INV050_CommunicationStatus | INV050 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV050_DCArcFault | INV050_DCArcFault | INV050 | Inverter | DC Arc Fault | Yes
ALM_INV050_DCInsulationFault | INV050_DCInsulationFault | INV050 | Inverter | DC Insulation Fault | Yes
ALM_INV050_DCOvervoltage | INV050_DCOvervoltage | INV050 | Inverter | DC Overvoltage | Yes
ALM_INV050_DeviceFault | INV050_DeviceFault | INV050 | Inverter | Device Fault | Yes
ALM_INV050_ExternalFanAbnormal | INV050_ExternalFanAbnormal | INV050 | Inverter | External fan abnormal | Yes
ALM_INV050_FanFailure | INV050_FanFailure | INV050 | Inverter | Fan Failure | Yes
ALM_INV050_Faulty | INV050_Faulty | INV050 | Inverter | Faulty | Yes
ALM_INV050_FaultyMonitoringUnit | INV050_FaultyMonitoringUnit | INV050 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV050_FaultyPowerCollector | INV050_FaultyPowerCollector | INV050 | Inverter | Faulty Power Collector | Yes
ALM_INV050_GeneralFaultTrip | INV050_GeneralFaultTrip | INV050 | Inverter | General Fault Trip | Yes
ALM_INV050_GridConnectionDeratingInverterInternalCauses | INV050_GridConnectionDeratingInverterInternalCauses | INV050 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV050_GridConnectionDeratingPowerRationing | INV050_GridConnectionDeratingPowerRationing | INV050 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV050_GridLoss | INV050_GridLoss | INV050 | Inverter | Grid Loss | Yes
ALM_INV050_GridOverfrequency | INV050_GridOverfrequency | INV050 | Inverter | Grid Overfrequency | Yes
ALM_INV050_GridOvervoltage | INV050_GridOvervoltage | INV050 | Inverter | Grid Overvoltage | Yes
ALM_INV050_GridTiedOffGridControllerAbnormal | INV050_GridTiedOffGridControllerAbnormal | INV050 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV050_GridUnderfrequency | INV050_GridUnderfrequency | INV050 | Inverter | Grid Underfrequency | Yes
ALM_INV050_GridUndervoltage | INV050_GridUndervoltage | INV050 | Inverter | Grid Undervoltage | Yes
ALM_INV050_GroundFault | INV050_GroundFault | INV050 | Inverter | Ground Fault | Yes
ALM_INV050_HighInputStringVoltageGround | INV050_HighInputStringVoltageGround | INV050 | Inverter | High input string voltage to ground | Yes
ALM_INV050_HighStringInputVoltage | INV050_HighStringInputVoltage | INV050 | Inverter | High string input voltage | Yes
ALM_INV050_InverterTripHistoryAvailable | INV050_InverterTripHistoryAvailable | INV050 | Inverter | Inverter Trip History Available | Yes
ALM_INV050_IslandingDetectionStatus | INV050_IslandingDetectionStatus | INV050 | Inverter | Islanding Detection Status | Yes
ALM_INV050_LicenseExpired | INV050_LicenseExpired | INV050 | Inverter | License Expired | Yes
ALM_INV050_LockingStatus | INV050_LockingStatus | INV050 | Inverter | Locking status | Yes
ALM_INV050_LowInsulationResistance | INV050_LowInsulationResistance | INV050 | Inverter | Low Insulation Resistance | Yes
ALM_INV050_OffGridOutputOverload | INV050_OffGridOutputOverload | INV050 | Inverter | Off-grid output overload | Yes
ALM_INV050_OptimizerFault | INV050_OptimizerFault | INV050 | Inverter | Optimizer fault | Yes
ALM_INV050_OutputDCComponentOverhigh | INV050_OutputDCComponentOverhigh | INV050 | Inverter | Output DC Component Overhigh | Yes
ALM_INV050_OutputOvercurrent | INV050_OutputOvercurrent | INV050 | Inverter | Output Overcurrent | Yes
ALM_INV050_PVStringLoss | INV050_PVStringLoss | INV050 | Inverter | PV String Loss | Yes
ALM_INV050_PassiveIslanding | INV050_PassiveIslanding | INV050 | Inverter | Passive Islanding | Yes
ALM_INV050_PeripheralPortShortCircuit | INV050_PeripheralPortShortCircuit | INV050 | Inverter | Peripheral port short circuit | Yes
ALM_INV050_PhaseWireShortCircuitedPE | INV050_PhaseWireShortCircuitedPE | INV050 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV050_PowerLimitationActiveGridCommand | INV050_PowerLimitationActiveGridCommand | INV050 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV050_StringReverseConnection | INV050_StringReverseConnection | INV050 | Inverter | String Reverse Connection | Yes
ALM_INV050_StringReversePolarity | INV050_StringReversePolarity | INV050 | Inverter | String Reverse Polarity | Yes
ALM_INV050_TransientACOvervoltage | INV050_TransientACOvervoltage | INV050 | Inverter | Transient AC Overvoltage | Yes
ALM_INV050_WarningActive | INV050_WarningActive | INV050 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV051_ACOvervoltage | INV051_ACOvervoltage | INV051 | Inverter | AC Overvoltage | Yes
ALM_INV051_ACUndervoltage | INV051_ACUndervoltage | INV051 | Inverter | AC Undervoltage | Yes
ALM_INV051_AFCISelfCheckFailure | INV051_AFCISelfCheckFailure | INV051 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV051_AbnormalGrounding | INV051_AbnormalGrounding | INV051 | Inverter | Abnormal Grounding | Yes
ALM_INV051_AbnormalPVModuleConfiguration | INV051_AbnormalPVModuleConfiguration | INV051 | Inverter | Abnormal PV module configuration | Yes
ALM_INV051_AbnormalResidualCurrent | INV051_AbnormalResidualCurrent | INV051 | Inverter | Abnormal Residual Current | Yes
ALM_INV051_AbnormalStringPower | INV051_AbnormalStringPower | INV051 | Inverter | Abnormal String Power | Yes
ALM_INV051_ActiveIslanding | INV051_ActiveIslanding | INV051 | Inverter | Active Islanding | Yes
ALM_INV051_BuiltPIDOperationAbnormal | INV051_BuiltPIDOperationAbnormal | INV051 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV051_CabinetOvertemperature | INV051_CabinetOvertemperature | INV051 | Inverter | Cabinet Overtemperature | Yes
ALM_INV051_CommunicationFailure | INV051_CommunicationFailure | INV051 | Inverter | Communication Failure | Yes
ALM_INV051_CommunicationStatus | INV051_CommunicationStatus | INV051 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV051_DCArcFault | INV051_DCArcFault | INV051 | Inverter | DC Arc Fault | Yes
ALM_INV051_DCInsulationFault | INV051_DCInsulationFault | INV051 | Inverter | DC Insulation Fault | Yes
ALM_INV051_DCOvervoltage | INV051_DCOvervoltage | INV051 | Inverter | DC Overvoltage | Yes
ALM_INV051_DeviceFault | INV051_DeviceFault | INV051 | Inverter | Device Fault | Yes
ALM_INV051_ExternalFanAbnormal | INV051_ExternalFanAbnormal | INV051 | Inverter | External fan abnormal | Yes
ALM_INV051_FanFailure | INV051_FanFailure | INV051 | Inverter | Fan Failure | Yes
ALM_INV051_Faulty | INV051_Faulty | INV051 | Inverter | Faulty | Yes
ALM_INV051_FaultyMonitoringUnit | INV051_FaultyMonitoringUnit | INV051 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV051_FaultyPowerCollector | INV051_FaultyPowerCollector | INV051 | Inverter | Faulty Power Collector | Yes
ALM_INV051_GeneralFaultTrip | INV051_GeneralFaultTrip | INV051 | Inverter | General Fault Trip | Yes
ALM_INV051_GridConnectionDeratingInverterInternalCauses | INV051_GridConnectionDeratingInverterInternalCauses | INV051 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV051_GridConnectionDeratingPowerRationing | INV051_GridConnectionDeratingPowerRationing | INV051 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV051_GridLoss | INV051_GridLoss | INV051 | Inverter | Grid Loss | Yes
ALM_INV051_GridOverfrequency | INV051_GridOverfrequency | INV051 | Inverter | Grid Overfrequency | Yes
ALM_INV051_GridOvervoltage | INV051_GridOvervoltage | INV051 | Inverter | Grid Overvoltage | Yes
ALM_INV051_GridTiedOffGridControllerAbnormal | INV051_GridTiedOffGridControllerAbnormal | INV051 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV051_GridUnderfrequency | INV051_GridUnderfrequency | INV051 | Inverter | Grid Underfrequency | Yes
ALM_INV051_GridUndervoltage | INV051_GridUndervoltage | INV051 | Inverter | Grid Undervoltage | Yes
ALM_INV051_GroundFault | INV051_GroundFault | INV051 | Inverter | Ground Fault | Yes
ALM_INV051_HighInputStringVoltageGround | INV051_HighInputStringVoltageGround | INV051 | Inverter | High input string voltage to ground | Yes
ALM_INV051_HighStringInputVoltage | INV051_HighStringInputVoltage | INV051 | Inverter | High string input voltage | Yes
ALM_INV051_InverterTripHistoryAvailable | INV051_InverterTripHistoryAvailable | INV051 | Inverter | Inverter Trip History Available | Yes
ALM_INV051_IslandingDetectionStatus | INV051_IslandingDetectionStatus | INV051 | Inverter | Islanding Detection Status | Yes
ALM_INV051_LicenseExpired | INV051_LicenseExpired | INV051 | Inverter | License Expired | Yes
ALM_INV051_LockingStatus | INV051_LockingStatus | INV051 | Inverter | Locking status | Yes
ALM_INV051_LowInsulationResistance | INV051_LowInsulationResistance | INV051 | Inverter | Low Insulation Resistance | Yes
ALM_INV051_OffGridOutputOverload | INV051_OffGridOutputOverload | INV051 | Inverter | Off-grid output overload | Yes
ALM_INV051_OptimizerFault | INV051_OptimizerFault | INV051 | Inverter | Optimizer fault | Yes
ALM_INV051_OutputDCComponentOverhigh | INV051_OutputDCComponentOverhigh | INV051 | Inverter | Output DC Component Overhigh | Yes
ALM_INV051_OutputOvercurrent | INV051_OutputOvercurrent | INV051 | Inverter | Output Overcurrent | Yes
ALM_INV051_PVStringLoss | INV051_PVStringLoss | INV051 | Inverter | PV String Loss | Yes
ALM_INV051_PassiveIslanding | INV051_PassiveIslanding | INV051 | Inverter | Passive Islanding | Yes
ALM_INV051_PeripheralPortShortCircuit | INV051_PeripheralPortShortCircuit | INV051 | Inverter | Peripheral port short circuit | Yes
ALM_INV051_PhaseWireShortCircuitedPE | INV051_PhaseWireShortCircuitedPE | INV051 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV051_PowerLimitationActiveGridCommand | INV051_PowerLimitationActiveGridCommand | INV051 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV051_StringReverseConnection | INV051_StringReverseConnection | INV051 | Inverter | String Reverse Connection | Yes
ALM_INV051_StringReversePolarity | INV051_StringReversePolarity | INV051 | Inverter | String Reverse Polarity | Yes
ALM_INV051_TransientACOvervoltage | INV051_TransientACOvervoltage | INV051 | Inverter | Transient AC Overvoltage | Yes
ALM_INV051_WarningActive | INV051_WarningActive | INV051 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV052_ACOvervoltage | INV052_ACOvervoltage | INV052 | Inverter | AC Overvoltage | Yes
ALM_INV052_ACUndervoltage | INV052_ACUndervoltage | INV052 | Inverter | AC Undervoltage | Yes
ALM_INV052_AFCISelfCheckFailure | INV052_AFCISelfCheckFailure | INV052 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV052_AbnormalGrounding | INV052_AbnormalGrounding | INV052 | Inverter | Abnormal Grounding | Yes
ALM_INV052_AbnormalPVModuleConfiguration | INV052_AbnormalPVModuleConfiguration | INV052 | Inverter | Abnormal PV module configuration | Yes
ALM_INV052_AbnormalResidualCurrent | INV052_AbnormalResidualCurrent | INV052 | Inverter | Abnormal Residual Current | Yes
ALM_INV052_AbnormalStringPower | INV052_AbnormalStringPower | INV052 | Inverter | Abnormal String Power | Yes
ALM_INV052_ActiveIslanding | INV052_ActiveIslanding | INV052 | Inverter | Active Islanding | Yes
ALM_INV052_BuiltPIDOperationAbnormal | INV052_BuiltPIDOperationAbnormal | INV052 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV052_CabinetOvertemperature | INV052_CabinetOvertemperature | INV052 | Inverter | Cabinet Overtemperature | Yes
ALM_INV052_CommunicationFailure | INV052_CommunicationFailure | INV052 | Inverter | Communication Failure | Yes
ALM_INV052_CommunicationStatus | INV052_CommunicationStatus | INV052 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV052_DCArcFault | INV052_DCArcFault | INV052 | Inverter | DC Arc Fault | Yes
ALM_INV052_DCInsulationFault | INV052_DCInsulationFault | INV052 | Inverter | DC Insulation Fault | Yes
ALM_INV052_DCOvervoltage | INV052_DCOvervoltage | INV052 | Inverter | DC Overvoltage | Yes
ALM_INV052_DeviceFault | INV052_DeviceFault | INV052 | Inverter | Device Fault | Yes
ALM_INV052_ExternalFanAbnormal | INV052_ExternalFanAbnormal | INV052 | Inverter | External fan abnormal | Yes
ALM_INV052_FanFailure | INV052_FanFailure | INV052 | Inverter | Fan Failure | Yes
ALM_INV052_Faulty | INV052_Faulty | INV052 | Inverter | Faulty | Yes
ALM_INV052_FaultyMonitoringUnit | INV052_FaultyMonitoringUnit | INV052 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV052_FaultyPowerCollector | INV052_FaultyPowerCollector | INV052 | Inverter | Faulty Power Collector | Yes
ALM_INV052_GeneralFaultTrip | INV052_GeneralFaultTrip | INV052 | Inverter | General Fault Trip | Yes
ALM_INV052_GridConnectionDeratingInverterInternalCauses | INV052_GridConnectionDeratingInverterInternalCauses | INV052 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV052_GridConnectionDeratingPowerRationing | INV052_GridConnectionDeratingPowerRationing | INV052 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV052_GridLoss | INV052_GridLoss | INV052 | Inverter | Grid Loss | Yes
ALM_INV052_GridOverfrequency | INV052_GridOverfrequency | INV052 | Inverter | Grid Overfrequency | Yes
ALM_INV052_GridOvervoltage | INV052_GridOvervoltage | INV052 | Inverter | Grid Overvoltage | Yes
ALM_INV052_GridTiedOffGridControllerAbnormal | INV052_GridTiedOffGridControllerAbnormal | INV052 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV052_GridUnderfrequency | INV052_GridUnderfrequency | INV052 | Inverter | Grid Underfrequency | Yes
ALM_INV052_GridUndervoltage | INV052_GridUndervoltage | INV052 | Inverter | Grid Undervoltage | Yes
ALM_INV052_GroundFault | INV052_GroundFault | INV052 | Inverter | Ground Fault | Yes
ALM_INV052_HighInputStringVoltageGround | INV052_HighInputStringVoltageGround | INV052 | Inverter | High input string voltage to ground | Yes
ALM_INV052_HighStringInputVoltage | INV052_HighStringInputVoltage | INV052 | Inverter | High string input voltage | Yes
ALM_INV052_InverterTripHistoryAvailable | INV052_InverterTripHistoryAvailable | INV052 | Inverter | Inverter Trip History Available | Yes
ALM_INV052_IslandingDetectionStatus | INV052_IslandingDetectionStatus | INV052 | Inverter | Islanding Detection Status | Yes
ALM_INV052_LicenseExpired | INV052_LicenseExpired | INV052 | Inverter | License Expired | Yes
ALM_INV052_LockingStatus | INV052_LockingStatus | INV052 | Inverter | Locking status | Yes
ALM_INV052_LowInsulationResistance | INV052_LowInsulationResistance | INV052 | Inverter | Low Insulation Resistance | Yes
ALM_INV052_OffGridOutputOverload | INV052_OffGridOutputOverload | INV052 | Inverter | Off-grid output overload | Yes
ALM_INV052_OptimizerFault | INV052_OptimizerFault | INV052 | Inverter | Optimizer fault | Yes
ALM_INV052_OutputDCComponentOverhigh | INV052_OutputDCComponentOverhigh | INV052 | Inverter | Output DC Component Overhigh | Yes
ALM_INV052_OutputOvercurrent | INV052_OutputOvercurrent | INV052 | Inverter | Output Overcurrent | Yes
ALM_INV052_PVStringLoss | INV052_PVStringLoss | INV052 | Inverter | PV String Loss | Yes
ALM_INV052_PassiveIslanding | INV052_PassiveIslanding | INV052 | Inverter | Passive Islanding | Yes
ALM_INV052_PeripheralPortShortCircuit | INV052_PeripheralPortShortCircuit | INV052 | Inverter | Peripheral port short circuit | Yes
ALM_INV052_PhaseWireShortCircuitedPE | INV052_PhaseWireShortCircuitedPE | INV052 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV052_PowerLimitationActiveGridCommand | INV052_PowerLimitationActiveGridCommand | INV052 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV052_StringReverseConnection | INV052_StringReverseConnection | INV052 | Inverter | String Reverse Connection | Yes
ALM_INV052_StringReversePolarity | INV052_StringReversePolarity | INV052 | Inverter | String Reverse Polarity | Yes
ALM_INV052_TransientACOvervoltage | INV052_TransientACOvervoltage | INV052 | Inverter | Transient AC Overvoltage | Yes
ALM_INV052_WarningActive | INV052_WarningActive | INV052 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV053_ACOvervoltage | INV053_ACOvervoltage | INV053 | Inverter | AC Overvoltage | Yes
ALM_INV053_ACUndervoltage | INV053_ACUndervoltage | INV053 | Inverter | AC Undervoltage | Yes
ALM_INV053_AFCISelfCheckFailure | INV053_AFCISelfCheckFailure | INV053 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV053_AbnormalGrounding | INV053_AbnormalGrounding | INV053 | Inverter | Abnormal Grounding | Yes
ALM_INV053_AbnormalPVModuleConfiguration | INV053_AbnormalPVModuleConfiguration | INV053 | Inverter | Abnormal PV module configuration | Yes
ALM_INV053_AbnormalResidualCurrent | INV053_AbnormalResidualCurrent | INV053 | Inverter | Abnormal Residual Current | Yes
ALM_INV053_AbnormalStringPower | INV053_AbnormalStringPower | INV053 | Inverter | Abnormal String Power | Yes
ALM_INV053_ActiveIslanding | INV053_ActiveIslanding | INV053 | Inverter | Active Islanding | Yes
ALM_INV053_BuiltPIDOperationAbnormal | INV053_BuiltPIDOperationAbnormal | INV053 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV053_CabinetOvertemperature | INV053_CabinetOvertemperature | INV053 | Inverter | Cabinet Overtemperature | Yes
ALM_INV053_CommunicationFailure | INV053_CommunicationFailure | INV053 | Inverter | Communication Failure | Yes
ALM_INV053_CommunicationStatus | INV053_CommunicationStatus | INV053 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV053_DCArcFault | INV053_DCArcFault | INV053 | Inverter | DC Arc Fault | Yes
ALM_INV053_DCInsulationFault | INV053_DCInsulationFault | INV053 | Inverter | DC Insulation Fault | Yes
ALM_INV053_DCOvervoltage | INV053_DCOvervoltage | INV053 | Inverter | DC Overvoltage | Yes
ALM_INV053_DeviceFault | INV053_DeviceFault | INV053 | Inverter | Device Fault | Yes
ALM_INV053_ExternalFanAbnormal | INV053_ExternalFanAbnormal | INV053 | Inverter | External fan abnormal | Yes
ALM_INV053_FanFailure | INV053_FanFailure | INV053 | Inverter | Fan Failure | Yes
ALM_INV053_Faulty | INV053_Faulty | INV053 | Inverter | Faulty | Yes
ALM_INV053_FaultyMonitoringUnit | INV053_FaultyMonitoringUnit | INV053 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV053_FaultyPowerCollector | INV053_FaultyPowerCollector | INV053 | Inverter | Faulty Power Collector | Yes
ALM_INV053_GeneralFaultTrip | INV053_GeneralFaultTrip | INV053 | Inverter | General Fault Trip | Yes
ALM_INV053_GridConnectionDeratingInverterInternalCauses | INV053_GridConnectionDeratingInverterInternalCauses | INV053 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV053_GridConnectionDeratingPowerRationing | INV053_GridConnectionDeratingPowerRationing | INV053 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV053_GridLoss | INV053_GridLoss | INV053 | Inverter | Grid Loss | Yes
ALM_INV053_GridOverfrequency | INV053_GridOverfrequency | INV053 | Inverter | Grid Overfrequency | Yes
ALM_INV053_GridOvervoltage | INV053_GridOvervoltage | INV053 | Inverter | Grid Overvoltage | Yes
ALM_INV053_GridTiedOffGridControllerAbnormal | INV053_GridTiedOffGridControllerAbnormal | INV053 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV053_GridUnderfrequency | INV053_GridUnderfrequency | INV053 | Inverter | Grid Underfrequency | Yes
ALM_INV053_GridUndervoltage | INV053_GridUndervoltage | INV053 | Inverter | Grid Undervoltage | Yes
ALM_INV053_GroundFault | INV053_GroundFault | INV053 | Inverter | Ground Fault | Yes
ALM_INV053_HighInputStringVoltageGround | INV053_HighInputStringVoltageGround | INV053 | Inverter | High input string voltage to ground | Yes
ALM_INV053_HighStringInputVoltage | INV053_HighStringInputVoltage | INV053 | Inverter | High string input voltage | Yes
ALM_INV053_InverterTripHistoryAvailable | INV053_InverterTripHistoryAvailable | INV053 | Inverter | Inverter Trip History Available | Yes
ALM_INV053_IslandingDetectionStatus | INV053_IslandingDetectionStatus | INV053 | Inverter | Islanding Detection Status | Yes
ALM_INV053_LicenseExpired | INV053_LicenseExpired | INV053 | Inverter | License Expired | Yes
ALM_INV053_LockingStatus | INV053_LockingStatus | INV053 | Inverter | Locking status | Yes
ALM_INV053_LowInsulationResistance | INV053_LowInsulationResistance | INV053 | Inverter | Low Insulation Resistance | Yes
ALM_INV053_OffGridOutputOverload | INV053_OffGridOutputOverload | INV053 | Inverter | Off-grid output overload | Yes
ALM_INV053_OptimizerFault | INV053_OptimizerFault | INV053 | Inverter | Optimizer fault | Yes
ALM_INV053_OutputDCComponentOverhigh | INV053_OutputDCComponentOverhigh | INV053 | Inverter | Output DC Component Overhigh | Yes
ALM_INV053_OutputOvercurrent | INV053_OutputOvercurrent | INV053 | Inverter | Output Overcurrent | Yes
ALM_INV053_PVStringLoss | INV053_PVStringLoss | INV053 | Inverter | PV String Loss | Yes
ALM_INV053_PassiveIslanding | INV053_PassiveIslanding | INV053 | Inverter | Passive Islanding | Yes
ALM_INV053_PeripheralPortShortCircuit | INV053_PeripheralPortShortCircuit | INV053 | Inverter | Peripheral port short circuit | Yes
ALM_INV053_PhaseWireShortCircuitedPE | INV053_PhaseWireShortCircuitedPE | INV053 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV053_PowerLimitationActiveGridCommand | INV053_PowerLimitationActiveGridCommand | INV053 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV053_StringReverseConnection | INV053_StringReverseConnection | INV053 | Inverter | String Reverse Connection | Yes
ALM_INV053_StringReversePolarity | INV053_StringReversePolarity | INV053 | Inverter | String Reverse Polarity | Yes
ALM_INV053_TransientACOvervoltage | INV053_TransientACOvervoltage | INV053 | Inverter | Transient AC Overvoltage | Yes
ALM_INV053_WarningActive | INV053_WarningActive | INV053 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV054_ACOvervoltage | INV054_ACOvervoltage | INV054 | Inverter | AC Overvoltage | Yes
ALM_INV054_ACUndervoltage | INV054_ACUndervoltage | INV054 | Inverter | AC Undervoltage | Yes
ALM_INV054_AFCISelfCheckFailure | INV054_AFCISelfCheckFailure | INV054 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV054_AbnormalGrounding | INV054_AbnormalGrounding | INV054 | Inverter | Abnormal Grounding | Yes
ALM_INV054_AbnormalPVModuleConfiguration | INV054_AbnormalPVModuleConfiguration | INV054 | Inverter | Abnormal PV module configuration | Yes
ALM_INV054_AbnormalResidualCurrent | INV054_AbnormalResidualCurrent | INV054 | Inverter | Abnormal Residual Current | Yes
ALM_INV054_AbnormalStringPower | INV054_AbnormalStringPower | INV054 | Inverter | Abnormal String Power | Yes
ALM_INV054_ActiveIslanding | INV054_ActiveIslanding | INV054 | Inverter | Active Islanding | Yes
ALM_INV054_BuiltPIDOperationAbnormal | INV054_BuiltPIDOperationAbnormal | INV054 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV054_CabinetOvertemperature | INV054_CabinetOvertemperature | INV054 | Inverter | Cabinet Overtemperature | Yes
ALM_INV054_CommunicationFailure | INV054_CommunicationFailure | INV054 | Inverter | Communication Failure | Yes
ALM_INV054_CommunicationStatus | INV054_CommunicationStatus | INV054 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV054_DCArcFault | INV054_DCArcFault | INV054 | Inverter | DC Arc Fault | Yes
ALM_INV054_DCInsulationFault | INV054_DCInsulationFault | INV054 | Inverter | DC Insulation Fault | Yes
ALM_INV054_DCOvervoltage | INV054_DCOvervoltage | INV054 | Inverter | DC Overvoltage | Yes
ALM_INV054_DeviceFault | INV054_DeviceFault | INV054 | Inverter | Device Fault | Yes
ALM_INV054_ExternalFanAbnormal | INV054_ExternalFanAbnormal | INV054 | Inverter | External fan abnormal | Yes
ALM_INV054_FanFailure | INV054_FanFailure | INV054 | Inverter | Fan Failure | Yes
ALM_INV054_Faulty | INV054_Faulty | INV054 | Inverter | Faulty | Yes
ALM_INV054_FaultyMonitoringUnit | INV054_FaultyMonitoringUnit | INV054 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV054_FaultyPowerCollector | INV054_FaultyPowerCollector | INV054 | Inverter | Faulty Power Collector | Yes
ALM_INV054_GeneralFaultTrip | INV054_GeneralFaultTrip | INV054 | Inverter | General Fault Trip | Yes
ALM_INV054_GridConnectionDeratingInverterInternalCauses | INV054_GridConnectionDeratingInverterInternalCauses | INV054 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV054_GridConnectionDeratingPowerRationing | INV054_GridConnectionDeratingPowerRationing | INV054 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV054_GridLoss | INV054_GridLoss | INV054 | Inverter | Grid Loss | Yes
ALM_INV054_GridOverfrequency | INV054_GridOverfrequency | INV054 | Inverter | Grid Overfrequency | Yes
ALM_INV054_GridOvervoltage | INV054_GridOvervoltage | INV054 | Inverter | Grid Overvoltage | Yes
ALM_INV054_GridTiedOffGridControllerAbnormal | INV054_GridTiedOffGridControllerAbnormal | INV054 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV054_GridUnderfrequency | INV054_GridUnderfrequency | INV054 | Inverter | Grid Underfrequency | Yes
ALM_INV054_GridUndervoltage | INV054_GridUndervoltage | INV054 | Inverter | Grid Undervoltage | Yes
ALM_INV054_GroundFault | INV054_GroundFault | INV054 | Inverter | Ground Fault | Yes
ALM_INV054_HighInputStringVoltageGround | INV054_HighInputStringVoltageGround | INV054 | Inverter | High input string voltage to ground | Yes
ALM_INV054_HighStringInputVoltage | INV054_HighStringInputVoltage | INV054 | Inverter | High string input voltage | Yes
ALM_INV054_InverterTripHistoryAvailable | INV054_InverterTripHistoryAvailable | INV054 | Inverter | Inverter Trip History Available | Yes
ALM_INV054_IslandingDetectionStatus | INV054_IslandingDetectionStatus | INV054 | Inverter | Islanding Detection Status | Yes
ALM_INV054_LicenseExpired | INV054_LicenseExpired | INV054 | Inverter | License Expired | Yes
ALM_INV054_LockingStatus | INV054_LockingStatus | INV054 | Inverter | Locking status | Yes
ALM_INV054_LowInsulationResistance | INV054_LowInsulationResistance | INV054 | Inverter | Low Insulation Resistance | Yes
ALM_INV054_OffGridOutputOverload | INV054_OffGridOutputOverload | INV054 | Inverter | Off-grid output overload | Yes
ALM_INV054_OptimizerFault | INV054_OptimizerFault | INV054 | Inverter | Optimizer fault | Yes
ALM_INV054_OutputDCComponentOverhigh | INV054_OutputDCComponentOverhigh | INV054 | Inverter | Output DC Component Overhigh | Yes
ALM_INV054_OutputOvercurrent | INV054_OutputOvercurrent | INV054 | Inverter | Output Overcurrent | Yes
ALM_INV054_PVStringLoss | INV054_PVStringLoss | INV054 | Inverter | PV String Loss | Yes
ALM_INV054_PassiveIslanding | INV054_PassiveIslanding | INV054 | Inverter | Passive Islanding | Yes
ALM_INV054_PeripheralPortShortCircuit | INV054_PeripheralPortShortCircuit | INV054 | Inverter | Peripheral port short circuit | Yes
ALM_INV054_PhaseWireShortCircuitedPE | INV054_PhaseWireShortCircuitedPE | INV054 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV054_PowerLimitationActiveGridCommand | INV054_PowerLimitationActiveGridCommand | INV054 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV054_StringReverseConnection | INV054_StringReverseConnection | INV054 | Inverter | String Reverse Connection | Yes
ALM_INV054_StringReversePolarity | INV054_StringReversePolarity | INV054 | Inverter | String Reverse Polarity | Yes
ALM_INV054_TransientACOvervoltage | INV054_TransientACOvervoltage | INV054 | Inverter | Transient AC Overvoltage | Yes
ALM_INV054_WarningActive | INV054_WarningActive | INV054 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV055_ACOvervoltage | INV055_ACOvervoltage | INV055 | Inverter | AC Overvoltage | Yes
ALM_INV055_ACUndervoltage | INV055_ACUndervoltage | INV055 | Inverter | AC Undervoltage | Yes
ALM_INV055_AFCISelfCheckFailure | INV055_AFCISelfCheckFailure | INV055 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV055_AbnormalGrounding | INV055_AbnormalGrounding | INV055 | Inverter | Abnormal Grounding | Yes
ALM_INV055_AbnormalPVModuleConfiguration | INV055_AbnormalPVModuleConfiguration | INV055 | Inverter | Abnormal PV module configuration | Yes
ALM_INV055_AbnormalResidualCurrent | INV055_AbnormalResidualCurrent | INV055 | Inverter | Abnormal Residual Current | Yes
ALM_INV055_AbnormalStringPower | INV055_AbnormalStringPower | INV055 | Inverter | Abnormal String Power | Yes
ALM_INV055_ActiveIslanding | INV055_ActiveIslanding | INV055 | Inverter | Active Islanding | Yes
ALM_INV055_BuiltPIDOperationAbnormal | INV055_BuiltPIDOperationAbnormal | INV055 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV055_CabinetOvertemperature | INV055_CabinetOvertemperature | INV055 | Inverter | Cabinet Overtemperature | Yes
ALM_INV055_CommunicationFailure | INV055_CommunicationFailure | INV055 | Inverter | Communication Failure | Yes
ALM_INV055_CommunicationStatus | INV055_CommunicationStatus | INV055 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV055_DCArcFault | INV055_DCArcFault | INV055 | Inverter | DC Arc Fault | Yes
ALM_INV055_DCInsulationFault | INV055_DCInsulationFault | INV055 | Inverter | DC Insulation Fault | Yes
ALM_INV055_DCOvervoltage | INV055_DCOvervoltage | INV055 | Inverter | DC Overvoltage | Yes
ALM_INV055_DeviceFault | INV055_DeviceFault | INV055 | Inverter | Device Fault | Yes
ALM_INV055_ExternalFanAbnormal | INV055_ExternalFanAbnormal | INV055 | Inverter | External fan abnormal | Yes
ALM_INV055_FanFailure | INV055_FanFailure | INV055 | Inverter | Fan Failure | Yes
ALM_INV055_Faulty | INV055_Faulty | INV055 | Inverter | Faulty | Yes
ALM_INV055_FaultyMonitoringUnit | INV055_FaultyMonitoringUnit | INV055 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV055_FaultyPowerCollector | INV055_FaultyPowerCollector | INV055 | Inverter | Faulty Power Collector | Yes
ALM_INV055_GeneralFaultTrip | INV055_GeneralFaultTrip | INV055 | Inverter | General Fault Trip | Yes
ALM_INV055_GridConnectionDeratingInverterInternalCauses | INV055_GridConnectionDeratingInverterInternalCauses | INV055 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV055_GridConnectionDeratingPowerRationing | INV055_GridConnectionDeratingPowerRationing | INV055 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV055_GridLoss | INV055_GridLoss | INV055 | Inverter | Grid Loss | Yes
ALM_INV055_GridOverfrequency | INV055_GridOverfrequency | INV055 | Inverter | Grid Overfrequency | Yes
ALM_INV055_GridOvervoltage | INV055_GridOvervoltage | INV055 | Inverter | Grid Overvoltage | Yes
ALM_INV055_GridTiedOffGridControllerAbnormal | INV055_GridTiedOffGridControllerAbnormal | INV055 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV055_GridUnderfrequency | INV055_GridUnderfrequency | INV055 | Inverter | Grid Underfrequency | Yes
ALM_INV055_GridUndervoltage | INV055_GridUndervoltage | INV055 | Inverter | Grid Undervoltage | Yes
ALM_INV055_GroundFault | INV055_GroundFault | INV055 | Inverter | Ground Fault | Yes
ALM_INV055_HighInputStringVoltageGround | INV055_HighInputStringVoltageGround | INV055 | Inverter | High input string voltage to ground | Yes
ALM_INV055_HighStringInputVoltage | INV055_HighStringInputVoltage | INV055 | Inverter | High string input voltage | Yes
ALM_INV055_InverterTripHistoryAvailable | INV055_InverterTripHistoryAvailable | INV055 | Inverter | Inverter Trip History Available | Yes
ALM_INV055_IslandingDetectionStatus | INV055_IslandingDetectionStatus | INV055 | Inverter | Islanding Detection Status | Yes
ALM_INV055_LicenseExpired | INV055_LicenseExpired | INV055 | Inverter | License Expired | Yes
ALM_INV055_LockingStatus | INV055_LockingStatus | INV055 | Inverter | Locking status | Yes
ALM_INV055_LowInsulationResistance | INV055_LowInsulationResistance | INV055 | Inverter | Low Insulation Resistance | Yes
ALM_INV055_OffGridOutputOverload | INV055_OffGridOutputOverload | INV055 | Inverter | Off-grid output overload | Yes
ALM_INV055_OptimizerFault | INV055_OptimizerFault | INV055 | Inverter | Optimizer fault | Yes
ALM_INV055_OutputDCComponentOverhigh | INV055_OutputDCComponentOverhigh | INV055 | Inverter | Output DC Component Overhigh | Yes
ALM_INV055_OutputOvercurrent | INV055_OutputOvercurrent | INV055 | Inverter | Output Overcurrent | Yes
ALM_INV055_PVStringLoss | INV055_PVStringLoss | INV055 | Inverter | PV String Loss | Yes
ALM_INV055_PassiveIslanding | INV055_PassiveIslanding | INV055 | Inverter | Passive Islanding | Yes
ALM_INV055_PeripheralPortShortCircuit | INV055_PeripheralPortShortCircuit | INV055 | Inverter | Peripheral port short circuit | Yes
ALM_INV055_PhaseWireShortCircuitedPE | INV055_PhaseWireShortCircuitedPE | INV055 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV055_PowerLimitationActiveGridCommand | INV055_PowerLimitationActiveGridCommand | INV055 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV055_StringReverseConnection | INV055_StringReverseConnection | INV055 | Inverter | String Reverse Connection | Yes
ALM_INV055_StringReversePolarity | INV055_StringReversePolarity | INV055 | Inverter | String Reverse Polarity | Yes
ALM_INV055_TransientACOvervoltage | INV055_TransientACOvervoltage | INV055 | Inverter | Transient AC Overvoltage | Yes
ALM_INV055_WarningActive | INV055_WarningActive | INV055 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV056_ACOvervoltage | INV056_ACOvervoltage | INV056 | Inverter | AC Overvoltage | Yes
ALM_INV056_ACUndervoltage | INV056_ACUndervoltage | INV056 | Inverter | AC Undervoltage | Yes
ALM_INV056_AFCISelfCheckFailure | INV056_AFCISelfCheckFailure | INV056 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV056_AbnormalGrounding | INV056_AbnormalGrounding | INV056 | Inverter | Abnormal Grounding | Yes
ALM_INV056_AbnormalPVModuleConfiguration | INV056_AbnormalPVModuleConfiguration | INV056 | Inverter | Abnormal PV module configuration | Yes
ALM_INV056_AbnormalResidualCurrent | INV056_AbnormalResidualCurrent | INV056 | Inverter | Abnormal Residual Current | Yes
ALM_INV056_AbnormalStringPower | INV056_AbnormalStringPower | INV056 | Inverter | Abnormal String Power | Yes
ALM_INV056_ActiveIslanding | INV056_ActiveIslanding | INV056 | Inverter | Active Islanding | Yes
ALM_INV056_BuiltPIDOperationAbnormal | INV056_BuiltPIDOperationAbnormal | INV056 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV056_CabinetOvertemperature | INV056_CabinetOvertemperature | INV056 | Inverter | Cabinet Overtemperature | Yes
ALM_INV056_CommunicationFailure | INV056_CommunicationFailure | INV056 | Inverter | Communication Failure | Yes
ALM_INV056_CommunicationStatus | INV056_CommunicationStatus | INV056 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV056_DCArcFault | INV056_DCArcFault | INV056 | Inverter | DC Arc Fault | Yes
ALM_INV056_DCInsulationFault | INV056_DCInsulationFault | INV056 | Inverter | DC Insulation Fault | Yes
ALM_INV056_DCOvervoltage | INV056_DCOvervoltage | INV056 | Inverter | DC Overvoltage | Yes
ALM_INV056_DeviceFault | INV056_DeviceFault | INV056 | Inverter | Device Fault | Yes
ALM_INV056_ExternalFanAbnormal | INV056_ExternalFanAbnormal | INV056 | Inverter | External fan abnormal | Yes
ALM_INV056_FanFailure | INV056_FanFailure | INV056 | Inverter | Fan Failure | Yes
ALM_INV056_Faulty | INV056_Faulty | INV056 | Inverter | Faulty | Yes
ALM_INV056_FaultyMonitoringUnit | INV056_FaultyMonitoringUnit | INV056 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV056_FaultyPowerCollector | INV056_FaultyPowerCollector | INV056 | Inverter | Faulty Power Collector | Yes
ALM_INV056_GeneralFaultTrip | INV056_GeneralFaultTrip | INV056 | Inverter | General Fault Trip | Yes
ALM_INV056_GridConnectionDeratingInverterInternalCauses | INV056_GridConnectionDeratingInverterInternalCauses | INV056 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV056_GridConnectionDeratingPowerRationing | INV056_GridConnectionDeratingPowerRationing | INV056 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV056_GridLoss | INV056_GridLoss | INV056 | Inverter | Grid Loss | Yes
ALM_INV056_GridOverfrequency | INV056_GridOverfrequency | INV056 | Inverter | Grid Overfrequency | Yes
ALM_INV056_GridOvervoltage | INV056_GridOvervoltage | INV056 | Inverter | Grid Overvoltage | Yes
ALM_INV056_GridTiedOffGridControllerAbnormal | INV056_GridTiedOffGridControllerAbnormal | INV056 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV056_GridUnderfrequency | INV056_GridUnderfrequency | INV056 | Inverter | Grid Underfrequency | Yes
ALM_INV056_GridUndervoltage | INV056_GridUndervoltage | INV056 | Inverter | Grid Undervoltage | Yes
ALM_INV056_GroundFault | INV056_GroundFault | INV056 | Inverter | Ground Fault | Yes
ALM_INV056_HighInputStringVoltageGround | INV056_HighInputStringVoltageGround | INV056 | Inverter | High input string voltage to ground | Yes
ALM_INV056_HighStringInputVoltage | INV056_HighStringInputVoltage | INV056 | Inverter | High string input voltage | Yes
ALM_INV056_InverterTripHistoryAvailable | INV056_InverterTripHistoryAvailable | INV056 | Inverter | Inverter Trip History Available | Yes
ALM_INV056_IslandingDetectionStatus | INV056_IslandingDetectionStatus | INV056 | Inverter | Islanding Detection Status | Yes
ALM_INV056_LicenseExpired | INV056_LicenseExpired | INV056 | Inverter | License Expired | Yes
ALM_INV056_LockingStatus | INV056_LockingStatus | INV056 | Inverter | Locking status | Yes
ALM_INV056_LowInsulationResistance | INV056_LowInsulationResistance | INV056 | Inverter | Low Insulation Resistance | Yes
ALM_INV056_OffGridOutputOverload | INV056_OffGridOutputOverload | INV056 | Inverter | Off-grid output overload | Yes
ALM_INV056_OptimizerFault | INV056_OptimizerFault | INV056 | Inverter | Optimizer fault | Yes
ALM_INV056_OutputDCComponentOverhigh | INV056_OutputDCComponentOverhigh | INV056 | Inverter | Output DC Component Overhigh | Yes
ALM_INV056_OutputOvercurrent | INV056_OutputOvercurrent | INV056 | Inverter | Output Overcurrent | Yes
ALM_INV056_PVStringLoss | INV056_PVStringLoss | INV056 | Inverter | PV String Loss | Yes
ALM_INV056_PassiveIslanding | INV056_PassiveIslanding | INV056 | Inverter | Passive Islanding | Yes
ALM_INV056_PeripheralPortShortCircuit | INV056_PeripheralPortShortCircuit | INV056 | Inverter | Peripheral port short circuit | Yes
ALM_INV056_PhaseWireShortCircuitedPE | INV056_PhaseWireShortCircuitedPE | INV056 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV056_PowerLimitationActiveGridCommand | INV056_PowerLimitationActiveGridCommand | INV056 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV056_StringReverseConnection | INV056_StringReverseConnection | INV056 | Inverter | String Reverse Connection | Yes
ALM_INV056_StringReversePolarity | INV056_StringReversePolarity | INV056 | Inverter | String Reverse Polarity | Yes
ALM_INV056_TransientACOvervoltage | INV056_TransientACOvervoltage | INV056 | Inverter | Transient AC Overvoltage | Yes
ALM_INV056_WarningActive | INV056_WarningActive | INV056 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV057_ACOvervoltage | INV057_ACOvervoltage | INV057 | Inverter | AC Overvoltage | Yes
ALM_INV057_ACUndervoltage | INV057_ACUndervoltage | INV057 | Inverter | AC Undervoltage | Yes
ALM_INV057_AFCISelfCheckFailure | INV057_AFCISelfCheckFailure | INV057 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV057_AbnormalGrounding | INV057_AbnormalGrounding | INV057 | Inverter | Abnormal Grounding | Yes
ALM_INV057_AbnormalPVModuleConfiguration | INV057_AbnormalPVModuleConfiguration | INV057 | Inverter | Abnormal PV module configuration | Yes
ALM_INV057_AbnormalResidualCurrent | INV057_AbnormalResidualCurrent | INV057 | Inverter | Abnormal Residual Current | Yes
ALM_INV057_AbnormalStringPower | INV057_AbnormalStringPower | INV057 | Inverter | Abnormal String Power | Yes
ALM_INV057_ActiveIslanding | INV057_ActiveIslanding | INV057 | Inverter | Active Islanding | Yes
ALM_INV057_BuiltPIDOperationAbnormal | INV057_BuiltPIDOperationAbnormal | INV057 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV057_CabinetOvertemperature | INV057_CabinetOvertemperature | INV057 | Inverter | Cabinet Overtemperature | Yes
ALM_INV057_CommunicationFailure | INV057_CommunicationFailure | INV057 | Inverter | Communication Failure | Yes
ALM_INV057_CommunicationStatus | INV057_CommunicationStatus | INV057 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV057_DCArcFault | INV057_DCArcFault | INV057 | Inverter | DC Arc Fault | Yes
ALM_INV057_DCInsulationFault | INV057_DCInsulationFault | INV057 | Inverter | DC Insulation Fault | Yes
ALM_INV057_DCOvervoltage | INV057_DCOvervoltage | INV057 | Inverter | DC Overvoltage | Yes
ALM_INV057_DeviceFault | INV057_DeviceFault | INV057 | Inverter | Device Fault | Yes
ALM_INV057_ExternalFanAbnormal | INV057_ExternalFanAbnormal | INV057 | Inverter | External fan abnormal | Yes
ALM_INV057_FanFailure | INV057_FanFailure | INV057 | Inverter | Fan Failure | Yes
ALM_INV057_Faulty | INV057_Faulty | INV057 | Inverter | Faulty | Yes
ALM_INV057_FaultyMonitoringUnit | INV057_FaultyMonitoringUnit | INV057 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV057_FaultyPowerCollector | INV057_FaultyPowerCollector | INV057 | Inverter | Faulty Power Collector | Yes
ALM_INV057_GeneralFaultTrip | INV057_GeneralFaultTrip | INV057 | Inverter | General Fault Trip | Yes
ALM_INV057_GridConnectionDeratingInverterInternalCauses | INV057_GridConnectionDeratingInverterInternalCauses | INV057 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV057_GridConnectionDeratingPowerRationing | INV057_GridConnectionDeratingPowerRationing | INV057 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV057_GridLoss | INV057_GridLoss | INV057 | Inverter | Grid Loss | Yes
ALM_INV057_GridOverfrequency | INV057_GridOverfrequency | INV057 | Inverter | Grid Overfrequency | Yes
ALM_INV057_GridOvervoltage | INV057_GridOvervoltage | INV057 | Inverter | Grid Overvoltage | Yes
ALM_INV057_GridTiedOffGridControllerAbnormal | INV057_GridTiedOffGridControllerAbnormal | INV057 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV057_GridUnderfrequency | INV057_GridUnderfrequency | INV057 | Inverter | Grid Underfrequency | Yes
ALM_INV057_GridUndervoltage | INV057_GridUndervoltage | INV057 | Inverter | Grid Undervoltage | Yes
ALM_INV057_GroundFault | INV057_GroundFault | INV057 | Inverter | Ground Fault | Yes
ALM_INV057_HighInputStringVoltageGround | INV057_HighInputStringVoltageGround | INV057 | Inverter | High input string voltage to ground | Yes
ALM_INV057_HighStringInputVoltage | INV057_HighStringInputVoltage | INV057 | Inverter | High string input voltage | Yes
ALM_INV057_InverterTripHistoryAvailable | INV057_InverterTripHistoryAvailable | INV057 | Inverter | Inverter Trip History Available | Yes
ALM_INV057_IslandingDetectionStatus | INV057_IslandingDetectionStatus | INV057 | Inverter | Islanding Detection Status | Yes
ALM_INV057_LicenseExpired | INV057_LicenseExpired | INV057 | Inverter | License Expired | Yes
ALM_INV057_LockingStatus | INV057_LockingStatus | INV057 | Inverter | Locking status | Yes
ALM_INV057_LowInsulationResistance | INV057_LowInsulationResistance | INV057 | Inverter | Low Insulation Resistance | Yes
ALM_INV057_OffGridOutputOverload | INV057_OffGridOutputOverload | INV057 | Inverter | Off-grid output overload | Yes
ALM_INV057_OptimizerFault | INV057_OptimizerFault | INV057 | Inverter | Optimizer fault | Yes
ALM_INV057_OutputDCComponentOverhigh | INV057_OutputDCComponentOverhigh | INV057 | Inverter | Output DC Component Overhigh | Yes
ALM_INV057_OutputOvercurrent | INV057_OutputOvercurrent | INV057 | Inverter | Output Overcurrent | Yes
ALM_INV057_PVStringLoss | INV057_PVStringLoss | INV057 | Inverter | PV String Loss | Yes
ALM_INV057_PassiveIslanding | INV057_PassiveIslanding | INV057 | Inverter | Passive Islanding | Yes
ALM_INV057_PeripheralPortShortCircuit | INV057_PeripheralPortShortCircuit | INV057 | Inverter | Peripheral port short circuit | Yes
ALM_INV057_PhaseWireShortCircuitedPE | INV057_PhaseWireShortCircuitedPE | INV057 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV057_PowerLimitationActiveGridCommand | INV057_PowerLimitationActiveGridCommand | INV057 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV057_StringReverseConnection | INV057_StringReverseConnection | INV057 | Inverter | String Reverse Connection | Yes
ALM_INV057_StringReversePolarity | INV057_StringReversePolarity | INV057 | Inverter | String Reverse Polarity | Yes
ALM_INV057_TransientACOvervoltage | INV057_TransientACOvervoltage | INV057 | Inverter | Transient AC Overvoltage | Yes
ALM_INV057_WarningActive | INV057_WarningActive | INV057 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV058_ACOvervoltage | INV058_ACOvervoltage | INV058 | Inverter | AC Overvoltage | Yes
ALM_INV058_ACUndervoltage | INV058_ACUndervoltage | INV058 | Inverter | AC Undervoltage | Yes
ALM_INV058_AFCISelfCheckFailure | INV058_AFCISelfCheckFailure | INV058 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV058_AbnormalGrounding | INV058_AbnormalGrounding | INV058 | Inverter | Abnormal Grounding | Yes
ALM_INV058_AbnormalPVModuleConfiguration | INV058_AbnormalPVModuleConfiguration | INV058 | Inverter | Abnormal PV module configuration | Yes
ALM_INV058_AbnormalResidualCurrent | INV058_AbnormalResidualCurrent | INV058 | Inverter | Abnormal Residual Current | Yes
ALM_INV058_AbnormalStringPower | INV058_AbnormalStringPower | INV058 | Inverter | Abnormal String Power | Yes
ALM_INV058_ActiveIslanding | INV058_ActiveIslanding | INV058 | Inverter | Active Islanding | Yes
ALM_INV058_BuiltPIDOperationAbnormal | INV058_BuiltPIDOperationAbnormal | INV058 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV058_CabinetOvertemperature | INV058_CabinetOvertemperature | INV058 | Inverter | Cabinet Overtemperature | Yes
ALM_INV058_CommunicationFailure | INV058_CommunicationFailure | INV058 | Inverter | Communication Failure | Yes
ALM_INV058_CommunicationStatus | INV058_CommunicationStatus | INV058 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV058_DCArcFault | INV058_DCArcFault | INV058 | Inverter | DC Arc Fault | Yes
ALM_INV058_DCInsulationFault | INV058_DCInsulationFault | INV058 | Inverter | DC Insulation Fault | Yes
ALM_INV058_DCOvervoltage | INV058_DCOvervoltage | INV058 | Inverter | DC Overvoltage | Yes
ALM_INV058_DeviceFault | INV058_DeviceFault | INV058 | Inverter | Device Fault | Yes
ALM_INV058_ExternalFanAbnormal | INV058_ExternalFanAbnormal | INV058 | Inverter | External fan abnormal | Yes
ALM_INV058_FanFailure | INV058_FanFailure | INV058 | Inverter | Fan Failure | Yes
ALM_INV058_Faulty | INV058_Faulty | INV058 | Inverter | Faulty | Yes
ALM_INV058_FaultyMonitoringUnit | INV058_FaultyMonitoringUnit | INV058 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV058_FaultyPowerCollector | INV058_FaultyPowerCollector | INV058 | Inverter | Faulty Power Collector | Yes
ALM_INV058_GeneralFaultTrip | INV058_GeneralFaultTrip | INV058 | Inverter | General Fault Trip | Yes
ALM_INV058_GridConnectionDeratingInverterInternalCauses | INV058_GridConnectionDeratingInverterInternalCauses | INV058 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV058_GridConnectionDeratingPowerRationing | INV058_GridConnectionDeratingPowerRationing | INV058 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV058_GridLoss | INV058_GridLoss | INV058 | Inverter | Grid Loss | Yes
ALM_INV058_GridOverfrequency | INV058_GridOverfrequency | INV058 | Inverter | Grid Overfrequency | Yes
ALM_INV058_GridOvervoltage | INV058_GridOvervoltage | INV058 | Inverter | Grid Overvoltage | Yes
ALM_INV058_GridTiedOffGridControllerAbnormal | INV058_GridTiedOffGridControllerAbnormal | INV058 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV058_GridUnderfrequency | INV058_GridUnderfrequency | INV058 | Inverter | Grid Underfrequency | Yes
ALM_INV058_GridUndervoltage | INV058_GridUndervoltage | INV058 | Inverter | Grid Undervoltage | Yes
ALM_INV058_GroundFault | INV058_GroundFault | INV058 | Inverter | Ground Fault | Yes
ALM_INV058_HighInputStringVoltageGround | INV058_HighInputStringVoltageGround | INV058 | Inverter | High input string voltage to ground | Yes
ALM_INV058_HighStringInputVoltage | INV058_HighStringInputVoltage | INV058 | Inverter | High string input voltage | Yes
ALM_INV058_InverterTripHistoryAvailable | INV058_InverterTripHistoryAvailable | INV058 | Inverter | Inverter Trip History Available | Yes
ALM_INV058_IslandingDetectionStatus | INV058_IslandingDetectionStatus | INV058 | Inverter | Islanding Detection Status | Yes
ALM_INV058_LicenseExpired | INV058_LicenseExpired | INV058 | Inverter | License Expired | Yes
ALM_INV058_LockingStatus | INV058_LockingStatus | INV058 | Inverter | Locking status | Yes
ALM_INV058_LowInsulationResistance | INV058_LowInsulationResistance | INV058 | Inverter | Low Insulation Resistance | Yes
ALM_INV058_OffGridOutputOverload | INV058_OffGridOutputOverload | INV058 | Inverter | Off-grid output overload | Yes
ALM_INV058_OptimizerFault | INV058_OptimizerFault | INV058 | Inverter | Optimizer fault | Yes
ALM_INV058_OutputDCComponentOverhigh | INV058_OutputDCComponentOverhigh | INV058 | Inverter | Output DC Component Overhigh | Yes
ALM_INV058_OutputOvercurrent | INV058_OutputOvercurrent | INV058 | Inverter | Output Overcurrent | Yes
ALM_INV058_PVStringLoss | INV058_PVStringLoss | INV058 | Inverter | PV String Loss | Yes
ALM_INV058_PassiveIslanding | INV058_PassiveIslanding | INV058 | Inverter | Passive Islanding | Yes
ALM_INV058_PeripheralPortShortCircuit | INV058_PeripheralPortShortCircuit | INV058 | Inverter | Peripheral port short circuit | Yes
ALM_INV058_PhaseWireShortCircuitedPE | INV058_PhaseWireShortCircuitedPE | INV058 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV058_PowerLimitationActiveGridCommand | INV058_PowerLimitationActiveGridCommand | INV058 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV058_StringReverseConnection | INV058_StringReverseConnection | INV058 | Inverter | String Reverse Connection | Yes
ALM_INV058_StringReversePolarity | INV058_StringReversePolarity | INV058 | Inverter | String Reverse Polarity | Yes
ALM_INV058_TransientACOvervoltage | INV058_TransientACOvervoltage | INV058 | Inverter | Transient AC Overvoltage | Yes
ALM_INV058_WarningActive | INV058_WarningActive | INV058 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV059_ACOvervoltage | INV059_ACOvervoltage | INV059 | Inverter | AC Overvoltage | Yes
ALM_INV059_ACUndervoltage | INV059_ACUndervoltage | INV059 | Inverter | AC Undervoltage | Yes
ALM_INV059_AFCISelfCheckFailure | INV059_AFCISelfCheckFailure | INV059 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV059_AbnormalGrounding | INV059_AbnormalGrounding | INV059 | Inverter | Abnormal Grounding | Yes
ALM_INV059_AbnormalPVModuleConfiguration | INV059_AbnormalPVModuleConfiguration | INV059 | Inverter | Abnormal PV module configuration | Yes
ALM_INV059_AbnormalResidualCurrent | INV059_AbnormalResidualCurrent | INV059 | Inverter | Abnormal Residual Current | Yes
ALM_INV059_AbnormalStringPower | INV059_AbnormalStringPower | INV059 | Inverter | Abnormal String Power | Yes
ALM_INV059_ActiveIslanding | INV059_ActiveIslanding | INV059 | Inverter | Active Islanding | Yes
ALM_INV059_BuiltPIDOperationAbnormal | INV059_BuiltPIDOperationAbnormal | INV059 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV059_CabinetOvertemperature | INV059_CabinetOvertemperature | INV059 | Inverter | Cabinet Overtemperature | Yes
ALM_INV059_CommunicationFailure | INV059_CommunicationFailure | INV059 | Inverter | Communication Failure | Yes
ALM_INV059_CommunicationStatus | INV059_CommunicationStatus | INV059 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV059_DCArcFault | INV059_DCArcFault | INV059 | Inverter | DC Arc Fault | Yes
ALM_INV059_DCInsulationFault | INV059_DCInsulationFault | INV059 | Inverter | DC Insulation Fault | Yes
ALM_INV059_DCOvervoltage | INV059_DCOvervoltage | INV059 | Inverter | DC Overvoltage | Yes
ALM_INV059_DeviceFault | INV059_DeviceFault | INV059 | Inverter | Device Fault | Yes
ALM_INV059_ExternalFanAbnormal | INV059_ExternalFanAbnormal | INV059 | Inverter | External fan abnormal | Yes
ALM_INV059_FanFailure | INV059_FanFailure | INV059 | Inverter | Fan Failure | Yes
ALM_INV059_Faulty | INV059_Faulty | INV059 | Inverter | Faulty | Yes
ALM_INV059_FaultyMonitoringUnit | INV059_FaultyMonitoringUnit | INV059 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV059_FaultyPowerCollector | INV059_FaultyPowerCollector | INV059 | Inverter | Faulty Power Collector | Yes
ALM_INV059_GeneralFaultTrip | INV059_GeneralFaultTrip | INV059 | Inverter | General Fault Trip | Yes
ALM_INV059_GridConnectionDeratingInverterInternalCauses | INV059_GridConnectionDeratingInverterInternalCauses | INV059 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV059_GridConnectionDeratingPowerRationing | INV059_GridConnectionDeratingPowerRationing | INV059 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV059_GridLoss | INV059_GridLoss | INV059 | Inverter | Grid Loss | Yes
ALM_INV059_GridOverfrequency | INV059_GridOverfrequency | INV059 | Inverter | Grid Overfrequency | Yes
ALM_INV059_GridOvervoltage | INV059_GridOvervoltage | INV059 | Inverter | Grid Overvoltage | Yes
ALM_INV059_GridTiedOffGridControllerAbnormal | INV059_GridTiedOffGridControllerAbnormal | INV059 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV059_GridUnderfrequency | INV059_GridUnderfrequency | INV059 | Inverter | Grid Underfrequency | Yes
ALM_INV059_GridUndervoltage | INV059_GridUndervoltage | INV059 | Inverter | Grid Undervoltage | Yes
ALM_INV059_GroundFault | INV059_GroundFault | INV059 | Inverter | Ground Fault | Yes
ALM_INV059_HighInputStringVoltageGround | INV059_HighInputStringVoltageGround | INV059 | Inverter | High input string voltage to ground | Yes
ALM_INV059_HighStringInputVoltage | INV059_HighStringInputVoltage | INV059 | Inverter | High string input voltage | Yes
ALM_INV059_InverterTripHistoryAvailable | INV059_InverterTripHistoryAvailable | INV059 | Inverter | Inverter Trip History Available | Yes
ALM_INV059_IslandingDetectionStatus | INV059_IslandingDetectionStatus | INV059 | Inverter | Islanding Detection Status | Yes
ALM_INV059_LicenseExpired | INV059_LicenseExpired | INV059 | Inverter | License Expired | Yes
ALM_INV059_LockingStatus | INV059_LockingStatus | INV059 | Inverter | Locking status | Yes
ALM_INV059_LowInsulationResistance | INV059_LowInsulationResistance | INV059 | Inverter | Low Insulation Resistance | Yes
ALM_INV059_OffGridOutputOverload | INV059_OffGridOutputOverload | INV059 | Inverter | Off-grid output overload | Yes
ALM_INV059_OptimizerFault | INV059_OptimizerFault | INV059 | Inverter | Optimizer fault | Yes
ALM_INV059_OutputDCComponentOverhigh | INV059_OutputDCComponentOverhigh | INV059 | Inverter | Output DC Component Overhigh | Yes
ALM_INV059_OutputOvercurrent | INV059_OutputOvercurrent | INV059 | Inverter | Output Overcurrent | Yes
ALM_INV059_PVStringLoss | INV059_PVStringLoss | INV059 | Inverter | PV String Loss | Yes
ALM_INV059_PassiveIslanding | INV059_PassiveIslanding | INV059 | Inverter | Passive Islanding | Yes
ALM_INV059_PeripheralPortShortCircuit | INV059_PeripheralPortShortCircuit | INV059 | Inverter | Peripheral port short circuit | Yes
ALM_INV059_PhaseWireShortCircuitedPE | INV059_PhaseWireShortCircuitedPE | INV059 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV059_PowerLimitationActiveGridCommand | INV059_PowerLimitationActiveGridCommand | INV059 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV059_StringReverseConnection | INV059_StringReverseConnection | INV059 | Inverter | String Reverse Connection | Yes
ALM_INV059_StringReversePolarity | INV059_StringReversePolarity | INV059 | Inverter | String Reverse Polarity | Yes
ALM_INV059_TransientACOvervoltage | INV059_TransientACOvervoltage | INV059 | Inverter | Transient AC Overvoltage | Yes
ALM_INV059_WarningActive | INV059_WarningActive | INV059 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV060_ACOvervoltage | INV060_ACOvervoltage | INV060 | Inverter | AC Overvoltage | Yes
ALM_INV060_ACUndervoltage | INV060_ACUndervoltage | INV060 | Inverter | AC Undervoltage | Yes
ALM_INV060_AFCISelfCheckFailure | INV060_AFCISelfCheckFailure | INV060 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV060_AbnormalGrounding | INV060_AbnormalGrounding | INV060 | Inverter | Abnormal Grounding | Yes
ALM_INV060_AbnormalPVModuleConfiguration | INV060_AbnormalPVModuleConfiguration | INV060 | Inverter | Abnormal PV module configuration | Yes
ALM_INV060_AbnormalResidualCurrent | INV060_AbnormalResidualCurrent | INV060 | Inverter | Abnormal Residual Current | Yes
ALM_INV060_AbnormalStringPower | INV060_AbnormalStringPower | INV060 | Inverter | Abnormal String Power | Yes
ALM_INV060_ActiveIslanding | INV060_ActiveIslanding | INV060 | Inverter | Active Islanding | Yes
ALM_INV060_BuiltPIDOperationAbnormal | INV060_BuiltPIDOperationAbnormal | INV060 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV060_CabinetOvertemperature | INV060_CabinetOvertemperature | INV060 | Inverter | Cabinet Overtemperature | Yes
ALM_INV060_CommunicationFailure | INV060_CommunicationFailure | INV060 | Inverter | Communication Failure | Yes
ALM_INV060_CommunicationStatus | INV060_CommunicationStatus | INV060 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV060_DCArcFault | INV060_DCArcFault | INV060 | Inverter | DC Arc Fault | Yes
ALM_INV060_DCInsulationFault | INV060_DCInsulationFault | INV060 | Inverter | DC Insulation Fault | Yes
ALM_INV060_DCOvervoltage | INV060_DCOvervoltage | INV060 | Inverter | DC Overvoltage | Yes
ALM_INV060_DeviceFault | INV060_DeviceFault | INV060 | Inverter | Device Fault | Yes
ALM_INV060_ExternalFanAbnormal | INV060_ExternalFanAbnormal | INV060 | Inverter | External fan abnormal | Yes
ALM_INV060_FanFailure | INV060_FanFailure | INV060 | Inverter | Fan Failure | Yes
ALM_INV060_Faulty | INV060_Faulty | INV060 | Inverter | Faulty | Yes
ALM_INV060_FaultyMonitoringUnit | INV060_FaultyMonitoringUnit | INV060 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV060_FaultyPowerCollector | INV060_FaultyPowerCollector | INV060 | Inverter | Faulty Power Collector | Yes
ALM_INV060_GeneralFaultTrip | INV060_GeneralFaultTrip | INV060 | Inverter | General Fault Trip | Yes
ALM_INV060_GridConnectionDeratingInverterInternalCauses | INV060_GridConnectionDeratingInverterInternalCauses | INV060 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV060_GridConnectionDeratingPowerRationing | INV060_GridConnectionDeratingPowerRationing | INV060 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV060_GridLoss | INV060_GridLoss | INV060 | Inverter | Grid Loss | Yes
ALM_INV060_GridOverfrequency | INV060_GridOverfrequency | INV060 | Inverter | Grid Overfrequency | Yes
ALM_INV060_GridOvervoltage | INV060_GridOvervoltage | INV060 | Inverter | Grid Overvoltage | Yes
ALM_INV060_GridTiedOffGridControllerAbnormal | INV060_GridTiedOffGridControllerAbnormal | INV060 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV060_GridUnderfrequency | INV060_GridUnderfrequency | INV060 | Inverter | Grid Underfrequency | Yes
ALM_INV060_GridUndervoltage | INV060_GridUndervoltage | INV060 | Inverter | Grid Undervoltage | Yes
ALM_INV060_GroundFault | INV060_GroundFault | INV060 | Inverter | Ground Fault | Yes
ALM_INV060_HighInputStringVoltageGround | INV060_HighInputStringVoltageGround | INV060 | Inverter | High input string voltage to ground | Yes
ALM_INV060_HighStringInputVoltage | INV060_HighStringInputVoltage | INV060 | Inverter | High string input voltage | Yes
ALM_INV060_InverterTripHistoryAvailable | INV060_InverterTripHistoryAvailable | INV060 | Inverter | Inverter Trip History Available | Yes
ALM_INV060_IslandingDetectionStatus | INV060_IslandingDetectionStatus | INV060 | Inverter | Islanding Detection Status | Yes
ALM_INV060_LicenseExpired | INV060_LicenseExpired | INV060 | Inverter | License Expired | Yes
ALM_INV060_LockingStatus | INV060_LockingStatus | INV060 | Inverter | Locking status | Yes
ALM_INV060_LowInsulationResistance | INV060_LowInsulationResistance | INV060 | Inverter | Low Insulation Resistance | Yes
ALM_INV060_OffGridOutputOverload | INV060_OffGridOutputOverload | INV060 | Inverter | Off-grid output overload | Yes
ALM_INV060_OptimizerFault | INV060_OptimizerFault | INV060 | Inverter | Optimizer fault | Yes
ALM_INV060_OutputDCComponentOverhigh | INV060_OutputDCComponentOverhigh | INV060 | Inverter | Output DC Component Overhigh | Yes
ALM_INV060_OutputOvercurrent | INV060_OutputOvercurrent | INV060 | Inverter | Output Overcurrent | Yes
ALM_INV060_PVStringLoss | INV060_PVStringLoss | INV060 | Inverter | PV String Loss | Yes
ALM_INV060_PassiveIslanding | INV060_PassiveIslanding | INV060 | Inverter | Passive Islanding | Yes
ALM_INV060_PeripheralPortShortCircuit | INV060_PeripheralPortShortCircuit | INV060 | Inverter | Peripheral port short circuit | Yes
ALM_INV060_PhaseWireShortCircuitedPE | INV060_PhaseWireShortCircuitedPE | INV060 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV060_PowerLimitationActiveGridCommand | INV060_PowerLimitationActiveGridCommand | INV060 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV060_StringReverseConnection | INV060_StringReverseConnection | INV060 | Inverter | String Reverse Connection | Yes
ALM_INV060_StringReversePolarity | INV060_StringReversePolarity | INV060 | Inverter | String Reverse Polarity | Yes
ALM_INV060_TransientACOvervoltage | INV060_TransientACOvervoltage | INV060 | Inverter | Transient AC Overvoltage | Yes
ALM_INV060_WarningActive | INV060_WarningActive | INV060 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV061_ACOvervoltage | INV061_ACOvervoltage | INV061 | Inverter | AC Overvoltage | Yes
ALM_INV061_ACUndervoltage | INV061_ACUndervoltage | INV061 | Inverter | AC Undervoltage | Yes
ALM_INV061_AFCISelfCheckFailure | INV061_AFCISelfCheckFailure | INV061 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV061_AbnormalGrounding | INV061_AbnormalGrounding | INV061 | Inverter | Abnormal Grounding | Yes
ALM_INV061_AbnormalPVModuleConfiguration | INV061_AbnormalPVModuleConfiguration | INV061 | Inverter | Abnormal PV module configuration | Yes
ALM_INV061_AbnormalResidualCurrent | INV061_AbnormalResidualCurrent | INV061 | Inverter | Abnormal Residual Current | Yes
ALM_INV061_AbnormalStringPower | INV061_AbnormalStringPower | INV061 | Inverter | Abnormal String Power | Yes
ALM_INV061_ActiveIslanding | INV061_ActiveIslanding | INV061 | Inverter | Active Islanding | Yes
ALM_INV061_BuiltPIDOperationAbnormal | INV061_BuiltPIDOperationAbnormal | INV061 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV061_CabinetOvertemperature | INV061_CabinetOvertemperature | INV061 | Inverter | Cabinet Overtemperature | Yes
ALM_INV061_CommunicationFailure | INV061_CommunicationFailure | INV061 | Inverter | Communication Failure | Yes
ALM_INV061_CommunicationStatus | INV061_CommunicationStatus | INV061 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV061_DCArcFault | INV061_DCArcFault | INV061 | Inverter | DC Arc Fault | Yes
ALM_INV061_DCInsulationFault | INV061_DCInsulationFault | INV061 | Inverter | DC Insulation Fault | Yes
ALM_INV061_DCOvervoltage | INV061_DCOvervoltage | INV061 | Inverter | DC Overvoltage | Yes
ALM_INV061_DeviceFault | INV061_DeviceFault | INV061 | Inverter | Device Fault | Yes
ALM_INV061_ExternalFanAbnormal | INV061_ExternalFanAbnormal | INV061 | Inverter | External fan abnormal | Yes
ALM_INV061_FanFailure | INV061_FanFailure | INV061 | Inverter | Fan Failure | Yes
ALM_INV061_Faulty | INV061_Faulty | INV061 | Inverter | Faulty | Yes
ALM_INV061_FaultyMonitoringUnit | INV061_FaultyMonitoringUnit | INV061 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV061_FaultyPowerCollector | INV061_FaultyPowerCollector | INV061 | Inverter | Faulty Power Collector | Yes
ALM_INV061_GeneralFaultTrip | INV061_GeneralFaultTrip | INV061 | Inverter | General Fault Trip | Yes
ALM_INV061_GridConnectionDeratingInverterInternalCauses | INV061_GridConnectionDeratingInverterInternalCauses | INV061 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV061_GridConnectionDeratingPowerRationing | INV061_GridConnectionDeratingPowerRationing | INV061 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV061_GridLoss | INV061_GridLoss | INV061 | Inverter | Grid Loss | Yes
ALM_INV061_GridOverfrequency | INV061_GridOverfrequency | INV061 | Inverter | Grid Overfrequency | Yes
ALM_INV061_GridOvervoltage | INV061_GridOvervoltage | INV061 | Inverter | Grid Overvoltage | Yes
ALM_INV061_GridTiedOffGridControllerAbnormal | INV061_GridTiedOffGridControllerAbnormal | INV061 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV061_GridUnderfrequency | INV061_GridUnderfrequency | INV061 | Inverter | Grid Underfrequency | Yes
ALM_INV061_GridUndervoltage | INV061_GridUndervoltage | INV061 | Inverter | Grid Undervoltage | Yes
ALM_INV061_GroundFault | INV061_GroundFault | INV061 | Inverter | Ground Fault | Yes
ALM_INV061_HighInputStringVoltageGround | INV061_HighInputStringVoltageGround | INV061 | Inverter | High input string voltage to ground | Yes
ALM_INV061_HighStringInputVoltage | INV061_HighStringInputVoltage | INV061 | Inverter | High string input voltage | Yes
ALM_INV061_InverterTripHistoryAvailable | INV061_InverterTripHistoryAvailable | INV061 | Inverter | Inverter Trip History Available | Yes
ALM_INV061_IslandingDetectionStatus | INV061_IslandingDetectionStatus | INV061 | Inverter | Islanding Detection Status | Yes
ALM_INV061_LicenseExpired | INV061_LicenseExpired | INV061 | Inverter | License Expired | Yes
ALM_INV061_LockingStatus | INV061_LockingStatus | INV061 | Inverter | Locking status | Yes
ALM_INV061_LowInsulationResistance | INV061_LowInsulationResistance | INV061 | Inverter | Low Insulation Resistance | Yes
ALM_INV061_OffGridOutputOverload | INV061_OffGridOutputOverload | INV061 | Inverter | Off-grid output overload | Yes
ALM_INV061_OptimizerFault | INV061_OptimizerFault | INV061 | Inverter | Optimizer fault | Yes
ALM_INV061_OutputDCComponentOverhigh | INV061_OutputDCComponentOverhigh | INV061 | Inverter | Output DC Component Overhigh | Yes
ALM_INV061_OutputOvercurrent | INV061_OutputOvercurrent | INV061 | Inverter | Output Overcurrent | Yes
ALM_INV061_PVStringLoss | INV061_PVStringLoss | INV061 | Inverter | PV String Loss | Yes
ALM_INV061_PassiveIslanding | INV061_PassiveIslanding | INV061 | Inverter | Passive Islanding | Yes
ALM_INV061_PeripheralPortShortCircuit | INV061_PeripheralPortShortCircuit | INV061 | Inverter | Peripheral port short circuit | Yes
ALM_INV061_PhaseWireShortCircuitedPE | INV061_PhaseWireShortCircuitedPE | INV061 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV061_PowerLimitationActiveGridCommand | INV061_PowerLimitationActiveGridCommand | INV061 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV061_StringReverseConnection | INV061_StringReverseConnection | INV061 | Inverter | String Reverse Connection | Yes
ALM_INV061_StringReversePolarity | INV061_StringReversePolarity | INV061 | Inverter | String Reverse Polarity | Yes
ALM_INV061_TransientACOvervoltage | INV061_TransientACOvervoltage | INV061 | Inverter | Transient AC Overvoltage | Yes
ALM_INV061_WarningActive | INV061_WarningActive | INV061 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV062_ACOvervoltage | INV062_ACOvervoltage | INV062 | Inverter | AC Overvoltage | Yes
ALM_INV062_ACUndervoltage | INV062_ACUndervoltage | INV062 | Inverter | AC Undervoltage | Yes
ALM_INV062_AFCISelfCheckFailure | INV062_AFCISelfCheckFailure | INV062 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV062_AbnormalGrounding | INV062_AbnormalGrounding | INV062 | Inverter | Abnormal Grounding | Yes
ALM_INV062_AbnormalPVModuleConfiguration | INV062_AbnormalPVModuleConfiguration | INV062 | Inverter | Abnormal PV module configuration | Yes
ALM_INV062_AbnormalResidualCurrent | INV062_AbnormalResidualCurrent | INV062 | Inverter | Abnormal Residual Current | Yes
ALM_INV062_AbnormalStringPower | INV062_AbnormalStringPower | INV062 | Inverter | Abnormal String Power | Yes
ALM_INV062_ActiveIslanding | INV062_ActiveIslanding | INV062 | Inverter | Active Islanding | Yes
ALM_INV062_BuiltPIDOperationAbnormal | INV062_BuiltPIDOperationAbnormal | INV062 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV062_CabinetOvertemperature | INV062_CabinetOvertemperature | INV062 | Inverter | Cabinet Overtemperature | Yes
ALM_INV062_CommunicationFailure | INV062_CommunicationFailure | INV062 | Inverter | Communication Failure | Yes
ALM_INV062_CommunicationStatus | INV062_CommunicationStatus | INV062 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV062_DCArcFault | INV062_DCArcFault | INV062 | Inverter | DC Arc Fault | Yes
ALM_INV062_DCInsulationFault | INV062_DCInsulationFault | INV062 | Inverter | DC Insulation Fault | Yes
ALM_INV062_DCOvervoltage | INV062_DCOvervoltage | INV062 | Inverter | DC Overvoltage | Yes
ALM_INV062_DeviceFault | INV062_DeviceFault | INV062 | Inverter | Device Fault | Yes
ALM_INV062_ExternalFanAbnormal | INV062_ExternalFanAbnormal | INV062 | Inverter | External fan abnormal | Yes
ALM_INV062_FanFailure | INV062_FanFailure | INV062 | Inverter | Fan Failure | Yes
ALM_INV062_Faulty | INV062_Faulty | INV062 | Inverter | Faulty | Yes
ALM_INV062_FaultyMonitoringUnit | INV062_FaultyMonitoringUnit | INV062 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV062_FaultyPowerCollector | INV062_FaultyPowerCollector | INV062 | Inverter | Faulty Power Collector | Yes
ALM_INV062_GeneralFaultTrip | INV062_GeneralFaultTrip | INV062 | Inverter | General Fault Trip | Yes
ALM_INV062_GridConnectionDeratingInverterInternalCauses | INV062_GridConnectionDeratingInverterInternalCauses | INV062 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV062_GridConnectionDeratingPowerRationing | INV062_GridConnectionDeratingPowerRationing | INV062 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV062_GridLoss | INV062_GridLoss | INV062 | Inverter | Grid Loss | Yes
ALM_INV062_GridOverfrequency | INV062_GridOverfrequency | INV062 | Inverter | Grid Overfrequency | Yes
ALM_INV062_GridOvervoltage | INV062_GridOvervoltage | INV062 | Inverter | Grid Overvoltage | Yes
ALM_INV062_GridTiedOffGridControllerAbnormal | INV062_GridTiedOffGridControllerAbnormal | INV062 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV062_GridUnderfrequency | INV062_GridUnderfrequency | INV062 | Inverter | Grid Underfrequency | Yes
ALM_INV062_GridUndervoltage | INV062_GridUndervoltage | INV062 | Inverter | Grid Undervoltage | Yes
ALM_INV062_GroundFault | INV062_GroundFault | INV062 | Inverter | Ground Fault | Yes
ALM_INV062_HighInputStringVoltageGround | INV062_HighInputStringVoltageGround | INV062 | Inverter | High input string voltage to ground | Yes
ALM_INV062_HighStringInputVoltage | INV062_HighStringInputVoltage | INV062 | Inverter | High string input voltage | Yes
ALM_INV062_InverterTripHistoryAvailable | INV062_InverterTripHistoryAvailable | INV062 | Inverter | Inverter Trip History Available | Yes
ALM_INV062_IslandingDetectionStatus | INV062_IslandingDetectionStatus | INV062 | Inverter | Islanding Detection Status | Yes
ALM_INV062_LicenseExpired | INV062_LicenseExpired | INV062 | Inverter | License Expired | Yes
ALM_INV062_LockingStatus | INV062_LockingStatus | INV062 | Inverter | Locking status | Yes
ALM_INV062_LowInsulationResistance | INV062_LowInsulationResistance | INV062 | Inverter | Low Insulation Resistance | Yes
ALM_INV062_OffGridOutputOverload | INV062_OffGridOutputOverload | INV062 | Inverter | Off-grid output overload | Yes
ALM_INV062_OptimizerFault | INV062_OptimizerFault | INV062 | Inverter | Optimizer fault | Yes
ALM_INV062_OutputDCComponentOverhigh | INV062_OutputDCComponentOverhigh | INV062 | Inverter | Output DC Component Overhigh | Yes
ALM_INV062_OutputOvercurrent | INV062_OutputOvercurrent | INV062 | Inverter | Output Overcurrent | Yes
ALM_INV062_PVStringLoss | INV062_PVStringLoss | INV062 | Inverter | PV String Loss | Yes
ALM_INV062_PassiveIslanding | INV062_PassiveIslanding | INV062 | Inverter | Passive Islanding | Yes
ALM_INV062_PeripheralPortShortCircuit | INV062_PeripheralPortShortCircuit | INV062 | Inverter | Peripheral port short circuit | Yes
ALM_INV062_PhaseWireShortCircuitedPE | INV062_PhaseWireShortCircuitedPE | INV062 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV062_PowerLimitationActiveGridCommand | INV062_PowerLimitationActiveGridCommand | INV062 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV062_StringReverseConnection | INV062_StringReverseConnection | INV062 | Inverter | String Reverse Connection | Yes
ALM_INV062_StringReversePolarity | INV062_StringReversePolarity | INV062 | Inverter | String Reverse Polarity | Yes
ALM_INV062_TransientACOvervoltage | INV062_TransientACOvervoltage | INV062 | Inverter | Transient AC Overvoltage | Yes
ALM_INV062_WarningActive | INV062_WarningActive | INV062 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV063_ACOvervoltage | INV063_ACOvervoltage | INV063 | Inverter | AC Overvoltage | Yes
ALM_INV063_ACUndervoltage | INV063_ACUndervoltage | INV063 | Inverter | AC Undervoltage | Yes
ALM_INV063_AFCISelfCheckFailure | INV063_AFCISelfCheckFailure | INV063 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV063_AbnormalGrounding | INV063_AbnormalGrounding | INV063 | Inverter | Abnormal Grounding | Yes
ALM_INV063_AbnormalPVModuleConfiguration | INV063_AbnormalPVModuleConfiguration | INV063 | Inverter | Abnormal PV module configuration | Yes
ALM_INV063_AbnormalResidualCurrent | INV063_AbnormalResidualCurrent | INV063 | Inverter | Abnormal Residual Current | Yes
ALM_INV063_AbnormalStringPower | INV063_AbnormalStringPower | INV063 | Inverter | Abnormal String Power | Yes
ALM_INV063_ActiveIslanding | INV063_ActiveIslanding | INV063 | Inverter | Active Islanding | Yes
ALM_INV063_BuiltPIDOperationAbnormal | INV063_BuiltPIDOperationAbnormal | INV063 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV063_CabinetOvertemperature | INV063_CabinetOvertemperature | INV063 | Inverter | Cabinet Overtemperature | Yes
ALM_INV063_CommunicationFailure | INV063_CommunicationFailure | INV063 | Inverter | Communication Failure | Yes
ALM_INV063_CommunicationStatus | INV063_CommunicationStatus | INV063 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV063_DCArcFault | INV063_DCArcFault | INV063 | Inverter | DC Arc Fault | Yes
ALM_INV063_DCInsulationFault | INV063_DCInsulationFault | INV063 | Inverter | DC Insulation Fault | Yes
ALM_INV063_DCOvervoltage | INV063_DCOvervoltage | INV063 | Inverter | DC Overvoltage | Yes
ALM_INV063_DeviceFault | INV063_DeviceFault | INV063 | Inverter | Device Fault | Yes
ALM_INV063_ExternalFanAbnormal | INV063_ExternalFanAbnormal | INV063 | Inverter | External fan abnormal | Yes
ALM_INV063_FanFailure | INV063_FanFailure | INV063 | Inverter | Fan Failure | Yes
ALM_INV063_Faulty | INV063_Faulty | INV063 | Inverter | Faulty | Yes
ALM_INV063_FaultyMonitoringUnit | INV063_FaultyMonitoringUnit | INV063 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV063_FaultyPowerCollector | INV063_FaultyPowerCollector | INV063 | Inverter | Faulty Power Collector | Yes
ALM_INV063_GeneralFaultTrip | INV063_GeneralFaultTrip | INV063 | Inverter | General Fault Trip | Yes
ALM_INV063_GridConnectionDeratingInverterInternalCauses | INV063_GridConnectionDeratingInverterInternalCauses | INV063 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV063_GridConnectionDeratingPowerRationing | INV063_GridConnectionDeratingPowerRationing | INV063 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV063_GridLoss | INV063_GridLoss | INV063 | Inverter | Grid Loss | Yes
ALM_INV063_GridOverfrequency | INV063_GridOverfrequency | INV063 | Inverter | Grid Overfrequency | Yes
ALM_INV063_GridOvervoltage | INV063_GridOvervoltage | INV063 | Inverter | Grid Overvoltage | Yes
ALM_INV063_GridTiedOffGridControllerAbnormal | INV063_GridTiedOffGridControllerAbnormal | INV063 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV063_GridUnderfrequency | INV063_GridUnderfrequency | INV063 | Inverter | Grid Underfrequency | Yes
ALM_INV063_GridUndervoltage | INV063_GridUndervoltage | INV063 | Inverter | Grid Undervoltage | Yes
ALM_INV063_GroundFault | INV063_GroundFault | INV063 | Inverter | Ground Fault | Yes
ALM_INV063_HighInputStringVoltageGround | INV063_HighInputStringVoltageGround | INV063 | Inverter | High input string voltage to ground | Yes
ALM_INV063_HighStringInputVoltage | INV063_HighStringInputVoltage | INV063 | Inverter | High string input voltage | Yes
ALM_INV063_InverterTripHistoryAvailable | INV063_InverterTripHistoryAvailable | INV063 | Inverter | Inverter Trip History Available | Yes
ALM_INV063_IslandingDetectionStatus | INV063_IslandingDetectionStatus | INV063 | Inverter | Islanding Detection Status | Yes
ALM_INV063_LicenseExpired | INV063_LicenseExpired | INV063 | Inverter | License Expired | Yes
ALM_INV063_LockingStatus | INV063_LockingStatus | INV063 | Inverter | Locking status | Yes
ALM_INV063_LowInsulationResistance | INV063_LowInsulationResistance | INV063 | Inverter | Low Insulation Resistance | Yes
ALM_INV063_OffGridOutputOverload | INV063_OffGridOutputOverload | INV063 | Inverter | Off-grid output overload | Yes
ALM_INV063_OptimizerFault | INV063_OptimizerFault | INV063 | Inverter | Optimizer fault | Yes
ALM_INV063_OutputDCComponentOverhigh | INV063_OutputDCComponentOverhigh | INV063 | Inverter | Output DC Component Overhigh | Yes
ALM_INV063_OutputOvercurrent | INV063_OutputOvercurrent | INV063 | Inverter | Output Overcurrent | Yes
ALM_INV063_PVStringLoss | INV063_PVStringLoss | INV063 | Inverter | PV String Loss | Yes
ALM_INV063_PassiveIslanding | INV063_PassiveIslanding | INV063 | Inverter | Passive Islanding | Yes
ALM_INV063_PeripheralPortShortCircuit | INV063_PeripheralPortShortCircuit | INV063 | Inverter | Peripheral port short circuit | Yes
ALM_INV063_PhaseWireShortCircuitedPE | INV063_PhaseWireShortCircuitedPE | INV063 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV063_PowerLimitationActiveGridCommand | INV063_PowerLimitationActiveGridCommand | INV063 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV063_StringReverseConnection | INV063_StringReverseConnection | INV063 | Inverter | String Reverse Connection | Yes
ALM_INV063_StringReversePolarity | INV063_StringReversePolarity | INV063 | Inverter | String Reverse Polarity | Yes
ALM_INV063_TransientACOvervoltage | INV063_TransientACOvervoltage | INV063 | Inverter | Transient AC Overvoltage | Yes
ALM_INV063_WarningActive | INV063_WarningActive | INV063 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV064_ACOvervoltage | INV064_ACOvervoltage | INV064 | Inverter | AC Overvoltage | Yes
ALM_INV064_ACUndervoltage | INV064_ACUndervoltage | INV064 | Inverter | AC Undervoltage | Yes
ALM_INV064_AFCISelfCheckFailure | INV064_AFCISelfCheckFailure | INV064 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV064_AbnormalGrounding | INV064_AbnormalGrounding | INV064 | Inverter | Abnormal Grounding | Yes
ALM_INV064_AbnormalPVModuleConfiguration | INV064_AbnormalPVModuleConfiguration | INV064 | Inverter | Abnormal PV module configuration | Yes
ALM_INV064_AbnormalResidualCurrent | INV064_AbnormalResidualCurrent | INV064 | Inverter | Abnormal Residual Current | Yes
ALM_INV064_AbnormalStringPower | INV064_AbnormalStringPower | INV064 | Inverter | Abnormal String Power | Yes
ALM_INV064_ActiveIslanding | INV064_ActiveIslanding | INV064 | Inverter | Active Islanding | Yes
ALM_INV064_BuiltPIDOperationAbnormal | INV064_BuiltPIDOperationAbnormal | INV064 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV064_CabinetOvertemperature | INV064_CabinetOvertemperature | INV064 | Inverter | Cabinet Overtemperature | Yes
ALM_INV064_CommunicationFailure | INV064_CommunicationFailure | INV064 | Inverter | Communication Failure | Yes
ALM_INV064_CommunicationStatus | INV064_CommunicationStatus | INV064 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV064_DCArcFault | INV064_DCArcFault | INV064 | Inverter | DC Arc Fault | Yes
ALM_INV064_DCInsulationFault | INV064_DCInsulationFault | INV064 | Inverter | DC Insulation Fault | Yes
ALM_INV064_DCOvervoltage | INV064_DCOvervoltage | INV064 | Inverter | DC Overvoltage | Yes
ALM_INV064_DeviceFault | INV064_DeviceFault | INV064 | Inverter | Device Fault | Yes
ALM_INV064_ExternalFanAbnormal | INV064_ExternalFanAbnormal | INV064 | Inverter | External fan abnormal | Yes
ALM_INV064_FanFailure | INV064_FanFailure | INV064 | Inverter | Fan Failure | Yes
ALM_INV064_Faulty | INV064_Faulty | INV064 | Inverter | Faulty | Yes
ALM_INV064_FaultyMonitoringUnit | INV064_FaultyMonitoringUnit | INV064 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV064_FaultyPowerCollector | INV064_FaultyPowerCollector | INV064 | Inverter | Faulty Power Collector | Yes
ALM_INV064_GeneralFaultTrip | INV064_GeneralFaultTrip | INV064 | Inverter | General Fault Trip | Yes
ALM_INV064_GridConnectionDeratingInverterInternalCauses | INV064_GridConnectionDeratingInverterInternalCauses | INV064 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV064_GridConnectionDeratingPowerRationing | INV064_GridConnectionDeratingPowerRationing | INV064 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV064_GridLoss | INV064_GridLoss | INV064 | Inverter | Grid Loss | Yes
ALM_INV064_GridOverfrequency | INV064_GridOverfrequency | INV064 | Inverter | Grid Overfrequency | Yes
ALM_INV064_GridOvervoltage | INV064_GridOvervoltage | INV064 | Inverter | Grid Overvoltage | Yes
ALM_INV064_GridTiedOffGridControllerAbnormal | INV064_GridTiedOffGridControllerAbnormal | INV064 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV064_GridUnderfrequency | INV064_GridUnderfrequency | INV064 | Inverter | Grid Underfrequency | Yes
ALM_INV064_GridUndervoltage | INV064_GridUndervoltage | INV064 | Inverter | Grid Undervoltage | Yes
ALM_INV064_GroundFault | INV064_GroundFault | INV064 | Inverter | Ground Fault | Yes
ALM_INV064_HighInputStringVoltageGround | INV064_HighInputStringVoltageGround | INV064 | Inverter | High input string voltage to ground | Yes
ALM_INV064_HighStringInputVoltage | INV064_HighStringInputVoltage | INV064 | Inverter | High string input voltage | Yes
ALM_INV064_InverterTripHistoryAvailable | INV064_InverterTripHistoryAvailable | INV064 | Inverter | Inverter Trip History Available | Yes
ALM_INV064_IslandingDetectionStatus | INV064_IslandingDetectionStatus | INV064 | Inverter | Islanding Detection Status | Yes
ALM_INV064_LicenseExpired | INV064_LicenseExpired | INV064 | Inverter | License Expired | Yes
ALM_INV064_LockingStatus | INV064_LockingStatus | INV064 | Inverter | Locking status | Yes
ALM_INV064_LowInsulationResistance | INV064_LowInsulationResistance | INV064 | Inverter | Low Insulation Resistance | Yes
ALM_INV064_OffGridOutputOverload | INV064_OffGridOutputOverload | INV064 | Inverter | Off-grid output overload | Yes
ALM_INV064_OptimizerFault | INV064_OptimizerFault | INV064 | Inverter | Optimizer fault | Yes
ALM_INV064_OutputDCComponentOverhigh | INV064_OutputDCComponentOverhigh | INV064 | Inverter | Output DC Component Overhigh | Yes
ALM_INV064_OutputOvercurrent | INV064_OutputOvercurrent | INV064 | Inverter | Output Overcurrent | Yes
ALM_INV064_PVStringLoss | INV064_PVStringLoss | INV064 | Inverter | PV String Loss | Yes
ALM_INV064_PassiveIslanding | INV064_PassiveIslanding | INV064 | Inverter | Passive Islanding | Yes
ALM_INV064_PeripheralPortShortCircuit | INV064_PeripheralPortShortCircuit | INV064 | Inverter | Peripheral port short circuit | Yes
ALM_INV064_PhaseWireShortCircuitedPE | INV064_PhaseWireShortCircuitedPE | INV064 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV064_PowerLimitationActiveGridCommand | INV064_PowerLimitationActiveGridCommand | INV064 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV064_StringReverseConnection | INV064_StringReverseConnection | INV064 | Inverter | String Reverse Connection | Yes
ALM_INV064_StringReversePolarity | INV064_StringReversePolarity | INV064 | Inverter | String Reverse Polarity | Yes
ALM_INV064_TransientACOvervoltage | INV064_TransientACOvervoltage | INV064 | Inverter | Transient AC Overvoltage | Yes
ALM_INV064_WarningActive | INV064_WarningActive | INV064 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV065_ACOvervoltage | INV065_ACOvervoltage | INV065 | Inverter | AC Overvoltage | Yes
ALM_INV065_ACUndervoltage | INV065_ACUndervoltage | INV065 | Inverter | AC Undervoltage | Yes
ALM_INV065_AFCISelfCheckFailure | INV065_AFCISelfCheckFailure | INV065 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV065_AbnormalGrounding | INV065_AbnormalGrounding | INV065 | Inverter | Abnormal Grounding | Yes
ALM_INV065_AbnormalPVModuleConfiguration | INV065_AbnormalPVModuleConfiguration | INV065 | Inverter | Abnormal PV module configuration | Yes
ALM_INV065_AbnormalResidualCurrent | INV065_AbnormalResidualCurrent | INV065 | Inverter | Abnormal Residual Current | Yes
ALM_INV065_AbnormalStringPower | INV065_AbnormalStringPower | INV065 | Inverter | Abnormal String Power | Yes
ALM_INV065_ActiveIslanding | INV065_ActiveIslanding | INV065 | Inverter | Active Islanding | Yes
ALM_INV065_BuiltPIDOperationAbnormal | INV065_BuiltPIDOperationAbnormal | INV065 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV065_CabinetOvertemperature | INV065_CabinetOvertemperature | INV065 | Inverter | Cabinet Overtemperature | Yes
ALM_INV065_CommunicationFailure | INV065_CommunicationFailure | INV065 | Inverter | Communication Failure | Yes
ALM_INV065_CommunicationStatus | INV065_CommunicationStatus | INV065 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV065_DCArcFault | INV065_DCArcFault | INV065 | Inverter | DC Arc Fault | Yes
ALM_INV065_DCInsulationFault | INV065_DCInsulationFault | INV065 | Inverter | DC Insulation Fault | Yes
ALM_INV065_DCOvervoltage | INV065_DCOvervoltage | INV065 | Inverter | DC Overvoltage | Yes
ALM_INV065_DeviceFault | INV065_DeviceFault | INV065 | Inverter | Device Fault | Yes
ALM_INV065_ExternalFanAbnormal | INV065_ExternalFanAbnormal | INV065 | Inverter | External fan abnormal | Yes
ALM_INV065_FanFailure | INV065_FanFailure | INV065 | Inverter | Fan Failure | Yes
ALM_INV065_Faulty | INV065_Faulty | INV065 | Inverter | Faulty | Yes
ALM_INV065_FaultyMonitoringUnit | INV065_FaultyMonitoringUnit | INV065 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV065_FaultyPowerCollector | INV065_FaultyPowerCollector | INV065 | Inverter | Faulty Power Collector | Yes
ALM_INV065_GeneralFaultTrip | INV065_GeneralFaultTrip | INV065 | Inverter | General Fault Trip | Yes
ALM_INV065_GridConnectionDeratingInverterInternalCauses | INV065_GridConnectionDeratingInverterInternalCauses | INV065 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV065_GridConnectionDeratingPowerRationing | INV065_GridConnectionDeratingPowerRationing | INV065 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV065_GridLoss | INV065_GridLoss | INV065 | Inverter | Grid Loss | Yes
ALM_INV065_GridOverfrequency | INV065_GridOverfrequency | INV065 | Inverter | Grid Overfrequency | Yes
ALM_INV065_GridOvervoltage | INV065_GridOvervoltage | INV065 | Inverter | Grid Overvoltage | Yes
ALM_INV065_GridTiedOffGridControllerAbnormal | INV065_GridTiedOffGridControllerAbnormal | INV065 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV065_GridUnderfrequency | INV065_GridUnderfrequency | INV065 | Inverter | Grid Underfrequency | Yes
ALM_INV065_GridUndervoltage | INV065_GridUndervoltage | INV065 | Inverter | Grid Undervoltage | Yes
ALM_INV065_GroundFault | INV065_GroundFault | INV065 | Inverter | Ground Fault | Yes
ALM_INV065_HighInputStringVoltageGround | INV065_HighInputStringVoltageGround | INV065 | Inverter | High input string voltage to ground | Yes
ALM_INV065_HighStringInputVoltage | INV065_HighStringInputVoltage | INV065 | Inverter | High string input voltage | Yes
ALM_INV065_InverterTripHistoryAvailable | INV065_InverterTripHistoryAvailable | INV065 | Inverter | Inverter Trip History Available | Yes
ALM_INV065_IslandingDetectionStatus | INV065_IslandingDetectionStatus | INV065 | Inverter | Islanding Detection Status | Yes
ALM_INV065_LicenseExpired | INV065_LicenseExpired | INV065 | Inverter | License Expired | Yes
ALM_INV065_LockingStatus | INV065_LockingStatus | INV065 | Inverter | Locking status | Yes
ALM_INV065_LowInsulationResistance | INV065_LowInsulationResistance | INV065 | Inverter | Low Insulation Resistance | Yes
ALM_INV065_OffGridOutputOverload | INV065_OffGridOutputOverload | INV065 | Inverter | Off-grid output overload | Yes
ALM_INV065_OptimizerFault | INV065_OptimizerFault | INV065 | Inverter | Optimizer fault | Yes
ALM_INV065_OutputDCComponentOverhigh | INV065_OutputDCComponentOverhigh | INV065 | Inverter | Output DC Component Overhigh | Yes
ALM_INV065_OutputOvercurrent | INV065_OutputOvercurrent | INV065 | Inverter | Output Overcurrent | Yes
ALM_INV065_PVStringLoss | INV065_PVStringLoss | INV065 | Inverter | PV String Loss | Yes
ALM_INV065_PassiveIslanding | INV065_PassiveIslanding | INV065 | Inverter | Passive Islanding | Yes
ALM_INV065_PeripheralPortShortCircuit | INV065_PeripheralPortShortCircuit | INV065 | Inverter | Peripheral port short circuit | Yes
ALM_INV065_PhaseWireShortCircuitedPE | INV065_PhaseWireShortCircuitedPE | INV065 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV065_PowerLimitationActiveGridCommand | INV065_PowerLimitationActiveGridCommand | INV065 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV065_StringReverseConnection | INV065_StringReverseConnection | INV065 | Inverter | String Reverse Connection | Yes
ALM_INV065_StringReversePolarity | INV065_StringReversePolarity | INV065 | Inverter | String Reverse Polarity | Yes
ALM_INV065_TransientACOvervoltage | INV065_TransientACOvervoltage | INV065 | Inverter | Transient AC Overvoltage | Yes
ALM_INV065_WarningActive | INV065_WarningActive | INV065 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV066_ACOvervoltage | INV066_ACOvervoltage | INV066 | Inverter | AC Overvoltage | Yes
ALM_INV066_ACUndervoltage | INV066_ACUndervoltage | INV066 | Inverter | AC Undervoltage | Yes
ALM_INV066_AFCISelfCheckFailure | INV066_AFCISelfCheckFailure | INV066 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV066_AbnormalGrounding | INV066_AbnormalGrounding | INV066 | Inverter | Abnormal Grounding | Yes
ALM_INV066_AbnormalPVModuleConfiguration | INV066_AbnormalPVModuleConfiguration | INV066 | Inverter | Abnormal PV module configuration | Yes
ALM_INV066_AbnormalResidualCurrent | INV066_AbnormalResidualCurrent | INV066 | Inverter | Abnormal Residual Current | Yes
ALM_INV066_AbnormalStringPower | INV066_AbnormalStringPower | INV066 | Inverter | Abnormal String Power | Yes
ALM_INV066_ActiveIslanding | INV066_ActiveIslanding | INV066 | Inverter | Active Islanding | Yes
ALM_INV066_BuiltPIDOperationAbnormal | INV066_BuiltPIDOperationAbnormal | INV066 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV066_CabinetOvertemperature | INV066_CabinetOvertemperature | INV066 | Inverter | Cabinet Overtemperature | Yes
ALM_INV066_CommunicationFailure | INV066_CommunicationFailure | INV066 | Inverter | Communication Failure | Yes
ALM_INV066_CommunicationStatus | INV066_CommunicationStatus | INV066 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV066_DCArcFault | INV066_DCArcFault | INV066 | Inverter | DC Arc Fault | Yes
ALM_INV066_DCInsulationFault | INV066_DCInsulationFault | INV066 | Inverter | DC Insulation Fault | Yes
ALM_INV066_DCOvervoltage | INV066_DCOvervoltage | INV066 | Inverter | DC Overvoltage | Yes
ALM_INV066_DeviceFault | INV066_DeviceFault | INV066 | Inverter | Device Fault | Yes
ALM_INV066_ExternalFanAbnormal | INV066_ExternalFanAbnormal | INV066 | Inverter | External fan abnormal | Yes
ALM_INV066_FanFailure | INV066_FanFailure | INV066 | Inverter | Fan Failure | Yes
ALM_INV066_Faulty | INV066_Faulty | INV066 | Inverter | Faulty | Yes
ALM_INV066_FaultyMonitoringUnit | INV066_FaultyMonitoringUnit | INV066 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV066_FaultyPowerCollector | INV066_FaultyPowerCollector | INV066 | Inverter | Faulty Power Collector | Yes
ALM_INV066_GeneralFaultTrip | INV066_GeneralFaultTrip | INV066 | Inverter | General Fault Trip | Yes
ALM_INV066_GridConnectionDeratingInverterInternalCauses | INV066_GridConnectionDeratingInverterInternalCauses | INV066 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV066_GridConnectionDeratingPowerRationing | INV066_GridConnectionDeratingPowerRationing | INV066 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV066_GridLoss | INV066_GridLoss | INV066 | Inverter | Grid Loss | Yes
ALM_INV066_GridOverfrequency | INV066_GridOverfrequency | INV066 | Inverter | Grid Overfrequency | Yes
ALM_INV066_GridOvervoltage | INV066_GridOvervoltage | INV066 | Inverter | Grid Overvoltage | Yes
ALM_INV066_GridTiedOffGridControllerAbnormal | INV066_GridTiedOffGridControllerAbnormal | INV066 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV066_GridUnderfrequency | INV066_GridUnderfrequency | INV066 | Inverter | Grid Underfrequency | Yes
ALM_INV066_GridUndervoltage | INV066_GridUndervoltage | INV066 | Inverter | Grid Undervoltage | Yes
ALM_INV066_GroundFault | INV066_GroundFault | INV066 | Inverter | Ground Fault | Yes
ALM_INV066_HighInputStringVoltageGround | INV066_HighInputStringVoltageGround | INV066 | Inverter | High input string voltage to ground | Yes
ALM_INV066_HighStringInputVoltage | INV066_HighStringInputVoltage | INV066 | Inverter | High string input voltage | Yes
ALM_INV066_InverterTripHistoryAvailable | INV066_InverterTripHistoryAvailable | INV066 | Inverter | Inverter Trip History Available | Yes
ALM_INV066_IslandingDetectionStatus | INV066_IslandingDetectionStatus | INV066 | Inverter | Islanding Detection Status | Yes
ALM_INV066_LicenseExpired | INV066_LicenseExpired | INV066 | Inverter | License Expired | Yes
ALM_INV066_LockingStatus | INV066_LockingStatus | INV066 | Inverter | Locking status | Yes
ALM_INV066_LowInsulationResistance | INV066_LowInsulationResistance | INV066 | Inverter | Low Insulation Resistance | Yes
ALM_INV066_OffGridOutputOverload | INV066_OffGridOutputOverload | INV066 | Inverter | Off-grid output overload | Yes
ALM_INV066_OptimizerFault | INV066_OptimizerFault | INV066 | Inverter | Optimizer fault | Yes
ALM_INV066_OutputDCComponentOverhigh | INV066_OutputDCComponentOverhigh | INV066 | Inverter | Output DC Component Overhigh | Yes
ALM_INV066_OutputOvercurrent | INV066_OutputOvercurrent | INV066 | Inverter | Output Overcurrent | Yes
ALM_INV066_PVStringLoss | INV066_PVStringLoss | INV066 | Inverter | PV String Loss | Yes
ALM_INV066_PassiveIslanding | INV066_PassiveIslanding | INV066 | Inverter | Passive Islanding | Yes
ALM_INV066_PeripheralPortShortCircuit | INV066_PeripheralPortShortCircuit | INV066 | Inverter | Peripheral port short circuit | Yes
ALM_INV066_PhaseWireShortCircuitedPE | INV066_PhaseWireShortCircuitedPE | INV066 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV066_PowerLimitationActiveGridCommand | INV066_PowerLimitationActiveGridCommand | INV066 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV066_StringReverseConnection | INV066_StringReverseConnection | INV066 | Inverter | String Reverse Connection | Yes
ALM_INV066_StringReversePolarity | INV066_StringReversePolarity | INV066 | Inverter | String Reverse Polarity | Yes
ALM_INV066_TransientACOvervoltage | INV066_TransientACOvervoltage | INV066 | Inverter | Transient AC Overvoltage | Yes
ALM_INV066_WarningActive | INV066_WarningActive | INV066 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV067_ACOvervoltage | INV067_ACOvervoltage | INV067 | Inverter | AC Overvoltage | Yes
ALM_INV067_ACUndervoltage | INV067_ACUndervoltage | INV067 | Inverter | AC Undervoltage | Yes
ALM_INV067_AFCISelfCheckFailure | INV067_AFCISelfCheckFailure | INV067 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV067_AbnormalGrounding | INV067_AbnormalGrounding | INV067 | Inverter | Abnormal Grounding | Yes
ALM_INV067_AbnormalPVModuleConfiguration | INV067_AbnormalPVModuleConfiguration | INV067 | Inverter | Abnormal PV module configuration | Yes
ALM_INV067_AbnormalResidualCurrent | INV067_AbnormalResidualCurrent | INV067 | Inverter | Abnormal Residual Current | Yes
ALM_INV067_AbnormalStringPower | INV067_AbnormalStringPower | INV067 | Inverter | Abnormal String Power | Yes
ALM_INV067_ActiveIslanding | INV067_ActiveIslanding | INV067 | Inverter | Active Islanding | Yes
ALM_INV067_BuiltPIDOperationAbnormal | INV067_BuiltPIDOperationAbnormal | INV067 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV067_CabinetOvertemperature | INV067_CabinetOvertemperature | INV067 | Inverter | Cabinet Overtemperature | Yes
ALM_INV067_CommunicationFailure | INV067_CommunicationFailure | INV067 | Inverter | Communication Failure | Yes
ALM_INV067_CommunicationStatus | INV067_CommunicationStatus | INV067 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV067_DCArcFault | INV067_DCArcFault | INV067 | Inverter | DC Arc Fault | Yes
ALM_INV067_DCInsulationFault | INV067_DCInsulationFault | INV067 | Inverter | DC Insulation Fault | Yes
ALM_INV067_DCOvervoltage | INV067_DCOvervoltage | INV067 | Inverter | DC Overvoltage | Yes
ALM_INV067_DeviceFault | INV067_DeviceFault | INV067 | Inverter | Device Fault | Yes
ALM_INV067_ExternalFanAbnormal | INV067_ExternalFanAbnormal | INV067 | Inverter | External fan abnormal | Yes
ALM_INV067_FanFailure | INV067_FanFailure | INV067 | Inverter | Fan Failure | Yes
ALM_INV067_Faulty | INV067_Faulty | INV067 | Inverter | Faulty | Yes
ALM_INV067_FaultyMonitoringUnit | INV067_FaultyMonitoringUnit | INV067 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV067_FaultyPowerCollector | INV067_FaultyPowerCollector | INV067 | Inverter | Faulty Power Collector | Yes
ALM_INV067_GeneralFaultTrip | INV067_GeneralFaultTrip | INV067 | Inverter | General Fault Trip | Yes
ALM_INV067_GridConnectionDeratingInverterInternalCauses | INV067_GridConnectionDeratingInverterInternalCauses | INV067 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV067_GridConnectionDeratingPowerRationing | INV067_GridConnectionDeratingPowerRationing | INV067 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV067_GridLoss | INV067_GridLoss | INV067 | Inverter | Grid Loss | Yes
ALM_INV067_GridOverfrequency | INV067_GridOverfrequency | INV067 | Inverter | Grid Overfrequency | Yes
ALM_INV067_GridOvervoltage | INV067_GridOvervoltage | INV067 | Inverter | Grid Overvoltage | Yes
ALM_INV067_GridTiedOffGridControllerAbnormal | INV067_GridTiedOffGridControllerAbnormal | INV067 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV067_GridUnderfrequency | INV067_GridUnderfrequency | INV067 | Inverter | Grid Underfrequency | Yes
ALM_INV067_GridUndervoltage | INV067_GridUndervoltage | INV067 | Inverter | Grid Undervoltage | Yes
ALM_INV067_GroundFault | INV067_GroundFault | INV067 | Inverter | Ground Fault | Yes
ALM_INV067_HighInputStringVoltageGround | INV067_HighInputStringVoltageGround | INV067 | Inverter | High input string voltage to ground | Yes
ALM_INV067_HighStringInputVoltage | INV067_HighStringInputVoltage | INV067 | Inverter | High string input voltage | Yes
ALM_INV067_InverterTripHistoryAvailable | INV067_InverterTripHistoryAvailable | INV067 | Inverter | Inverter Trip History Available | Yes
ALM_INV067_IslandingDetectionStatus | INV067_IslandingDetectionStatus | INV067 | Inverter | Islanding Detection Status | Yes
ALM_INV067_LicenseExpired | INV067_LicenseExpired | INV067 | Inverter | License Expired | Yes
ALM_INV067_LockingStatus | INV067_LockingStatus | INV067 | Inverter | Locking status | Yes
ALM_INV067_LowInsulationResistance | INV067_LowInsulationResistance | INV067 | Inverter | Low Insulation Resistance | Yes
ALM_INV067_OffGridOutputOverload | INV067_OffGridOutputOverload | INV067 | Inverter | Off-grid output overload | Yes
ALM_INV067_OptimizerFault | INV067_OptimizerFault | INV067 | Inverter | Optimizer fault | Yes
ALM_INV067_OutputDCComponentOverhigh | INV067_OutputDCComponentOverhigh | INV067 | Inverter | Output DC Component Overhigh | Yes
ALM_INV067_OutputOvercurrent | INV067_OutputOvercurrent | INV067 | Inverter | Output Overcurrent | Yes
ALM_INV067_PVStringLoss | INV067_PVStringLoss | INV067 | Inverter | PV String Loss | Yes
ALM_INV067_PassiveIslanding | INV067_PassiveIslanding | INV067 | Inverter | Passive Islanding | Yes
ALM_INV067_PeripheralPortShortCircuit | INV067_PeripheralPortShortCircuit | INV067 | Inverter | Peripheral port short circuit | Yes
ALM_INV067_PhaseWireShortCircuitedPE | INV067_PhaseWireShortCircuitedPE | INV067 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV067_PowerLimitationActiveGridCommand | INV067_PowerLimitationActiveGridCommand | INV067 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV067_StringReverseConnection | INV067_StringReverseConnection | INV067 | Inverter | String Reverse Connection | Yes
ALM_INV067_StringReversePolarity | INV067_StringReversePolarity | INV067 | Inverter | String Reverse Polarity | Yes
ALM_INV067_TransientACOvervoltage | INV067_TransientACOvervoltage | INV067 | Inverter | Transient AC Overvoltage | Yes
ALM_INV067_WarningActive | INV067_WarningActive | INV067 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV068_ACOvervoltage | INV068_ACOvervoltage | INV068 | Inverter | AC Overvoltage | Yes
ALM_INV068_ACUndervoltage | INV068_ACUndervoltage | INV068 | Inverter | AC Undervoltage | Yes
ALM_INV068_AFCISelfCheckFailure | INV068_AFCISelfCheckFailure | INV068 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV068_AbnormalGrounding | INV068_AbnormalGrounding | INV068 | Inverter | Abnormal Grounding | Yes
ALM_INV068_AbnormalPVModuleConfiguration | INV068_AbnormalPVModuleConfiguration | INV068 | Inverter | Abnormal PV module configuration | Yes
ALM_INV068_AbnormalResidualCurrent | INV068_AbnormalResidualCurrent | INV068 | Inverter | Abnormal Residual Current | Yes
ALM_INV068_AbnormalStringPower | INV068_AbnormalStringPower | INV068 | Inverter | Abnormal String Power | Yes
ALM_INV068_ActiveIslanding | INV068_ActiveIslanding | INV068 | Inverter | Active Islanding | Yes
ALM_INV068_BuiltPIDOperationAbnormal | INV068_BuiltPIDOperationAbnormal | INV068 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV068_CabinetOvertemperature | INV068_CabinetOvertemperature | INV068 | Inverter | Cabinet Overtemperature | Yes
ALM_INV068_CommunicationFailure | INV068_CommunicationFailure | INV068 | Inverter | Communication Failure | Yes
ALM_INV068_CommunicationStatus | INV068_CommunicationStatus | INV068 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV068_DCArcFault | INV068_DCArcFault | INV068 | Inverter | DC Arc Fault | Yes
ALM_INV068_DCInsulationFault | INV068_DCInsulationFault | INV068 | Inverter | DC Insulation Fault | Yes
ALM_INV068_DCOvervoltage | INV068_DCOvervoltage | INV068 | Inverter | DC Overvoltage | Yes
ALM_INV068_DeviceFault | INV068_DeviceFault | INV068 | Inverter | Device Fault | Yes
ALM_INV068_ExternalFanAbnormal | INV068_ExternalFanAbnormal | INV068 | Inverter | External fan abnormal | Yes
ALM_INV068_FanFailure | INV068_FanFailure | INV068 | Inverter | Fan Failure | Yes
ALM_INV068_Faulty | INV068_Faulty | INV068 | Inverter | Faulty | Yes
ALM_INV068_FaultyMonitoringUnit | INV068_FaultyMonitoringUnit | INV068 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV068_FaultyPowerCollector | INV068_FaultyPowerCollector | INV068 | Inverter | Faulty Power Collector | Yes
ALM_INV068_GeneralFaultTrip | INV068_GeneralFaultTrip | INV068 | Inverter | General Fault Trip | Yes
ALM_INV068_GridConnectionDeratingInverterInternalCauses | INV068_GridConnectionDeratingInverterInternalCauses | INV068 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV068_GridConnectionDeratingPowerRationing | INV068_GridConnectionDeratingPowerRationing | INV068 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV068_GridLoss | INV068_GridLoss | INV068 | Inverter | Grid Loss | Yes
ALM_INV068_GridOverfrequency | INV068_GridOverfrequency | INV068 | Inverter | Grid Overfrequency | Yes
ALM_INV068_GridOvervoltage | INV068_GridOvervoltage | INV068 | Inverter | Grid Overvoltage | Yes
ALM_INV068_GridTiedOffGridControllerAbnormal | INV068_GridTiedOffGridControllerAbnormal | INV068 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV068_GridUnderfrequency | INV068_GridUnderfrequency | INV068 | Inverter | Grid Underfrequency | Yes
ALM_INV068_GridUndervoltage | INV068_GridUndervoltage | INV068 | Inverter | Grid Undervoltage | Yes
ALM_INV068_GroundFault | INV068_GroundFault | INV068 | Inverter | Ground Fault | Yes
ALM_INV068_HighInputStringVoltageGround | INV068_HighInputStringVoltageGround | INV068 | Inverter | High input string voltage to ground | Yes
ALM_INV068_HighStringInputVoltage | INV068_HighStringInputVoltage | INV068 | Inverter | High string input voltage | Yes
ALM_INV068_InverterTripHistoryAvailable | INV068_InverterTripHistoryAvailable | INV068 | Inverter | Inverter Trip History Available | Yes
ALM_INV068_IslandingDetectionStatus | INV068_IslandingDetectionStatus | INV068 | Inverter | Islanding Detection Status | Yes
ALM_INV068_LicenseExpired | INV068_LicenseExpired | INV068 | Inverter | License Expired | Yes
ALM_INV068_LockingStatus | INV068_LockingStatus | INV068 | Inverter | Locking status | Yes
ALM_INV068_LowInsulationResistance | INV068_LowInsulationResistance | INV068 | Inverter | Low Insulation Resistance | Yes
ALM_INV068_OffGridOutputOverload | INV068_OffGridOutputOverload | INV068 | Inverter | Off-grid output overload | Yes
ALM_INV068_OptimizerFault | INV068_OptimizerFault | INV068 | Inverter | Optimizer fault | Yes
ALM_INV068_OutputDCComponentOverhigh | INV068_OutputDCComponentOverhigh | INV068 | Inverter | Output DC Component Overhigh | Yes
ALM_INV068_OutputOvercurrent | INV068_OutputOvercurrent | INV068 | Inverter | Output Overcurrent | Yes
ALM_INV068_PVStringLoss | INV068_PVStringLoss | INV068 | Inverter | PV String Loss | Yes
ALM_INV068_PassiveIslanding | INV068_PassiveIslanding | INV068 | Inverter | Passive Islanding | Yes
ALM_INV068_PeripheralPortShortCircuit | INV068_PeripheralPortShortCircuit | INV068 | Inverter | Peripheral port short circuit | Yes
ALM_INV068_PhaseWireShortCircuitedPE | INV068_PhaseWireShortCircuitedPE | INV068 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV068_PowerLimitationActiveGridCommand | INV068_PowerLimitationActiveGridCommand | INV068 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV068_StringReverseConnection | INV068_StringReverseConnection | INV068 | Inverter | String Reverse Connection | Yes
ALM_INV068_StringReversePolarity | INV068_StringReversePolarity | INV068 | Inverter | String Reverse Polarity | Yes
ALM_INV068_TransientACOvervoltage | INV068_TransientACOvervoltage | INV068 | Inverter | Transient AC Overvoltage | Yes
ALM_INV068_WarningActive | INV068_WarningActive | INV068 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV069_ACOvervoltage | INV069_ACOvervoltage | INV069 | Inverter | AC Overvoltage | Yes
ALM_INV069_ACUndervoltage | INV069_ACUndervoltage | INV069 | Inverter | AC Undervoltage | Yes
ALM_INV069_AFCISelfCheckFailure | INV069_AFCISelfCheckFailure | INV069 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV069_AbnormalGrounding | INV069_AbnormalGrounding | INV069 | Inverter | Abnormal Grounding | Yes
ALM_INV069_AbnormalPVModuleConfiguration | INV069_AbnormalPVModuleConfiguration | INV069 | Inverter | Abnormal PV module configuration | Yes
ALM_INV069_AbnormalResidualCurrent | INV069_AbnormalResidualCurrent | INV069 | Inverter | Abnormal Residual Current | Yes
ALM_INV069_AbnormalStringPower | INV069_AbnormalStringPower | INV069 | Inverter | Abnormal String Power | Yes
ALM_INV069_ActiveIslanding | INV069_ActiveIslanding | INV069 | Inverter | Active Islanding | Yes
ALM_INV069_BuiltPIDOperationAbnormal | INV069_BuiltPIDOperationAbnormal | INV069 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV069_CabinetOvertemperature | INV069_CabinetOvertemperature | INV069 | Inverter | Cabinet Overtemperature | Yes
ALM_INV069_CommunicationFailure | INV069_CommunicationFailure | INV069 | Inverter | Communication Failure | Yes
ALM_INV069_CommunicationStatus | INV069_CommunicationStatus | INV069 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV069_DCArcFault | INV069_DCArcFault | INV069 | Inverter | DC Arc Fault | Yes
ALM_INV069_DCInsulationFault | INV069_DCInsulationFault | INV069 | Inverter | DC Insulation Fault | Yes
ALM_INV069_DCOvervoltage | INV069_DCOvervoltage | INV069 | Inverter | DC Overvoltage | Yes
ALM_INV069_DeviceFault | INV069_DeviceFault | INV069 | Inverter | Device Fault | Yes
ALM_INV069_ExternalFanAbnormal | INV069_ExternalFanAbnormal | INV069 | Inverter | External fan abnormal | Yes
ALM_INV069_FanFailure | INV069_FanFailure | INV069 | Inverter | Fan Failure | Yes
ALM_INV069_Faulty | INV069_Faulty | INV069 | Inverter | Faulty | Yes
ALM_INV069_FaultyMonitoringUnit | INV069_FaultyMonitoringUnit | INV069 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV069_FaultyPowerCollector | INV069_FaultyPowerCollector | INV069 | Inverter | Faulty Power Collector | Yes
ALM_INV069_GeneralFaultTrip | INV069_GeneralFaultTrip | INV069 | Inverter | General Fault Trip | Yes
ALM_INV069_GridConnectionDeratingInverterInternalCauses | INV069_GridConnectionDeratingInverterInternalCauses | INV069 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV069_GridConnectionDeratingPowerRationing | INV069_GridConnectionDeratingPowerRationing | INV069 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV069_GridLoss | INV069_GridLoss | INV069 | Inverter | Grid Loss | Yes
ALM_INV069_GridOverfrequency | INV069_GridOverfrequency | INV069 | Inverter | Grid Overfrequency | Yes
ALM_INV069_GridOvervoltage | INV069_GridOvervoltage | INV069 | Inverter | Grid Overvoltage | Yes
ALM_INV069_GridTiedOffGridControllerAbnormal | INV069_GridTiedOffGridControllerAbnormal | INV069 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV069_GridUnderfrequency | INV069_GridUnderfrequency | INV069 | Inverter | Grid Underfrequency | Yes
ALM_INV069_GridUndervoltage | INV069_GridUndervoltage | INV069 | Inverter | Grid Undervoltage | Yes
ALM_INV069_GroundFault | INV069_GroundFault | INV069 | Inverter | Ground Fault | Yes
ALM_INV069_HighInputStringVoltageGround | INV069_HighInputStringVoltageGround | INV069 | Inverter | High input string voltage to ground | Yes
ALM_INV069_HighStringInputVoltage | INV069_HighStringInputVoltage | INV069 | Inverter | High string input voltage | Yes
ALM_INV069_InverterTripHistoryAvailable | INV069_InverterTripHistoryAvailable | INV069 | Inverter | Inverter Trip History Available | Yes
ALM_INV069_IslandingDetectionStatus | INV069_IslandingDetectionStatus | INV069 | Inverter | Islanding Detection Status | Yes
ALM_INV069_LicenseExpired | INV069_LicenseExpired | INV069 | Inverter | License Expired | Yes
ALM_INV069_LockingStatus | INV069_LockingStatus | INV069 | Inverter | Locking status | Yes
ALM_INV069_LowInsulationResistance | INV069_LowInsulationResistance | INV069 | Inverter | Low Insulation Resistance | Yes
ALM_INV069_OffGridOutputOverload | INV069_OffGridOutputOverload | INV069 | Inverter | Off-grid output overload | Yes
ALM_INV069_OptimizerFault | INV069_OptimizerFault | INV069 | Inverter | Optimizer fault | Yes
ALM_INV069_OutputDCComponentOverhigh | INV069_OutputDCComponentOverhigh | INV069 | Inverter | Output DC Component Overhigh | Yes
ALM_INV069_OutputOvercurrent | INV069_OutputOvercurrent | INV069 | Inverter | Output Overcurrent | Yes
ALM_INV069_PVStringLoss | INV069_PVStringLoss | INV069 | Inverter | PV String Loss | Yes
ALM_INV069_PassiveIslanding | INV069_PassiveIslanding | INV069 | Inverter | Passive Islanding | Yes
ALM_INV069_PeripheralPortShortCircuit | INV069_PeripheralPortShortCircuit | INV069 | Inverter | Peripheral port short circuit | Yes
ALM_INV069_PhaseWireShortCircuitedPE | INV069_PhaseWireShortCircuitedPE | INV069 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV069_PowerLimitationActiveGridCommand | INV069_PowerLimitationActiveGridCommand | INV069 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV069_StringReverseConnection | INV069_StringReverseConnection | INV069 | Inverter | String Reverse Connection | Yes
ALM_INV069_StringReversePolarity | INV069_StringReversePolarity | INV069 | Inverter | String Reverse Polarity | Yes
ALM_INV069_TransientACOvervoltage | INV069_TransientACOvervoltage | INV069 | Inverter | Transient AC Overvoltage | Yes
ALM_INV069_WarningActive | INV069_WarningActive | INV069 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV070_ACOvervoltage | INV070_ACOvervoltage | INV070 | Inverter | AC Overvoltage | Yes
ALM_INV070_ACUndervoltage | INV070_ACUndervoltage | INV070 | Inverter | AC Undervoltage | Yes
ALM_INV070_AFCISelfCheckFailure | INV070_AFCISelfCheckFailure | INV070 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV070_AbnormalGrounding | INV070_AbnormalGrounding | INV070 | Inverter | Abnormal Grounding | Yes
ALM_INV070_AbnormalPVModuleConfiguration | INV070_AbnormalPVModuleConfiguration | INV070 | Inverter | Abnormal PV module configuration | Yes
ALM_INV070_AbnormalResidualCurrent | INV070_AbnormalResidualCurrent | INV070 | Inverter | Abnormal Residual Current | Yes
ALM_INV070_AbnormalStringPower | INV070_AbnormalStringPower | INV070 | Inverter | Abnormal String Power | Yes
ALM_INV070_ActiveIslanding | INV070_ActiveIslanding | INV070 | Inverter | Active Islanding | Yes
ALM_INV070_BuiltPIDOperationAbnormal | INV070_BuiltPIDOperationAbnormal | INV070 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV070_CabinetOvertemperature | INV070_CabinetOvertemperature | INV070 | Inverter | Cabinet Overtemperature | Yes
ALM_INV070_CommunicationFailure | INV070_CommunicationFailure | INV070 | Inverter | Communication Failure | Yes
ALM_INV070_CommunicationStatus | INV070_CommunicationStatus | INV070 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV070_DCArcFault | INV070_DCArcFault | INV070 | Inverter | DC Arc Fault | Yes
ALM_INV070_DCInsulationFault | INV070_DCInsulationFault | INV070 | Inverter | DC Insulation Fault | Yes
ALM_INV070_DCOvervoltage | INV070_DCOvervoltage | INV070 | Inverter | DC Overvoltage | Yes
ALM_INV070_DeviceFault | INV070_DeviceFault | INV070 | Inverter | Device Fault | Yes
ALM_INV070_ExternalFanAbnormal | INV070_ExternalFanAbnormal | INV070 | Inverter | External fan abnormal | Yes
ALM_INV070_FanFailure | INV070_FanFailure | INV070 | Inverter | Fan Failure | Yes
ALM_INV070_Faulty | INV070_Faulty | INV070 | Inverter | Faulty | Yes
ALM_INV070_FaultyMonitoringUnit | INV070_FaultyMonitoringUnit | INV070 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV070_FaultyPowerCollector | INV070_FaultyPowerCollector | INV070 | Inverter | Faulty Power Collector | Yes
ALM_INV070_GeneralFaultTrip | INV070_GeneralFaultTrip | INV070 | Inverter | General Fault Trip | Yes
ALM_INV070_GridConnectionDeratingInverterInternalCauses | INV070_GridConnectionDeratingInverterInternalCauses | INV070 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV070_GridConnectionDeratingPowerRationing | INV070_GridConnectionDeratingPowerRationing | INV070 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV070_GridLoss | INV070_GridLoss | INV070 | Inverter | Grid Loss | Yes
ALM_INV070_GridOverfrequency | INV070_GridOverfrequency | INV070 | Inverter | Grid Overfrequency | Yes
ALM_INV070_GridOvervoltage | INV070_GridOvervoltage | INV070 | Inverter | Grid Overvoltage | Yes
ALM_INV070_GridTiedOffGridControllerAbnormal | INV070_GridTiedOffGridControllerAbnormal | INV070 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV070_GridUnderfrequency | INV070_GridUnderfrequency | INV070 | Inverter | Grid Underfrequency | Yes
ALM_INV070_GridUndervoltage | INV070_GridUndervoltage | INV070 | Inverter | Grid Undervoltage | Yes
ALM_INV070_GroundFault | INV070_GroundFault | INV070 | Inverter | Ground Fault | Yes
ALM_INV070_HighInputStringVoltageGround | INV070_HighInputStringVoltageGround | INV070 | Inverter | High input string voltage to ground | Yes
ALM_INV070_HighStringInputVoltage | INV070_HighStringInputVoltage | INV070 | Inverter | High string input voltage | Yes
ALM_INV070_InverterTripHistoryAvailable | INV070_InverterTripHistoryAvailable | INV070 | Inverter | Inverter Trip History Available | Yes
ALM_INV070_IslandingDetectionStatus | INV070_IslandingDetectionStatus | INV070 | Inverter | Islanding Detection Status | Yes
ALM_INV070_LicenseExpired | INV070_LicenseExpired | INV070 | Inverter | License Expired | Yes
ALM_INV070_LockingStatus | INV070_LockingStatus | INV070 | Inverter | Locking status | Yes
ALM_INV070_LowInsulationResistance | INV070_LowInsulationResistance | INV070 | Inverter | Low Insulation Resistance | Yes
ALM_INV070_OffGridOutputOverload | INV070_OffGridOutputOverload | INV070 | Inverter | Off-grid output overload | Yes
ALM_INV070_OptimizerFault | INV070_OptimizerFault | INV070 | Inverter | Optimizer fault | Yes
ALM_INV070_OutputDCComponentOverhigh | INV070_OutputDCComponentOverhigh | INV070 | Inverter | Output DC Component Overhigh | Yes
ALM_INV070_OutputOvercurrent | INV070_OutputOvercurrent | INV070 | Inverter | Output Overcurrent | Yes
ALM_INV070_PVStringLoss | INV070_PVStringLoss | INV070 | Inverter | PV String Loss | Yes
ALM_INV070_PassiveIslanding | INV070_PassiveIslanding | INV070 | Inverter | Passive Islanding | Yes
ALM_INV070_PeripheralPortShortCircuit | INV070_PeripheralPortShortCircuit | INV070 | Inverter | Peripheral port short circuit | Yes
ALM_INV070_PhaseWireShortCircuitedPE | INV070_PhaseWireShortCircuitedPE | INV070 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV070_PowerLimitationActiveGridCommand | INV070_PowerLimitationActiveGridCommand | INV070 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV070_StringReverseConnection | INV070_StringReverseConnection | INV070 | Inverter | String Reverse Connection | Yes
ALM_INV070_StringReversePolarity | INV070_StringReversePolarity | INV070 | Inverter | String Reverse Polarity | Yes
ALM_INV070_TransientACOvervoltage | INV070_TransientACOvervoltage | INV070 | Inverter | Transient AC Overvoltage | Yes
ALM_INV070_WarningActive | INV070_WarningActive | INV070 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV071_ACOvervoltage | INV071_ACOvervoltage | INV071 | Inverter | AC Overvoltage | Yes
ALM_INV071_ACUndervoltage | INV071_ACUndervoltage | INV071 | Inverter | AC Undervoltage | Yes
ALM_INV071_AFCISelfCheckFailure | INV071_AFCISelfCheckFailure | INV071 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV071_AbnormalGrounding | INV071_AbnormalGrounding | INV071 | Inverter | Abnormal Grounding | Yes
ALM_INV071_AbnormalPVModuleConfiguration | INV071_AbnormalPVModuleConfiguration | INV071 | Inverter | Abnormal PV module configuration | Yes
ALM_INV071_AbnormalResidualCurrent | INV071_AbnormalResidualCurrent | INV071 | Inverter | Abnormal Residual Current | Yes
ALM_INV071_AbnormalStringPower | INV071_AbnormalStringPower | INV071 | Inverter | Abnormal String Power | Yes
ALM_INV071_ActiveIslanding | INV071_ActiveIslanding | INV071 | Inverter | Active Islanding | Yes
ALM_INV071_BuiltPIDOperationAbnormal | INV071_BuiltPIDOperationAbnormal | INV071 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV071_CabinetOvertemperature | INV071_CabinetOvertemperature | INV071 | Inverter | Cabinet Overtemperature | Yes
ALM_INV071_CommunicationFailure | INV071_CommunicationFailure | INV071 | Inverter | Communication Failure | Yes
ALM_INV071_CommunicationStatus | INV071_CommunicationStatus | INV071 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV071_DCArcFault | INV071_DCArcFault | INV071 | Inverter | DC Arc Fault | Yes
ALM_INV071_DCInsulationFault | INV071_DCInsulationFault | INV071 | Inverter | DC Insulation Fault | Yes
ALM_INV071_DCOvervoltage | INV071_DCOvervoltage | INV071 | Inverter | DC Overvoltage | Yes
ALM_INV071_DeviceFault | INV071_DeviceFault | INV071 | Inverter | Device Fault | Yes
ALM_INV071_ExternalFanAbnormal | INV071_ExternalFanAbnormal | INV071 | Inverter | External fan abnormal | Yes
ALM_INV071_FanFailure | INV071_FanFailure | INV071 | Inverter | Fan Failure | Yes
ALM_INV071_Faulty | INV071_Faulty | INV071 | Inverter | Faulty | Yes
ALM_INV071_FaultyMonitoringUnit | INV071_FaultyMonitoringUnit | INV071 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV071_FaultyPowerCollector | INV071_FaultyPowerCollector | INV071 | Inverter | Faulty Power Collector | Yes
ALM_INV071_GeneralFaultTrip | INV071_GeneralFaultTrip | INV071 | Inverter | General Fault Trip | Yes
ALM_INV071_GridConnectionDeratingInverterInternalCauses | INV071_GridConnectionDeratingInverterInternalCauses | INV071 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV071_GridConnectionDeratingPowerRationing | INV071_GridConnectionDeratingPowerRationing | INV071 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV071_GridLoss | INV071_GridLoss | INV071 | Inverter | Grid Loss | Yes
ALM_INV071_GridOverfrequency | INV071_GridOverfrequency | INV071 | Inverter | Grid Overfrequency | Yes
ALM_INV071_GridOvervoltage | INV071_GridOvervoltage | INV071 | Inverter | Grid Overvoltage | Yes
ALM_INV071_GridTiedOffGridControllerAbnormal | INV071_GridTiedOffGridControllerAbnormal | INV071 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV071_GridUnderfrequency | INV071_GridUnderfrequency | INV071 | Inverter | Grid Underfrequency | Yes
ALM_INV071_GridUndervoltage | INV071_GridUndervoltage | INV071 | Inverter | Grid Undervoltage | Yes
ALM_INV071_GroundFault | INV071_GroundFault | INV071 | Inverter | Ground Fault | Yes
ALM_INV071_HighInputStringVoltageGround | INV071_HighInputStringVoltageGround | INV071 | Inverter | High input string voltage to ground | Yes
ALM_INV071_HighStringInputVoltage | INV071_HighStringInputVoltage | INV071 | Inverter | High string input voltage | Yes
ALM_INV071_InverterTripHistoryAvailable | INV071_InverterTripHistoryAvailable | INV071 | Inverter | Inverter Trip History Available | Yes
ALM_INV071_IslandingDetectionStatus | INV071_IslandingDetectionStatus | INV071 | Inverter | Islanding Detection Status | Yes
ALM_INV071_LicenseExpired | INV071_LicenseExpired | INV071 | Inverter | License Expired | Yes
ALM_INV071_LockingStatus | INV071_LockingStatus | INV071 | Inverter | Locking status | Yes
ALM_INV071_LowInsulationResistance | INV071_LowInsulationResistance | INV071 | Inverter | Low Insulation Resistance | Yes
ALM_INV071_OffGridOutputOverload | INV071_OffGridOutputOverload | INV071 | Inverter | Off-grid output overload | Yes
ALM_INV071_OptimizerFault | INV071_OptimizerFault | INV071 | Inverter | Optimizer fault | Yes
ALM_INV071_OutputDCComponentOverhigh | INV071_OutputDCComponentOverhigh | INV071 | Inverter | Output DC Component Overhigh | Yes
ALM_INV071_OutputOvercurrent | INV071_OutputOvercurrent | INV071 | Inverter | Output Overcurrent | Yes
ALM_INV071_PVStringLoss | INV071_PVStringLoss | INV071 | Inverter | PV String Loss | Yes
ALM_INV071_PassiveIslanding | INV071_PassiveIslanding | INV071 | Inverter | Passive Islanding | Yes
ALM_INV071_PeripheralPortShortCircuit | INV071_PeripheralPortShortCircuit | INV071 | Inverter | Peripheral port short circuit | Yes
ALM_INV071_PhaseWireShortCircuitedPE | INV071_PhaseWireShortCircuitedPE | INV071 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV071_PowerLimitationActiveGridCommand | INV071_PowerLimitationActiveGridCommand | INV071 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV071_StringReverseConnection | INV071_StringReverseConnection | INV071 | Inverter | String Reverse Connection | Yes
ALM_INV071_StringReversePolarity | INV071_StringReversePolarity | INV071 | Inverter | String Reverse Polarity | Yes
ALM_INV071_TransientACOvervoltage | INV071_TransientACOvervoltage | INV071 | Inverter | Transient AC Overvoltage | Yes
ALM_INV071_WarningActive | INV071_WarningActive | INV071 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV072_ACOvervoltage | INV072_ACOvervoltage | INV072 | Inverter | AC Overvoltage | Yes
ALM_INV072_ACUndervoltage | INV072_ACUndervoltage | INV072 | Inverter | AC Undervoltage | Yes
ALM_INV072_AFCISelfCheckFailure | INV072_AFCISelfCheckFailure | INV072 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV072_AbnormalGrounding | INV072_AbnormalGrounding | INV072 | Inverter | Abnormal Grounding | Yes
ALM_INV072_AbnormalPVModuleConfiguration | INV072_AbnormalPVModuleConfiguration | INV072 | Inverter | Abnormal PV module configuration | Yes
ALM_INV072_AbnormalResidualCurrent | INV072_AbnormalResidualCurrent | INV072 | Inverter | Abnormal Residual Current | Yes
ALM_INV072_AbnormalStringPower | INV072_AbnormalStringPower | INV072 | Inverter | Abnormal String Power | Yes
ALM_INV072_ActiveIslanding | INV072_ActiveIslanding | INV072 | Inverter | Active Islanding | Yes
ALM_INV072_BuiltPIDOperationAbnormal | INV072_BuiltPIDOperationAbnormal | INV072 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV072_CabinetOvertemperature | INV072_CabinetOvertemperature | INV072 | Inverter | Cabinet Overtemperature | Yes
ALM_INV072_CommunicationFailure | INV072_CommunicationFailure | INV072 | Inverter | Communication Failure | Yes
ALM_INV072_CommunicationStatus | INV072_CommunicationStatus | INV072 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV072_DCArcFault | INV072_DCArcFault | INV072 | Inverter | DC Arc Fault | Yes
ALM_INV072_DCInsulationFault | INV072_DCInsulationFault | INV072 | Inverter | DC Insulation Fault | Yes
ALM_INV072_DCOvervoltage | INV072_DCOvervoltage | INV072 | Inverter | DC Overvoltage | Yes
ALM_INV072_DeviceFault | INV072_DeviceFault | INV072 | Inverter | Device Fault | Yes
ALM_INV072_ExternalFanAbnormal | INV072_ExternalFanAbnormal | INV072 | Inverter | External fan abnormal | Yes
ALM_INV072_FanFailure | INV072_FanFailure | INV072 | Inverter | Fan Failure | Yes
ALM_INV072_Faulty | INV072_Faulty | INV072 | Inverter | Faulty | Yes
ALM_INV072_FaultyMonitoringUnit | INV072_FaultyMonitoringUnit | INV072 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV072_FaultyPowerCollector | INV072_FaultyPowerCollector | INV072 | Inverter | Faulty Power Collector | Yes
ALM_INV072_GeneralFaultTrip | INV072_GeneralFaultTrip | INV072 | Inverter | General Fault Trip | Yes
ALM_INV072_GridConnectionDeratingInverterInternalCauses | INV072_GridConnectionDeratingInverterInternalCauses | INV072 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV072_GridConnectionDeratingPowerRationing | INV072_GridConnectionDeratingPowerRationing | INV072 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV072_GridLoss | INV072_GridLoss | INV072 | Inverter | Grid Loss | Yes
ALM_INV072_GridOverfrequency | INV072_GridOverfrequency | INV072 | Inverter | Grid Overfrequency | Yes
ALM_INV072_GridOvervoltage | INV072_GridOvervoltage | INV072 | Inverter | Grid Overvoltage | Yes
ALM_INV072_GridTiedOffGridControllerAbnormal | INV072_GridTiedOffGridControllerAbnormal | INV072 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV072_GridUnderfrequency | INV072_GridUnderfrequency | INV072 | Inverter | Grid Underfrequency | Yes
ALM_INV072_GridUndervoltage | INV072_GridUndervoltage | INV072 | Inverter | Grid Undervoltage | Yes
ALM_INV072_GroundFault | INV072_GroundFault | INV072 | Inverter | Ground Fault | Yes
ALM_INV072_HighInputStringVoltageGround | INV072_HighInputStringVoltageGround | INV072 | Inverter | High input string voltage to ground | Yes
ALM_INV072_HighStringInputVoltage | INV072_HighStringInputVoltage | INV072 | Inverter | High string input voltage | Yes
ALM_INV072_InverterTripHistoryAvailable | INV072_InverterTripHistoryAvailable | INV072 | Inverter | Inverter Trip History Available | Yes
ALM_INV072_IslandingDetectionStatus | INV072_IslandingDetectionStatus | INV072 | Inverter | Islanding Detection Status | Yes
ALM_INV072_LicenseExpired | INV072_LicenseExpired | INV072 | Inverter | License Expired | Yes
ALM_INV072_LockingStatus | INV072_LockingStatus | INV072 | Inverter | Locking status | Yes
ALM_INV072_LowInsulationResistance | INV072_LowInsulationResistance | INV072 | Inverter | Low Insulation Resistance | Yes
ALM_INV072_OffGridOutputOverload | INV072_OffGridOutputOverload | INV072 | Inverter | Off-grid output overload | Yes
ALM_INV072_OptimizerFault | INV072_OptimizerFault | INV072 | Inverter | Optimizer fault | Yes
ALM_INV072_OutputDCComponentOverhigh | INV072_OutputDCComponentOverhigh | INV072 | Inverter | Output DC Component Overhigh | Yes
ALM_INV072_OutputOvercurrent | INV072_OutputOvercurrent | INV072 | Inverter | Output Overcurrent | Yes
ALM_INV072_PVStringLoss | INV072_PVStringLoss | INV072 | Inverter | PV String Loss | Yes
ALM_INV072_PassiveIslanding | INV072_PassiveIslanding | INV072 | Inverter | Passive Islanding | Yes
ALM_INV072_PeripheralPortShortCircuit | INV072_PeripheralPortShortCircuit | INV072 | Inverter | Peripheral port short circuit | Yes
ALM_INV072_PhaseWireShortCircuitedPE | INV072_PhaseWireShortCircuitedPE | INV072 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV072_PowerLimitationActiveGridCommand | INV072_PowerLimitationActiveGridCommand | INV072 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV072_StringReverseConnection | INV072_StringReverseConnection | INV072 | Inverter | String Reverse Connection | Yes
ALM_INV072_StringReversePolarity | INV072_StringReversePolarity | INV072 | Inverter | String Reverse Polarity | Yes
ALM_INV072_TransientACOvervoltage | INV072_TransientACOvervoltage | INV072 | Inverter | Transient AC Overvoltage | Yes
ALM_INV072_WarningActive | INV072_WarningActive | INV072 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV073_ACOvervoltage | INV073_ACOvervoltage | INV073 | Inverter | AC Overvoltage | Yes
ALM_INV073_ACUndervoltage | INV073_ACUndervoltage | INV073 | Inverter | AC Undervoltage | Yes
ALM_INV073_AFCISelfCheckFailure | INV073_AFCISelfCheckFailure | INV073 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV073_AbnormalGrounding | INV073_AbnormalGrounding | INV073 | Inverter | Abnormal Grounding | Yes
ALM_INV073_AbnormalPVModuleConfiguration | INV073_AbnormalPVModuleConfiguration | INV073 | Inverter | Abnormal PV module configuration | Yes
ALM_INV073_AbnormalResidualCurrent | INV073_AbnormalResidualCurrent | INV073 | Inverter | Abnormal Residual Current | Yes
ALM_INV073_AbnormalStringPower | INV073_AbnormalStringPower | INV073 | Inverter | Abnormal String Power | Yes
ALM_INV073_ActiveIslanding | INV073_ActiveIslanding | INV073 | Inverter | Active Islanding | Yes
ALM_INV073_BuiltPIDOperationAbnormal | INV073_BuiltPIDOperationAbnormal | INV073 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV073_CabinetOvertemperature | INV073_CabinetOvertemperature | INV073 | Inverter | Cabinet Overtemperature | Yes
ALM_INV073_CommunicationFailure | INV073_CommunicationFailure | INV073 | Inverter | Communication Failure | Yes
ALM_INV073_CommunicationStatus | INV073_CommunicationStatus | INV073 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV073_DCArcFault | INV073_DCArcFault | INV073 | Inverter | DC Arc Fault | Yes
ALM_INV073_DCInsulationFault | INV073_DCInsulationFault | INV073 | Inverter | DC Insulation Fault | Yes
ALM_INV073_DCOvervoltage | INV073_DCOvervoltage | INV073 | Inverter | DC Overvoltage | Yes
ALM_INV073_DeviceFault | INV073_DeviceFault | INV073 | Inverter | Device Fault | Yes
ALM_INV073_ExternalFanAbnormal | INV073_ExternalFanAbnormal | INV073 | Inverter | External fan abnormal | Yes
ALM_INV073_FanFailure | INV073_FanFailure | INV073 | Inverter | Fan Failure | Yes
ALM_INV073_Faulty | INV073_Faulty | INV073 | Inverter | Faulty | Yes
ALM_INV073_FaultyMonitoringUnit | INV073_FaultyMonitoringUnit | INV073 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV073_FaultyPowerCollector | INV073_FaultyPowerCollector | INV073 | Inverter | Faulty Power Collector | Yes
ALM_INV073_GeneralFaultTrip | INV073_GeneralFaultTrip | INV073 | Inverter | General Fault Trip | Yes
ALM_INV073_GridConnectionDeratingInverterInternalCauses | INV073_GridConnectionDeratingInverterInternalCauses | INV073 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV073_GridConnectionDeratingPowerRationing | INV073_GridConnectionDeratingPowerRationing | INV073 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV073_GridLoss | INV073_GridLoss | INV073 | Inverter | Grid Loss | Yes
ALM_INV073_GridOverfrequency | INV073_GridOverfrequency | INV073 | Inverter | Grid Overfrequency | Yes
ALM_INV073_GridOvervoltage | INV073_GridOvervoltage | INV073 | Inverter | Grid Overvoltage | Yes
ALM_INV073_GridTiedOffGridControllerAbnormal | INV073_GridTiedOffGridControllerAbnormal | INV073 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV073_GridUnderfrequency | INV073_GridUnderfrequency | INV073 | Inverter | Grid Underfrequency | Yes
ALM_INV073_GridUndervoltage | INV073_GridUndervoltage | INV073 | Inverter | Grid Undervoltage | Yes
ALM_INV073_GroundFault | INV073_GroundFault | INV073 | Inverter | Ground Fault | Yes
ALM_INV073_HighInputStringVoltageGround | INV073_HighInputStringVoltageGround | INV073 | Inverter | High input string voltage to ground | Yes
ALM_INV073_HighStringInputVoltage | INV073_HighStringInputVoltage | INV073 | Inverter | High string input voltage | Yes
ALM_INV073_InverterTripHistoryAvailable | INV073_InverterTripHistoryAvailable | INV073 | Inverter | Inverter Trip History Available | Yes
ALM_INV073_IslandingDetectionStatus | INV073_IslandingDetectionStatus | INV073 | Inverter | Islanding Detection Status | Yes
ALM_INV073_LicenseExpired | INV073_LicenseExpired | INV073 | Inverter | License Expired | Yes
ALM_INV073_LockingStatus | INV073_LockingStatus | INV073 | Inverter | Locking status | Yes
ALM_INV073_LowInsulationResistance | INV073_LowInsulationResistance | INV073 | Inverter | Low Insulation Resistance | Yes
ALM_INV073_OffGridOutputOverload | INV073_OffGridOutputOverload | INV073 | Inverter | Off-grid output overload | Yes
ALM_INV073_OptimizerFault | INV073_OptimizerFault | INV073 | Inverter | Optimizer fault | Yes
ALM_INV073_OutputDCComponentOverhigh | INV073_OutputDCComponentOverhigh | INV073 | Inverter | Output DC Component Overhigh | Yes
ALM_INV073_OutputOvercurrent | INV073_OutputOvercurrent | INV073 | Inverter | Output Overcurrent | Yes
ALM_INV073_PVStringLoss | INV073_PVStringLoss | INV073 | Inverter | PV String Loss | Yes
ALM_INV073_PassiveIslanding | INV073_PassiveIslanding | INV073 | Inverter | Passive Islanding | Yes
ALM_INV073_PeripheralPortShortCircuit | INV073_PeripheralPortShortCircuit | INV073 | Inverter | Peripheral port short circuit | Yes
ALM_INV073_PhaseWireShortCircuitedPE | INV073_PhaseWireShortCircuitedPE | INV073 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV073_PowerLimitationActiveGridCommand | INV073_PowerLimitationActiveGridCommand | INV073 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV073_StringReverseConnection | INV073_StringReverseConnection | INV073 | Inverter | String Reverse Connection | Yes
ALM_INV073_StringReversePolarity | INV073_StringReversePolarity | INV073 | Inverter | String Reverse Polarity | Yes
ALM_INV073_TransientACOvervoltage | INV073_TransientACOvervoltage | INV073 | Inverter | Transient AC Overvoltage | Yes
ALM_INV073_WarningActive | INV073_WarningActive | INV073 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV074_ACOvervoltage | INV074_ACOvervoltage | INV074 | Inverter | AC Overvoltage | Yes
ALM_INV074_ACUndervoltage | INV074_ACUndervoltage | INV074 | Inverter | AC Undervoltage | Yes
ALM_INV074_AFCISelfCheckFailure | INV074_AFCISelfCheckFailure | INV074 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV074_AbnormalGrounding | INV074_AbnormalGrounding | INV074 | Inverter | Abnormal Grounding | Yes
ALM_INV074_AbnormalPVModuleConfiguration | INV074_AbnormalPVModuleConfiguration | INV074 | Inverter | Abnormal PV module configuration | Yes
ALM_INV074_AbnormalResidualCurrent | INV074_AbnormalResidualCurrent | INV074 | Inverter | Abnormal Residual Current | Yes
ALM_INV074_AbnormalStringPower | INV074_AbnormalStringPower | INV074 | Inverter | Abnormal String Power | Yes
ALM_INV074_ActiveIslanding | INV074_ActiveIslanding | INV074 | Inverter | Active Islanding | Yes
ALM_INV074_BuiltPIDOperationAbnormal | INV074_BuiltPIDOperationAbnormal | INV074 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV074_CabinetOvertemperature | INV074_CabinetOvertemperature | INV074 | Inverter | Cabinet Overtemperature | Yes
ALM_INV074_CommunicationFailure | INV074_CommunicationFailure | INV074 | Inverter | Communication Failure | Yes
ALM_INV074_CommunicationStatus | INV074_CommunicationStatus | INV074 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV074_DCArcFault | INV074_DCArcFault | INV074 | Inverter | DC Arc Fault | Yes
ALM_INV074_DCInsulationFault | INV074_DCInsulationFault | INV074 | Inverter | DC Insulation Fault | Yes
ALM_INV074_DCOvervoltage | INV074_DCOvervoltage | INV074 | Inverter | DC Overvoltage | Yes
ALM_INV074_DeviceFault | INV074_DeviceFault | INV074 | Inverter | Device Fault | Yes
ALM_INV074_ExternalFanAbnormal | INV074_ExternalFanAbnormal | INV074 | Inverter | External fan abnormal | Yes
ALM_INV074_FanFailure | INV074_FanFailure | INV074 | Inverter | Fan Failure | Yes
ALM_INV074_Faulty | INV074_Faulty | INV074 | Inverter | Faulty | Yes
ALM_INV074_FaultyMonitoringUnit | INV074_FaultyMonitoringUnit | INV074 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV074_FaultyPowerCollector | INV074_FaultyPowerCollector | INV074 | Inverter | Faulty Power Collector | Yes
ALM_INV074_GeneralFaultTrip | INV074_GeneralFaultTrip | INV074 | Inverter | General Fault Trip | Yes
ALM_INV074_GridConnectionDeratingInverterInternalCauses | INV074_GridConnectionDeratingInverterInternalCauses | INV074 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV074_GridConnectionDeratingPowerRationing | INV074_GridConnectionDeratingPowerRationing | INV074 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV074_GridLoss | INV074_GridLoss | INV074 | Inverter | Grid Loss | Yes
ALM_INV074_GridOverfrequency | INV074_GridOverfrequency | INV074 | Inverter | Grid Overfrequency | Yes
ALM_INV074_GridOvervoltage | INV074_GridOvervoltage | INV074 | Inverter | Grid Overvoltage | Yes
ALM_INV074_GridTiedOffGridControllerAbnormal | INV074_GridTiedOffGridControllerAbnormal | INV074 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV074_GridUnderfrequency | INV074_GridUnderfrequency | INV074 | Inverter | Grid Underfrequency | Yes
ALM_INV074_GridUndervoltage | INV074_GridUndervoltage | INV074 | Inverter | Grid Undervoltage | Yes
ALM_INV074_GroundFault | INV074_GroundFault | INV074 | Inverter | Ground Fault | Yes
ALM_INV074_HighInputStringVoltageGround | INV074_HighInputStringVoltageGround | INV074 | Inverter | High input string voltage to ground | Yes
ALM_INV074_HighStringInputVoltage | INV074_HighStringInputVoltage | INV074 | Inverter | High string input voltage | Yes
ALM_INV074_InverterTripHistoryAvailable | INV074_InverterTripHistoryAvailable | INV074 | Inverter | Inverter Trip History Available | Yes
ALM_INV074_IslandingDetectionStatus | INV074_IslandingDetectionStatus | INV074 | Inverter | Islanding Detection Status | Yes
ALM_INV074_LicenseExpired | INV074_LicenseExpired | INV074 | Inverter | License Expired | Yes
ALM_INV074_LockingStatus | INV074_LockingStatus | INV074 | Inverter | Locking status | Yes
ALM_INV074_LowInsulationResistance | INV074_LowInsulationResistance | INV074 | Inverter | Low Insulation Resistance | Yes
ALM_INV074_OffGridOutputOverload | INV074_OffGridOutputOverload | INV074 | Inverter | Off-grid output overload | Yes
ALM_INV074_OptimizerFault | INV074_OptimizerFault | INV074 | Inverter | Optimizer fault | Yes
ALM_INV074_OutputDCComponentOverhigh | INV074_OutputDCComponentOverhigh | INV074 | Inverter | Output DC Component Overhigh | Yes
ALM_INV074_OutputOvercurrent | INV074_OutputOvercurrent | INV074 | Inverter | Output Overcurrent | Yes
ALM_INV074_PVStringLoss | INV074_PVStringLoss | INV074 | Inverter | PV String Loss | Yes
ALM_INV074_PassiveIslanding | INV074_PassiveIslanding | INV074 | Inverter | Passive Islanding | Yes
ALM_INV074_PeripheralPortShortCircuit | INV074_PeripheralPortShortCircuit | INV074 | Inverter | Peripheral port short circuit | Yes
ALM_INV074_PhaseWireShortCircuitedPE | INV074_PhaseWireShortCircuitedPE | INV074 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV074_PowerLimitationActiveGridCommand | INV074_PowerLimitationActiveGridCommand | INV074 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV074_StringReverseConnection | INV074_StringReverseConnection | INV074 | Inverter | String Reverse Connection | Yes
ALM_INV074_StringReversePolarity | INV074_StringReversePolarity | INV074 | Inverter | String Reverse Polarity | Yes
ALM_INV074_TransientACOvervoltage | INV074_TransientACOvervoltage | INV074 | Inverter | Transient AC Overvoltage | Yes
ALM_INV074_WarningActive | INV074_WarningActive | INV074 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_INV075_ACOvervoltage | INV075_ACOvervoltage | INV075 | Inverter | AC Overvoltage | Yes
ALM_INV075_ACUndervoltage | INV075_ACUndervoltage | INV075 | Inverter | AC Undervoltage | Yes
ALM_INV075_AFCISelfCheckFailure | INV075_AFCISelfCheckFailure | INV075 | Inverter | AFCI Self-Check Failure | Yes
ALM_INV075_AbnormalGrounding | INV075_AbnormalGrounding | INV075 | Inverter | Abnormal Grounding | Yes
ALM_INV075_AbnormalPVModuleConfiguration | INV075_AbnormalPVModuleConfiguration | INV075 | Inverter | Abnormal PV module configuration | Yes
ALM_INV075_AbnormalResidualCurrent | INV075_AbnormalResidualCurrent | INV075 | Inverter | Abnormal Residual Current | Yes
ALM_INV075_AbnormalStringPower | INV075_AbnormalStringPower | INV075 | Inverter | Abnormal String Power | Yes
ALM_INV075_ActiveIslanding | INV075_ActiveIslanding | INV075 | Inverter | Active Islanding | Yes
ALM_INV075_BuiltPIDOperationAbnormal | INV075_BuiltPIDOperationAbnormal | INV075 | Inverter | Built-in PID operation abnormal | Yes
ALM_INV075_CabinetOvertemperature | INV075_CabinetOvertemperature | INV075 | Inverter | Cabinet Overtemperature | Yes
ALM_INV075_CommunicationFailure | INV075_CommunicationFailure | INV075 | Inverter | Communication Failure | Yes
ALM_INV075_CommunicationStatus | INV075_CommunicationStatus | INV075 | Inverter | Communication Status (Healthy / Lost) | Yes
ALM_INV075_DCArcFault | INV075_DCArcFault | INV075 | Inverter | DC Arc Fault | Yes
ALM_INV075_DCInsulationFault | INV075_DCInsulationFault | INV075 | Inverter | DC Insulation Fault | Yes
ALM_INV075_DCOvervoltage | INV075_DCOvervoltage | INV075 | Inverter | DC Overvoltage | Yes
ALM_INV075_DeviceFault | INV075_DeviceFault | INV075 | Inverter | Device Fault | Yes
ALM_INV075_ExternalFanAbnormal | INV075_ExternalFanAbnormal | INV075 | Inverter | External fan abnormal | Yes
ALM_INV075_FanFailure | INV075_FanFailure | INV075 | Inverter | Fan Failure | Yes
ALM_INV075_Faulty | INV075_Faulty | INV075 | Inverter | Faulty | Yes
ALM_INV075_FaultyMonitoringUnit | INV075_FaultyMonitoringUnit | INV075 | Inverter | Faulty Monitoring Unit | Yes
ALM_INV075_FaultyPowerCollector | INV075_FaultyPowerCollector | INV075 | Inverter | Faulty Power Collector | Yes
ALM_INV075_GeneralFaultTrip | INV075_GeneralFaultTrip | INV075 | Inverter | General Fault Trip | Yes
ALM_INV075_GridConnectionDeratingInverterInternalCauses | INV075_GridConnectionDeratingInverterInternalCauses | INV075 | Inverter | Grid connection with derating due to inverter internal causes | Yes
ALM_INV075_GridConnectionDeratingPowerRationing | INV075_GridConnectionDeratingPowerRationing | INV075 | Inverter | Grid connection with derating due to power rationing | Yes
ALM_INV075_GridLoss | INV075_GridLoss | INV075 | Inverter | Grid Loss | Yes
ALM_INV075_GridOverfrequency | INV075_GridOverfrequency | INV075 | Inverter | Grid Overfrequency | Yes
ALM_INV075_GridOvervoltage | INV075_GridOvervoltage | INV075 | Inverter | Grid Overvoltage | Yes
ALM_INV075_GridTiedOffGridControllerAbnormal | INV075_GridTiedOffGridControllerAbnormal | INV075 | Inverter | Grid-tied/Off-grid controller abnormal | Yes
ALM_INV075_GridUnderfrequency | INV075_GridUnderfrequency | INV075 | Inverter | Grid Underfrequency | Yes
ALM_INV075_GridUndervoltage | INV075_GridUndervoltage | INV075 | Inverter | Grid Undervoltage | Yes
ALM_INV075_GroundFault | INV075_GroundFault | INV075 | Inverter | Ground Fault | Yes
ALM_INV075_HighInputStringVoltageGround | INV075_HighInputStringVoltageGround | INV075 | Inverter | High input string voltage to ground | Yes
ALM_INV075_HighStringInputVoltage | INV075_HighStringInputVoltage | INV075 | Inverter | High string input voltage | Yes
ALM_INV075_InverterTripHistoryAvailable | INV075_InverterTripHistoryAvailable | INV075 | Inverter | Inverter Trip History Available | Yes
ALM_INV075_IslandingDetectionStatus | INV075_IslandingDetectionStatus | INV075 | Inverter | Islanding Detection Status | Yes
ALM_INV075_LicenseExpired | INV075_LicenseExpired | INV075 | Inverter | License Expired | Yes
ALM_INV075_LockingStatus | INV075_LockingStatus | INV075 | Inverter | Locking status | Yes
ALM_INV075_LowInsulationResistance | INV075_LowInsulationResistance | INV075 | Inverter | Low Insulation Resistance | Yes
ALM_INV075_OffGridOutputOverload | INV075_OffGridOutputOverload | INV075 | Inverter | Off-grid output overload | Yes
ALM_INV075_OptimizerFault | INV075_OptimizerFault | INV075 | Inverter | Optimizer fault | Yes
ALM_INV075_OutputDCComponentOverhigh | INV075_OutputDCComponentOverhigh | INV075 | Inverter | Output DC Component Overhigh | Yes
ALM_INV075_OutputOvercurrent | INV075_OutputOvercurrent | INV075 | Inverter | Output Overcurrent | Yes
ALM_INV075_PVStringLoss | INV075_PVStringLoss | INV075 | Inverter | PV String Loss | Yes
ALM_INV075_PassiveIslanding | INV075_PassiveIslanding | INV075 | Inverter | Passive Islanding | Yes
ALM_INV075_PeripheralPortShortCircuit | INV075_PeripheralPortShortCircuit | INV075 | Inverter | Peripheral port short circuit | Yes
ALM_INV075_PhaseWireShortCircuitedPE | INV075_PhaseWireShortCircuitedPE | INV075 | Inverter | Phase Wire Short-Circuited to PE | Yes
ALM_INV075_PowerLimitationActiveGridCommand | INV075_PowerLimitationActiveGridCommand | INV075 | Inverter | Power Limitation Active due to Grid Command | Yes
ALM_INV075_StringReverseConnection | INV075_StringReverseConnection | INV075 | Inverter | String Reverse Connection | Yes
ALM_INV075_StringReversePolarity | INV075_StringReversePolarity | INV075 | Inverter | String Reverse Polarity | Yes
ALM_INV075_TransientACOvervoltage | INV075_TransientACOvervoltage | INV075 | Inverter | Transient AC Overvoltage | Yes
ALM_INV075_WarningActive | INV075_WarningActive | INV075 | Inverter | Warning Active (Derating, Overtemperature) | Yes
ALM_PR001_CircuitBreakerFailureFailExternalTrip | PR001_CircuitBreakerFailureFailExternalTrip | PR001 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR001_CircuitBreakerFailureInternalReTrip | PR001_CircuitBreakerFailureInternalReTrip | PR001 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR001_CircuitBreakerFailureTimerRunning | PR001_CircuitBreakerFailureTimerRunning | PR001 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR001_CircuitBreakerTripMaster1 | PR001_CircuitBreakerTripMaster1 | PR001 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR001_ACTripFlag | PR001_ACTripFlag | PR001 | Protection Relay | AC Trip Flag | Yes
ALM_PR001_DCTripFlag | PR001_DCTripFlag | PR001 | Protection Relay | DC Trip Flag | Yes
ALM_PR001_MCBTripFlag | PR001_MCBTripFlag | PR001 | Protection Relay | MCB Trip Flag | Yes
ALM_PR001_RelayTripFlag | PR001_RelayTripFlag | PR001 | Protection Relay | Relay trip Flag | Yes
ALM_PR001_DirectionalEarthFault | PR001_DirectionalEarthFault | PR001 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR001_DirectionalOvercurrentHighStage | PR001_DirectionalOvercurrentHighStage | PR001 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR001_DirectionalOvercurrentLowStage | PR001_DirectionalOvercurrentLowStage | PR001 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR001_InstantaneousOvercurrent | PR001_InstantaneousOvercurrent | PR001 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR001_NegativeSequenceOvercurrentProtection | PR001_NegativeSequenceOvercurrentProtection | PR001 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR001_ProtectionRelayStatus | PR001_ProtectionRelayStatus | PR001 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR001_SpringChargedDischargedAlarm | PR001_SpringChargedDischargedAlarm | PR001 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR001_TimeOvercurrent | PR001_TimeOvercurrent | PR001 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR002_CircuitBreakerFailureFailExternalTrip | PR002_CircuitBreakerFailureFailExternalTrip | PR002 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR002_CircuitBreakerFailureInternalReTrip | PR002_CircuitBreakerFailureInternalReTrip | PR002 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR002_CircuitBreakerFailureTimerRunning | PR002_CircuitBreakerFailureTimerRunning | PR002 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR002_CircuitBreakerTripMaster1 | PR002_CircuitBreakerTripMaster1 | PR002 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR002_ACTripFlag | PR002_ACTripFlag | PR002 | Protection Relay | AC Trip Flag | Yes
ALM_PR002_DCTripFlag | PR002_DCTripFlag | PR002 | Protection Relay | DC Trip Flag | Yes
ALM_PR002_MCBTripFlag | PR002_MCBTripFlag | PR002 | Protection Relay | MCB Trip Flag | Yes
ALM_PR002_RelayTripFlag | PR002_RelayTripFlag | PR002 | Protection Relay | Relay trip Flag | Yes
ALM_PR002_DirectionalEarthFault | PR002_DirectionalEarthFault | PR002 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR002_DirectionalOvercurrentHighStage | PR002_DirectionalOvercurrentHighStage | PR002 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR002_DirectionalOvercurrentLowStage | PR002_DirectionalOvercurrentLowStage | PR002 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR002_InstantaneousOvercurrent | PR002_InstantaneousOvercurrent | PR002 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR002_NegativeSequenceOvercurrentProtection | PR002_NegativeSequenceOvercurrentProtection | PR002 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR002_ProtectionRelayStatus | PR002_ProtectionRelayStatus | PR002 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR002_SpringChargedDischargedAlarm | PR002_SpringChargedDischargedAlarm | PR002 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR002_TimeOvercurrent | PR002_TimeOvercurrent | PR002 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR003_CircuitBreakerFailureFailExternalTrip | PR003_CircuitBreakerFailureFailExternalTrip | PR003 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR003_CircuitBreakerFailureInternalReTrip | PR003_CircuitBreakerFailureInternalReTrip | PR003 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR003_CircuitBreakerFailureTimerRunning | PR003_CircuitBreakerFailureTimerRunning | PR003 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR003_CircuitBreakerTripMaster1 | PR003_CircuitBreakerTripMaster1 | PR003 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR003_ACTripFlag | PR003_ACTripFlag | PR003 | Protection Relay | AC Trip Flag | Yes
ALM_PR003_DCTripFlag | PR003_DCTripFlag | PR003 | Protection Relay | DC Trip Flag | Yes
ALM_PR003_MCBTripFlag | PR003_MCBTripFlag | PR003 | Protection Relay | MCB Trip Flag | Yes
ALM_PR003_RelayTripFlag | PR003_RelayTripFlag | PR003 | Protection Relay | Relay trip Flag | Yes
ALM_PR003_DirectionalEarthFault | PR003_DirectionalEarthFault | PR003 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR003_DirectionalOvercurrentHighStage | PR003_DirectionalOvercurrentHighStage | PR003 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR003_DirectionalOvercurrentLowStage | PR003_DirectionalOvercurrentLowStage | PR003 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR003_InstantaneousOvercurrent | PR003_InstantaneousOvercurrent | PR003 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR003_NegativeSequenceOvercurrentProtection | PR003_NegativeSequenceOvercurrentProtection | PR003 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR003_ProtectionRelayStatus | PR003_ProtectionRelayStatus | PR003 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR003_SpringChargedDischargedAlarm | PR003_SpringChargedDischargedAlarm | PR003 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR003_TimeOvercurrent | PR003_TimeOvercurrent | PR003 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR004_CircuitBreakerFailureFailExternalTrip | PR004_CircuitBreakerFailureFailExternalTrip | PR004 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR004_CircuitBreakerFailureInternalReTrip | PR004_CircuitBreakerFailureInternalReTrip | PR004 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR004_CircuitBreakerFailureTimerRunning | PR004_CircuitBreakerFailureTimerRunning | PR004 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR004_CircuitBreakerTripMaster1 | PR004_CircuitBreakerTripMaster1 | PR004 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR004_ACTripFlag | PR004_ACTripFlag | PR004 | Protection Relay | AC Trip Flag | Yes
ALM_PR004_DCTripFlag | PR004_DCTripFlag | PR004 | Protection Relay | DC Trip Flag | Yes
ALM_PR004_MCBTripFlag | PR004_MCBTripFlag | PR004 | Protection Relay | MCB Trip Flag | Yes
ALM_PR004_RelayTripFlag | PR004_RelayTripFlag | PR004 | Protection Relay | Relay trip Flag | Yes
ALM_PR004_DirectionalEarthFault | PR004_DirectionalEarthFault | PR004 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR004_DirectionalOvercurrentHighStage | PR004_DirectionalOvercurrentHighStage | PR004 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR004_DirectionalOvercurrentLowStage | PR004_DirectionalOvercurrentLowStage | PR004 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR004_InstantaneousOvercurrent | PR004_InstantaneousOvercurrent | PR004 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR004_NegativeSequenceOvercurrentProtection | PR004_NegativeSequenceOvercurrentProtection | PR004 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR004_ProtectionRelayStatus | PR004_ProtectionRelayStatus | PR004 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR004_SpringChargedDischargedAlarm | PR004_SpringChargedDischargedAlarm | PR004 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR004_TimeOvercurrent | PR004_TimeOvercurrent | PR004 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR005_CircuitBreakerFailureFailExternalTrip | PR005_CircuitBreakerFailureFailExternalTrip | PR005 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR005_CircuitBreakerFailureInternalReTrip | PR005_CircuitBreakerFailureInternalReTrip | PR005 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR005_CircuitBreakerFailureTimerRunning | PR005_CircuitBreakerFailureTimerRunning | PR005 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR005_CircuitBreakerTripMaster1 | PR005_CircuitBreakerTripMaster1 | PR005 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR005_ACTripFlag | PR005_ACTripFlag | PR005 | Protection Relay | AC Trip Flag | Yes
ALM_PR005_DCTripFlag | PR005_DCTripFlag | PR005 | Protection Relay | DC Trip Flag | Yes
ALM_PR005_MCBTripFlag | PR005_MCBTripFlag | PR005 | Protection Relay | MCB Trip Flag | Yes
ALM_PR005_RelayTripFlag | PR005_RelayTripFlag | PR005 | Protection Relay | Relay trip Flag | Yes
ALM_PR005_DirectionalEarthFault | PR005_DirectionalEarthFault | PR005 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR005_DirectionalOvercurrentHighStage | PR005_DirectionalOvercurrentHighStage | PR005 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR005_DirectionalOvercurrentLowStage | PR005_DirectionalOvercurrentLowStage | PR005 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR005_InstantaneousOvercurrent | PR005_InstantaneousOvercurrent | PR005 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR005_NegativeSequenceOvercurrentProtection | PR005_NegativeSequenceOvercurrentProtection | PR005 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR005_ProtectionRelayStatus | PR005_ProtectionRelayStatus | PR005 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR005_SpringChargedDischargedAlarm | PR005_SpringChargedDischargedAlarm | PR005 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR005_TimeOvercurrent | PR005_TimeOvercurrent | PR005 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR006_CircuitBreakerFailureFailExternalTrip | PR006_CircuitBreakerFailureFailExternalTrip | PR006 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR006_CircuitBreakerFailureInternalReTrip | PR006_CircuitBreakerFailureInternalReTrip | PR006 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR006_CircuitBreakerFailureTimerRunning | PR006_CircuitBreakerFailureTimerRunning | PR006 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR006_CircuitBreakerTripMaster1 | PR006_CircuitBreakerTripMaster1 | PR006 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR006_ACTripFlag | PR006_ACTripFlag | PR006 | Protection Relay | AC Trip Flag | Yes
ALM_PR006_DCTripFlag | PR006_DCTripFlag | PR006 | Protection Relay | DC Trip Flag | Yes
ALM_PR006_MCBTripFlag | PR006_MCBTripFlag | PR006 | Protection Relay | MCB Trip Flag | Yes
ALM_PR006_RelayTripFlag | PR006_RelayTripFlag | PR006 | Protection Relay | Relay trip Flag | Yes
ALM_PR006_DirectionalEarthFault | PR006_DirectionalEarthFault | PR006 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR006_DirectionalOvercurrentHighStage | PR006_DirectionalOvercurrentHighStage | PR006 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR006_DirectionalOvercurrentLowStage | PR006_DirectionalOvercurrentLowStage | PR006 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR006_InstantaneousOvercurrent | PR006_InstantaneousOvercurrent | PR006 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR006_NegativeSequenceOvercurrentProtection | PR006_NegativeSequenceOvercurrentProtection | PR006 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR006_ProtectionRelayStatus | PR006_ProtectionRelayStatus | PR006 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR006_SpringChargedDischargedAlarm | PR006_SpringChargedDischargedAlarm | PR006 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR006_TimeOvercurrent | PR006_TimeOvercurrent | PR006 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR007_CircuitBreakerFailureFailExternalTrip | PR007_CircuitBreakerFailureFailExternalTrip | PR007 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR007_CircuitBreakerFailureInternalReTrip | PR007_CircuitBreakerFailureInternalReTrip | PR007 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR007_CircuitBreakerFailureTimerRunning | PR007_CircuitBreakerFailureTimerRunning | PR007 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR007_CircuitBreakerTripMaster1 | PR007_CircuitBreakerTripMaster1 | PR007 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR007_ACTripFlag | PR007_ACTripFlag | PR007 | Protection Relay | AC Trip Flag | Yes
ALM_PR007_DCTripFlag | PR007_DCTripFlag | PR007 | Protection Relay | DC Trip Flag | Yes
ALM_PR007_MCBTripFlag | PR007_MCBTripFlag | PR007 | Protection Relay | MCB Trip Flag | Yes
ALM_PR007_RelayTripFlag | PR007_RelayTripFlag | PR007 | Protection Relay | Relay trip Flag | Yes
ALM_PR007_DirectionalEarthFault | PR007_DirectionalEarthFault | PR007 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR007_DirectionalOvercurrentHighStage | PR007_DirectionalOvercurrentHighStage | PR007 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR007_DirectionalOvercurrentLowStage | PR007_DirectionalOvercurrentLowStage | PR007 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR007_InstantaneousOvercurrent | PR007_InstantaneousOvercurrent | PR007 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR007_NegativeSequenceOvercurrentProtection | PR007_NegativeSequenceOvercurrentProtection | PR007 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR007_ProtectionRelayStatus | PR007_ProtectionRelayStatus | PR007 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR007_SpringChargedDischargedAlarm | PR007_SpringChargedDischargedAlarm | PR007 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR007_TimeOvercurrent | PR007_TimeOvercurrent | PR007 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR008_CircuitBreakerFailureFailExternalTrip | PR008_CircuitBreakerFailureFailExternalTrip | PR008 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR008_CircuitBreakerFailureInternalReTrip | PR008_CircuitBreakerFailureInternalReTrip | PR008 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR008_CircuitBreakerFailureTimerRunning | PR008_CircuitBreakerFailureTimerRunning | PR008 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR008_CircuitBreakerTripMaster1 | PR008_CircuitBreakerTripMaster1 | PR008 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR008_ACTripFlag | PR008_ACTripFlag | PR008 | Protection Relay | AC Trip Flag | Yes
ALM_PR008_DCTripFlag | PR008_DCTripFlag | PR008 | Protection Relay | DC Trip Flag | Yes
ALM_PR008_MCBTripFlag | PR008_MCBTripFlag | PR008 | Protection Relay | MCB Trip Flag | Yes
ALM_PR008_RelayTripFlag | PR008_RelayTripFlag | PR008 | Protection Relay | Relay trip Flag | Yes
ALM_PR008_DirectionalEarthFault | PR008_DirectionalEarthFault | PR008 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR008_DirectionalOvercurrentHighStage | PR008_DirectionalOvercurrentHighStage | PR008 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR008_DirectionalOvercurrentLowStage | PR008_DirectionalOvercurrentLowStage | PR008 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR008_InstantaneousOvercurrent | PR008_InstantaneousOvercurrent | PR008 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR008_NegativeSequenceOvercurrentProtection | PR008_NegativeSequenceOvercurrentProtection | PR008 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR008_ProtectionRelayStatus | PR008_ProtectionRelayStatus | PR008 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR008_SpringChargedDischargedAlarm | PR008_SpringChargedDischargedAlarm | PR008 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR008_TimeOvercurrent | PR008_TimeOvercurrent | PR008 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR009_CircuitBreakerFailureFailExternalTrip | PR009_CircuitBreakerFailureFailExternalTrip | PR009 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR009_CircuitBreakerFailureInternalReTrip | PR009_CircuitBreakerFailureInternalReTrip | PR009 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR009_CircuitBreakerFailureTimerRunning | PR009_CircuitBreakerFailureTimerRunning | PR009 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR009_CircuitBreakerTripMaster1 | PR009_CircuitBreakerTripMaster1 | PR009 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR009_ACTripFlag | PR009_ACTripFlag | PR009 | Protection Relay | AC Trip Flag | Yes
ALM_PR009_DCTripFlag | PR009_DCTripFlag | PR009 | Protection Relay | DC Trip Flag | Yes
ALM_PR009_MCBTripFlag | PR009_MCBTripFlag | PR009 | Protection Relay | MCB Trip Flag | Yes
ALM_PR009_RelayTripFlag | PR009_RelayTripFlag | PR009 | Protection Relay | Relay trip Flag | Yes
ALM_PR009_DirectionalEarthFault | PR009_DirectionalEarthFault | PR009 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR009_DirectionalOvercurrentHighStage | PR009_DirectionalOvercurrentHighStage | PR009 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR009_DirectionalOvercurrentLowStage | PR009_DirectionalOvercurrentLowStage | PR009 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR009_InstantaneousOvercurrent | PR009_InstantaneousOvercurrent | PR009 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR009_NegativeSequenceOvercurrentProtection | PR009_NegativeSequenceOvercurrentProtection | PR009 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR009_ProtectionRelayStatus | PR009_ProtectionRelayStatus | PR009 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR009_SpringChargedDischargedAlarm | PR009_SpringChargedDischargedAlarm | PR009 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR009_TimeOvercurrent | PR009_TimeOvercurrent | PR009 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR010_CircuitBreakerFailureFailExternalTrip | PR010_CircuitBreakerFailureFailExternalTrip | PR010 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR010_CircuitBreakerFailureInternalReTrip | PR010_CircuitBreakerFailureInternalReTrip | PR010 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR010_CircuitBreakerFailureTimerRunning | PR010_CircuitBreakerFailureTimerRunning | PR010 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR010_CircuitBreakerTripMaster1 | PR010_CircuitBreakerTripMaster1 | PR010 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR010_ACTripFlag | PR010_ACTripFlag | PR010 | Protection Relay | AC Trip Flag | Yes
ALM_PR010_DCTripFlag | PR010_DCTripFlag | PR010 | Protection Relay | DC Trip Flag | Yes
ALM_PR010_MCBTripFlag | PR010_MCBTripFlag | PR010 | Protection Relay | MCB Trip Flag | Yes
ALM_PR010_RelayTripFlag | PR010_RelayTripFlag | PR010 | Protection Relay | Relay trip Flag | Yes
ALM_PR010_DirectionalEarthFault | PR010_DirectionalEarthFault | PR010 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR010_DirectionalOvercurrentHighStage | PR010_DirectionalOvercurrentHighStage | PR010 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR010_DirectionalOvercurrentLowStage | PR010_DirectionalOvercurrentLowStage | PR010 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR010_InstantaneousOvercurrent | PR010_InstantaneousOvercurrent | PR010 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR010_NegativeSequenceOvercurrentProtection | PR010_NegativeSequenceOvercurrentProtection | PR010 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR010_ProtectionRelayStatus | PR010_ProtectionRelayStatus | PR010 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR010_SpringChargedDischargedAlarm | PR010_SpringChargedDischargedAlarm | PR010 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR010_TimeOvercurrent | PR010_TimeOvercurrent | PR010 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR011_CircuitBreakerFailureFailExternalTrip | PR011_CircuitBreakerFailureFailExternalTrip | PR011 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR011_CircuitBreakerFailureInternalReTrip | PR011_CircuitBreakerFailureInternalReTrip | PR011 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR011_CircuitBreakerFailureTimerRunning | PR011_CircuitBreakerFailureTimerRunning | PR011 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR011_CircuitBreakerTripMaster1 | PR011_CircuitBreakerTripMaster1 | PR011 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR011_ACTripFlag | PR011_ACTripFlag | PR011 | Protection Relay | AC Trip Flag | Yes
ALM_PR011_DCTripFlag | PR011_DCTripFlag | PR011 | Protection Relay | DC Trip Flag | Yes
ALM_PR011_MCBTripFlag | PR011_MCBTripFlag | PR011 | Protection Relay | MCB Trip Flag | Yes
ALM_PR011_RelayTripFlag | PR011_RelayTripFlag | PR011 | Protection Relay | Relay trip Flag | Yes
ALM_PR011_DirectionalEarthFault | PR011_DirectionalEarthFault | PR011 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR011_DirectionalOvercurrentHighStage | PR011_DirectionalOvercurrentHighStage | PR011 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR011_DirectionalOvercurrentLowStage | PR011_DirectionalOvercurrentLowStage | PR011 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR011_InstantaneousOvercurrent | PR011_InstantaneousOvercurrent | PR011 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR011_NegativeSequenceOvercurrentProtection | PR011_NegativeSequenceOvercurrentProtection | PR011 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR011_ProtectionRelayStatus | PR011_ProtectionRelayStatus | PR011 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR011_SpringChargedDischargedAlarm | PR011_SpringChargedDischargedAlarm | PR011 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR011_TimeOvercurrent | PR011_TimeOvercurrent | PR011 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR012_CircuitBreakerFailureFailExternalTrip | PR012_CircuitBreakerFailureFailExternalTrip | PR012 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR012_CircuitBreakerFailureInternalReTrip | PR012_CircuitBreakerFailureInternalReTrip | PR012 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR012_CircuitBreakerFailureTimerRunning | PR012_CircuitBreakerFailureTimerRunning | PR012 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR012_CircuitBreakerTripMaster1 | PR012_CircuitBreakerTripMaster1 | PR012 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR012_ACTripFlag | PR012_ACTripFlag | PR012 | Protection Relay | AC Trip Flag | Yes
ALM_PR012_DCTripFlag | PR012_DCTripFlag | PR012 | Protection Relay | DC Trip Flag | Yes
ALM_PR012_MCBTripFlag | PR012_MCBTripFlag | PR012 | Protection Relay | MCB Trip Flag | Yes
ALM_PR012_RelayTripFlag | PR012_RelayTripFlag | PR012 | Protection Relay | Relay trip Flag | Yes
ALM_PR012_DirectionalEarthFault | PR012_DirectionalEarthFault | PR012 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR012_DirectionalOvercurrentHighStage | PR012_DirectionalOvercurrentHighStage | PR012 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR012_DirectionalOvercurrentLowStage | PR012_DirectionalOvercurrentLowStage | PR012 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR012_InstantaneousOvercurrent | PR012_InstantaneousOvercurrent | PR012 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR012_NegativeSequenceOvercurrentProtection | PR012_NegativeSequenceOvercurrentProtection | PR012 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR012_ProtectionRelayStatus | PR012_ProtectionRelayStatus | PR012 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR012_SpringChargedDischargedAlarm | PR012_SpringChargedDischargedAlarm | PR012 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR012_TimeOvercurrent | PR012_TimeOvercurrent | PR012 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR013_CircuitBreakerFailureFailExternalTrip | PR013_CircuitBreakerFailureFailExternalTrip | PR013 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR013_CircuitBreakerFailureInternalReTrip | PR013_CircuitBreakerFailureInternalReTrip | PR013 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR013_CircuitBreakerFailureTimerRunning | PR013_CircuitBreakerFailureTimerRunning | PR013 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR013_CircuitBreakerTripMaster1 | PR013_CircuitBreakerTripMaster1 | PR013 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR013_ACTripFlag | PR013_ACTripFlag | PR013 | Protection Relay | AC Trip Flag | Yes
ALM_PR013_DCTripFlag | PR013_DCTripFlag | PR013 | Protection Relay | DC Trip Flag | Yes
ALM_PR013_MCBTripFlag | PR013_MCBTripFlag | PR013 | Protection Relay | MCB Trip Flag | Yes
ALM_PR013_RelayTripFlag | PR013_RelayTripFlag | PR013 | Protection Relay | Relay trip Flag | Yes
ALM_PR013_DirectionalEarthFault | PR013_DirectionalEarthFault | PR013 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR013_DirectionalOvercurrentHighStage | PR013_DirectionalOvercurrentHighStage | PR013 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR013_DirectionalOvercurrentLowStage | PR013_DirectionalOvercurrentLowStage | PR013 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR013_InstantaneousOvercurrent | PR013_InstantaneousOvercurrent | PR013 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR013_NegativeSequenceOvercurrentProtection | PR013_NegativeSequenceOvercurrentProtection | PR013 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR013_ProtectionRelayStatus | PR013_ProtectionRelayStatus | PR013 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR013_SpringChargedDischargedAlarm | PR013_SpringChargedDischargedAlarm | PR013 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR013_TimeOvercurrent | PR013_TimeOvercurrent | PR013 | Protection Relay | - (51) Time Overcurrent | Yes
ALM_PR014_CircuitBreakerFailureFailExternalTrip | PR014_CircuitBreakerFailureFailExternalTrip | PR014 | Protection Relay | - (51BF) Circuit breaker failure Fail, external trip | Yes
ALM_PR014_CircuitBreakerFailureInternalReTrip | PR014_CircuitBreakerFailureInternalReTrip | PR014 | Protection Relay | - (51BF) Circuit breaker failure Internal re-trip | Yes
ALM_PR014_CircuitBreakerFailureTimerRunning | PR014_CircuitBreakerFailureTimerRunning | PR014 | Protection Relay | - (51BF) Circuit breaker failure Timer running | Yes
ALM_PR014_CircuitBreakerTripMaster1 | PR014_CircuitBreakerTripMaster1 | PR014 | Protection Relay | Circuit breaker tripMaster1 | Yes
ALM_PR014_ACTripFlag | PR014_ACTripFlag | PR014 | Protection Relay | AC Trip Flag | Yes
ALM_PR014_DCTripFlag | PR014_DCTripFlag | PR014 | Protection Relay | DC Trip Flag | Yes
ALM_PR014_MCBTripFlag | PR014_MCBTripFlag | PR014 | Protection Relay | MCB Trip Flag | Yes
ALM_PR014_RelayTripFlag | PR014_RelayTripFlag | PR014 | Protection Relay | Relay trip Flag | Yes
ALM_PR014_DirectionalEarthFault | PR014_DirectionalEarthFault | PR014 | Protection Relay | - (67N) Directional Earth Fault | Yes
ALM_PR014_DirectionalOvercurrentHighStage | PR014_DirectionalOvercurrentHighStage | PR014 | Protection Relay | - (67) Directional overcurrent high stage (1) | Yes
ALM_PR014_DirectionalOvercurrentLowStage | PR014_DirectionalOvercurrentLowStage | PR014 | Protection Relay | - (67) Directional overcurrent low stage (1) | Yes
ALM_PR014_InstantaneousOvercurrent | PR014_InstantaneousOvercurrent | PR014 | Protection Relay | - (50) instantaneous overcurrent | Yes
ALM_PR014_NegativeSequenceOvercurrentProtection | PR014_NegativeSequenceOvercurrentProtection | PR014 | Protection Relay | - (46) Negative-sequence overcurrent protection (1) | Yes
ALM_PR014_ProtectionRelayStatus | PR014_ProtectionRelayStatus | PR014 | Protection Relay | Protection Relay Status ( Alarm) | Yes
ALM_PR014_SpringChargedDischargedAlarm | PR014_SpringChargedDischargedAlarm | PR014 | Protection Relay | Spring charged/discharged Alarm | Yes
ALM_PR014_TimeOvercurrent | PR014_TimeOvercurrent | PR014 | Protection Relay | - (51) Time Overcurrent | Yes

## Event_List
Event List
Event Name | Source Tag | Device ID | Device Type | Signal Description
EVT_INV001_InverterGridConnectionStatus | INV001_InverterGridConnectionStatus | INV001 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV001_InverterStartupShutdownStatus | INV001_InverterStartupShutdownStatus | INV001 | Inverter | Inverter startup/shutdown status
EVT_INV001_PowerCurtailmentStatus | INV001_PowerCurtailmentStatus | INV001 | Inverter | Power Curtailment Status
EVT_INV001_RemoteOFFStatus | INV001_RemoteOFFStatus | INV001 | Inverter | Remote ON/OFF Status
EVT_INV002_InverterGridConnectionStatus | INV002_InverterGridConnectionStatus | INV002 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV002_InverterStartupShutdownStatus | INV002_InverterStartupShutdownStatus | INV002 | Inverter | Inverter startup/shutdown status
EVT_INV002_PowerCurtailmentStatus | INV002_PowerCurtailmentStatus | INV002 | Inverter | Power Curtailment Status
EVT_INV002_RemoteOFFStatus | INV002_RemoteOFFStatus | INV002 | Inverter | Remote ON/OFF Status
EVT_INV003_InverterGridConnectionStatus | INV003_InverterGridConnectionStatus | INV003 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV003_InverterStartupShutdownStatus | INV003_InverterStartupShutdownStatus | INV003 | Inverter | Inverter startup/shutdown status
EVT_INV003_PowerCurtailmentStatus | INV003_PowerCurtailmentStatus | INV003 | Inverter | Power Curtailment Status
EVT_INV003_RemoteOFFStatus | INV003_RemoteOFFStatus | INV003 | Inverter | Remote ON/OFF Status
EVT_INV004_InverterGridConnectionStatus | INV004_InverterGridConnectionStatus | INV004 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV004_InverterStartupShutdownStatus | INV004_InverterStartupShutdownStatus | INV004 | Inverter | Inverter startup/shutdown status
EVT_INV004_PowerCurtailmentStatus | INV004_PowerCurtailmentStatus | INV004 | Inverter | Power Curtailment Status
EVT_INV004_RemoteOFFStatus | INV004_RemoteOFFStatus | INV004 | Inverter | Remote ON/OFF Status
EVT_INV005_InverterGridConnectionStatus | INV005_InverterGridConnectionStatus | INV005 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV005_InverterStartupShutdownStatus | INV005_InverterStartupShutdownStatus | INV005 | Inverter | Inverter startup/shutdown status
EVT_INV005_PowerCurtailmentStatus | INV005_PowerCurtailmentStatus | INV005 | Inverter | Power Curtailment Status
EVT_INV005_RemoteOFFStatus | INV005_RemoteOFFStatus | INV005 | Inverter | Remote ON/OFF Status
EVT_INV006_InverterGridConnectionStatus | INV006_InverterGridConnectionStatus | INV006 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV006_InverterStartupShutdownStatus | INV006_InverterStartupShutdownStatus | INV006 | Inverter | Inverter startup/shutdown status
EVT_INV006_PowerCurtailmentStatus | INV006_PowerCurtailmentStatus | INV006 | Inverter | Power Curtailment Status
EVT_INV006_RemoteOFFStatus | INV006_RemoteOFFStatus | INV006 | Inverter | Remote ON/OFF Status
EVT_INV007_InverterGridConnectionStatus | INV007_InverterGridConnectionStatus | INV007 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV007_InverterStartupShutdownStatus | INV007_InverterStartupShutdownStatus | INV007 | Inverter | Inverter startup/shutdown status
EVT_INV007_PowerCurtailmentStatus | INV007_PowerCurtailmentStatus | INV007 | Inverter | Power Curtailment Status
EVT_INV007_RemoteOFFStatus | INV007_RemoteOFFStatus | INV007 | Inverter | Remote ON/OFF Status
EVT_INV008_InverterGridConnectionStatus | INV008_InverterGridConnectionStatus | INV008 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV008_InverterStartupShutdownStatus | INV008_InverterStartupShutdownStatus | INV008 | Inverter | Inverter startup/shutdown status
EVT_INV008_PowerCurtailmentStatus | INV008_PowerCurtailmentStatus | INV008 | Inverter | Power Curtailment Status
EVT_INV008_RemoteOFFStatus | INV008_RemoteOFFStatus | INV008 | Inverter | Remote ON/OFF Status
EVT_INV009_InverterGridConnectionStatus | INV009_InverterGridConnectionStatus | INV009 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV009_InverterStartupShutdownStatus | INV009_InverterStartupShutdownStatus | INV009 | Inverter | Inverter startup/shutdown status
EVT_INV009_PowerCurtailmentStatus | INV009_PowerCurtailmentStatus | INV009 | Inverter | Power Curtailment Status
EVT_INV009_RemoteOFFStatus | INV009_RemoteOFFStatus | INV009 | Inverter | Remote ON/OFF Status
EVT_INV010_InverterGridConnectionStatus | INV010_InverterGridConnectionStatus | INV010 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV010_InverterStartupShutdownStatus | INV010_InverterStartupShutdownStatus | INV010 | Inverter | Inverter startup/shutdown status
EVT_INV010_PowerCurtailmentStatus | INV010_PowerCurtailmentStatus | INV010 | Inverter | Power Curtailment Status
EVT_INV010_RemoteOFFStatus | INV010_RemoteOFFStatus | INV010 | Inverter | Remote ON/OFF Status
EVT_INV011_InverterGridConnectionStatus | INV011_InverterGridConnectionStatus | INV011 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV011_InverterStartupShutdownStatus | INV011_InverterStartupShutdownStatus | INV011 | Inverter | Inverter startup/shutdown status
EVT_INV011_PowerCurtailmentStatus | INV011_PowerCurtailmentStatus | INV011 | Inverter | Power Curtailment Status
EVT_INV011_RemoteOFFStatus | INV011_RemoteOFFStatus | INV011 | Inverter | Remote ON/OFF Status
EVT_INV012_InverterGridConnectionStatus | INV012_InverterGridConnectionStatus | INV012 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV012_InverterStartupShutdownStatus | INV012_InverterStartupShutdownStatus | INV012 | Inverter | Inverter startup/shutdown status
EVT_INV012_PowerCurtailmentStatus | INV012_PowerCurtailmentStatus | INV012 | Inverter | Power Curtailment Status
EVT_INV012_RemoteOFFStatus | INV012_RemoteOFFStatus | INV012 | Inverter | Remote ON/OFF Status
EVT_INV013_InverterGridConnectionStatus | INV013_InverterGridConnectionStatus | INV013 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV013_InverterStartupShutdownStatus | INV013_InverterStartupShutdownStatus | INV013 | Inverter | Inverter startup/shutdown status
EVT_INV013_PowerCurtailmentStatus | INV013_PowerCurtailmentStatus | INV013 | Inverter | Power Curtailment Status
EVT_INV013_RemoteOFFStatus | INV013_RemoteOFFStatus | INV013 | Inverter | Remote ON/OFF Status
EVT_INV014_InverterGridConnectionStatus | INV014_InverterGridConnectionStatus | INV014 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV014_InverterStartupShutdownStatus | INV014_InverterStartupShutdownStatus | INV014 | Inverter | Inverter startup/shutdown status
EVT_INV014_PowerCurtailmentStatus | INV014_PowerCurtailmentStatus | INV014 | Inverter | Power Curtailment Status
EVT_INV014_RemoteOFFStatus | INV014_RemoteOFFStatus | INV014 | Inverter | Remote ON/OFF Status
EVT_INV015_InverterGridConnectionStatus | INV015_InverterGridConnectionStatus | INV015 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV015_InverterStartupShutdownStatus | INV015_InverterStartupShutdownStatus | INV015 | Inverter | Inverter startup/shutdown status
EVT_INV015_PowerCurtailmentStatus | INV015_PowerCurtailmentStatus | INV015 | Inverter | Power Curtailment Status
EVT_INV015_RemoteOFFStatus | INV015_RemoteOFFStatus | INV015 | Inverter | Remote ON/OFF Status
EVT_INV016_InverterGridConnectionStatus | INV016_InverterGridConnectionStatus | INV016 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV016_InverterStartupShutdownStatus | INV016_InverterStartupShutdownStatus | INV016 | Inverter | Inverter startup/shutdown status
EVT_INV016_PowerCurtailmentStatus | INV016_PowerCurtailmentStatus | INV016 | Inverter | Power Curtailment Status
EVT_INV016_RemoteOFFStatus | INV016_RemoteOFFStatus | INV016 | Inverter | Remote ON/OFF Status
EVT_INV017_InverterGridConnectionStatus | INV017_InverterGridConnectionStatus | INV017 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV017_InverterStartupShutdownStatus | INV017_InverterStartupShutdownStatus | INV017 | Inverter | Inverter startup/shutdown status
EVT_INV017_PowerCurtailmentStatus | INV017_PowerCurtailmentStatus | INV017 | Inverter | Power Curtailment Status
EVT_INV017_RemoteOFFStatus | INV017_RemoteOFFStatus | INV017 | Inverter | Remote ON/OFF Status
EVT_INV018_InverterGridConnectionStatus | INV018_InverterGridConnectionStatus | INV018 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV018_InverterStartupShutdownStatus | INV018_InverterStartupShutdownStatus | INV018 | Inverter | Inverter startup/shutdown status
EVT_INV018_PowerCurtailmentStatus | INV018_PowerCurtailmentStatus | INV018 | Inverter | Power Curtailment Status
EVT_INV018_RemoteOFFStatus | INV018_RemoteOFFStatus | INV018 | Inverter | Remote ON/OFF Status
EVT_INV019_InverterGridConnectionStatus | INV019_InverterGridConnectionStatus | INV019 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV019_InverterStartupShutdownStatus | INV019_InverterStartupShutdownStatus | INV019 | Inverter | Inverter startup/shutdown status
EVT_INV019_PowerCurtailmentStatus | INV019_PowerCurtailmentStatus | INV019 | Inverter | Power Curtailment Status
EVT_INV019_RemoteOFFStatus | INV019_RemoteOFFStatus | INV019 | Inverter | Remote ON/OFF Status
EVT_INV020_InverterGridConnectionStatus | INV020_InverterGridConnectionStatus | INV020 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV020_InverterStartupShutdownStatus | INV020_InverterStartupShutdownStatus | INV020 | Inverter | Inverter startup/shutdown status
EVT_INV020_PowerCurtailmentStatus | INV020_PowerCurtailmentStatus | INV020 | Inverter | Power Curtailment Status
EVT_INV020_RemoteOFFStatus | INV020_RemoteOFFStatus | INV020 | Inverter | Remote ON/OFF Status
EVT_INV021_InverterGridConnectionStatus | INV021_InverterGridConnectionStatus | INV021 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV021_InverterStartupShutdownStatus | INV021_InverterStartupShutdownStatus | INV021 | Inverter | Inverter startup/shutdown status
EVT_INV021_PowerCurtailmentStatus | INV021_PowerCurtailmentStatus | INV021 | Inverter | Power Curtailment Status
EVT_INV021_RemoteOFFStatus | INV021_RemoteOFFStatus | INV021 | Inverter | Remote ON/OFF Status
EVT_INV022_InverterGridConnectionStatus | INV022_InverterGridConnectionStatus | INV022 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV022_InverterStartupShutdownStatus | INV022_InverterStartupShutdownStatus | INV022 | Inverter | Inverter startup/shutdown status
EVT_INV022_PowerCurtailmentStatus | INV022_PowerCurtailmentStatus | INV022 | Inverter | Power Curtailment Status
EVT_INV022_RemoteOFFStatus | INV022_RemoteOFFStatus | INV022 | Inverter | Remote ON/OFF Status
EVT_INV023_InverterGridConnectionStatus | INV023_InverterGridConnectionStatus | INV023 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV023_InverterStartupShutdownStatus | INV023_InverterStartupShutdownStatus | INV023 | Inverter | Inverter startup/shutdown status
EVT_INV023_PowerCurtailmentStatus | INV023_PowerCurtailmentStatus | INV023 | Inverter | Power Curtailment Status
EVT_INV023_RemoteOFFStatus | INV023_RemoteOFFStatus | INV023 | Inverter | Remote ON/OFF Status
EVT_INV024_InverterGridConnectionStatus | INV024_InverterGridConnectionStatus | INV024 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV024_InverterStartupShutdownStatus | INV024_InverterStartupShutdownStatus | INV024 | Inverter | Inverter startup/shutdown status
EVT_INV024_PowerCurtailmentStatus | INV024_PowerCurtailmentStatus | INV024 | Inverter | Power Curtailment Status
EVT_INV024_RemoteOFFStatus | INV024_RemoteOFFStatus | INV024 | Inverter | Remote ON/OFF Status
EVT_INV025_InverterGridConnectionStatus | INV025_InverterGridConnectionStatus | INV025 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV025_InverterStartupShutdownStatus | INV025_InverterStartupShutdownStatus | INV025 | Inverter | Inverter startup/shutdown status
EVT_INV025_PowerCurtailmentStatus | INV025_PowerCurtailmentStatus | INV025 | Inverter | Power Curtailment Status
EVT_INV025_RemoteOFFStatus | INV025_RemoteOFFStatus | INV025 | Inverter | Remote ON/OFF Status
EVT_INV026_InverterGridConnectionStatus | INV026_InverterGridConnectionStatus | INV026 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV026_InverterStartupShutdownStatus | INV026_InverterStartupShutdownStatus | INV026 | Inverter | Inverter startup/shutdown status
EVT_INV026_PowerCurtailmentStatus | INV026_PowerCurtailmentStatus | INV026 | Inverter | Power Curtailment Status
EVT_INV026_RemoteOFFStatus | INV026_RemoteOFFStatus | INV026 | Inverter | Remote ON/OFF Status
EVT_INV027_InverterGridConnectionStatus | INV027_InverterGridConnectionStatus | INV027 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV027_InverterStartupShutdownStatus | INV027_InverterStartupShutdownStatus | INV027 | Inverter | Inverter startup/shutdown status
EVT_INV027_PowerCurtailmentStatus | INV027_PowerCurtailmentStatus | INV027 | Inverter | Power Curtailment Status
EVT_INV027_RemoteOFFStatus | INV027_RemoteOFFStatus | INV027 | Inverter | Remote ON/OFF Status
EVT_INV028_InverterGridConnectionStatus | INV028_InverterGridConnectionStatus | INV028 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV028_InverterStartupShutdownStatus | INV028_InverterStartupShutdownStatus | INV028 | Inverter | Inverter startup/shutdown status
EVT_INV028_PowerCurtailmentStatus | INV028_PowerCurtailmentStatus | INV028 | Inverter | Power Curtailment Status
EVT_INV028_RemoteOFFStatus | INV028_RemoteOFFStatus | INV028 | Inverter | Remote ON/OFF Status
EVT_INV029_InverterGridConnectionStatus | INV029_InverterGridConnectionStatus | INV029 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV029_InverterStartupShutdownStatus | INV029_InverterStartupShutdownStatus | INV029 | Inverter | Inverter startup/shutdown status
EVT_INV029_PowerCurtailmentStatus | INV029_PowerCurtailmentStatus | INV029 | Inverter | Power Curtailment Status
EVT_INV029_RemoteOFFStatus | INV029_RemoteOFFStatus | INV029 | Inverter | Remote ON/OFF Status
EVT_INV030_InverterGridConnectionStatus | INV030_InverterGridConnectionStatus | INV030 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV030_InverterStartupShutdownStatus | INV030_InverterStartupShutdownStatus | INV030 | Inverter | Inverter startup/shutdown status
EVT_INV030_PowerCurtailmentStatus | INV030_PowerCurtailmentStatus | INV030 | Inverter | Power Curtailment Status
EVT_INV030_RemoteOFFStatus | INV030_RemoteOFFStatus | INV030 | Inverter | Remote ON/OFF Status
EVT_INV031_InverterGridConnectionStatus | INV031_InverterGridConnectionStatus | INV031 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV031_InverterStartupShutdownStatus | INV031_InverterStartupShutdownStatus | INV031 | Inverter | Inverter startup/shutdown status
EVT_INV031_PowerCurtailmentStatus | INV031_PowerCurtailmentStatus | INV031 | Inverter | Power Curtailment Status
EVT_INV031_RemoteOFFStatus | INV031_RemoteOFFStatus | INV031 | Inverter | Remote ON/OFF Status
EVT_INV032_InverterGridConnectionStatus | INV032_InverterGridConnectionStatus | INV032 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV032_InverterStartupShutdownStatus | INV032_InverterStartupShutdownStatus | INV032 | Inverter | Inverter startup/shutdown status
EVT_INV032_PowerCurtailmentStatus | INV032_PowerCurtailmentStatus | INV032 | Inverter | Power Curtailment Status
EVT_INV032_RemoteOFFStatus | INV032_RemoteOFFStatus | INV032 | Inverter | Remote ON/OFF Status
EVT_INV033_InverterGridConnectionStatus | INV033_InverterGridConnectionStatus | INV033 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV033_InverterStartupShutdownStatus | INV033_InverterStartupShutdownStatus | INV033 | Inverter | Inverter startup/shutdown status
EVT_INV033_PowerCurtailmentStatus | INV033_PowerCurtailmentStatus | INV033 | Inverter | Power Curtailment Status
EVT_INV033_RemoteOFFStatus | INV033_RemoteOFFStatus | INV033 | Inverter | Remote ON/OFF Status
EVT_INV034_InverterGridConnectionStatus | INV034_InverterGridConnectionStatus | INV034 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV034_InverterStartupShutdownStatus | INV034_InverterStartupShutdownStatus | INV034 | Inverter | Inverter startup/shutdown status
EVT_INV034_PowerCurtailmentStatus | INV034_PowerCurtailmentStatus | INV034 | Inverter | Power Curtailment Status
EVT_INV034_RemoteOFFStatus | INV034_RemoteOFFStatus | INV034 | Inverter | Remote ON/OFF Status
EVT_INV035_InverterGridConnectionStatus | INV035_InverterGridConnectionStatus | INV035 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV035_InverterStartupShutdownStatus | INV035_InverterStartupShutdownStatus | INV035 | Inverter | Inverter startup/shutdown status
EVT_INV035_PowerCurtailmentStatus | INV035_PowerCurtailmentStatus | INV035 | Inverter | Power Curtailment Status
EVT_INV035_RemoteOFFStatus | INV035_RemoteOFFStatus | INV035 | Inverter | Remote ON/OFF Status
EVT_INV036_InverterGridConnectionStatus | INV036_InverterGridConnectionStatus | INV036 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV036_InverterStartupShutdownStatus | INV036_InverterStartupShutdownStatus | INV036 | Inverter | Inverter startup/shutdown status
EVT_INV036_PowerCurtailmentStatus | INV036_PowerCurtailmentStatus | INV036 | Inverter | Power Curtailment Status
EVT_INV036_RemoteOFFStatus | INV036_RemoteOFFStatus | INV036 | Inverter | Remote ON/OFF Status
EVT_INV037_InverterGridConnectionStatus | INV037_InverterGridConnectionStatus | INV037 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV037_InverterStartupShutdownStatus | INV037_InverterStartupShutdownStatus | INV037 | Inverter | Inverter startup/shutdown status
EVT_INV037_PowerCurtailmentStatus | INV037_PowerCurtailmentStatus | INV037 | Inverter | Power Curtailment Status
EVT_INV037_RemoteOFFStatus | INV037_RemoteOFFStatus | INV037 | Inverter | Remote ON/OFF Status
EVT_INV038_InverterGridConnectionStatus | INV038_InverterGridConnectionStatus | INV038 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV038_InverterStartupShutdownStatus | INV038_InverterStartupShutdownStatus | INV038 | Inverter | Inverter startup/shutdown status
EVT_INV038_PowerCurtailmentStatus | INV038_PowerCurtailmentStatus | INV038 | Inverter | Power Curtailment Status
EVT_INV038_RemoteOFFStatus | INV038_RemoteOFFStatus | INV038 | Inverter | Remote ON/OFF Status
EVT_INV039_InverterGridConnectionStatus | INV039_InverterGridConnectionStatus | INV039 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV039_InverterStartupShutdownStatus | INV039_InverterStartupShutdownStatus | INV039 | Inverter | Inverter startup/shutdown status
EVT_INV039_PowerCurtailmentStatus | INV039_PowerCurtailmentStatus | INV039 | Inverter | Power Curtailment Status
EVT_INV039_RemoteOFFStatus | INV039_RemoteOFFStatus | INV039 | Inverter | Remote ON/OFF Status
EVT_INV040_InverterGridConnectionStatus | INV040_InverterGridConnectionStatus | INV040 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV040_InverterStartupShutdownStatus | INV040_InverterStartupShutdownStatus | INV040 | Inverter | Inverter startup/shutdown status
EVT_INV040_PowerCurtailmentStatus | INV040_PowerCurtailmentStatus | INV040 | Inverter | Power Curtailment Status
EVT_INV040_RemoteOFFStatus | INV040_RemoteOFFStatus | INV040 | Inverter | Remote ON/OFF Status
EVT_INV041_InverterGridConnectionStatus | INV041_InverterGridConnectionStatus | INV041 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV041_InverterStartupShutdownStatus | INV041_InverterStartupShutdownStatus | INV041 | Inverter | Inverter startup/shutdown status
EVT_INV041_PowerCurtailmentStatus | INV041_PowerCurtailmentStatus | INV041 | Inverter | Power Curtailment Status
EVT_INV041_RemoteOFFStatus | INV041_RemoteOFFStatus | INV041 | Inverter | Remote ON/OFF Status
EVT_INV042_InverterGridConnectionStatus | INV042_InverterGridConnectionStatus | INV042 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV042_InverterStartupShutdownStatus | INV042_InverterStartupShutdownStatus | INV042 | Inverter | Inverter startup/shutdown status
EVT_INV042_PowerCurtailmentStatus | INV042_PowerCurtailmentStatus | INV042 | Inverter | Power Curtailment Status
EVT_INV042_RemoteOFFStatus | INV042_RemoteOFFStatus | INV042 | Inverter | Remote ON/OFF Status
EVT_INV043_InverterGridConnectionStatus | INV043_InverterGridConnectionStatus | INV043 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV043_InverterStartupShutdownStatus | INV043_InverterStartupShutdownStatus | INV043 | Inverter | Inverter startup/shutdown status
EVT_INV043_PowerCurtailmentStatus | INV043_PowerCurtailmentStatus | INV043 | Inverter | Power Curtailment Status
EVT_INV043_RemoteOFFStatus | INV043_RemoteOFFStatus | INV043 | Inverter | Remote ON/OFF Status
EVT_INV044_InverterGridConnectionStatus | INV044_InverterGridConnectionStatus | INV044 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV044_InverterStartupShutdownStatus | INV044_InverterStartupShutdownStatus | INV044 | Inverter | Inverter startup/shutdown status
EVT_INV044_PowerCurtailmentStatus | INV044_PowerCurtailmentStatus | INV044 | Inverter | Power Curtailment Status
EVT_INV044_RemoteOFFStatus | INV044_RemoteOFFStatus | INV044 | Inverter | Remote ON/OFF Status
EVT_INV045_InverterGridConnectionStatus | INV045_InverterGridConnectionStatus | INV045 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV045_InverterStartupShutdownStatus | INV045_InverterStartupShutdownStatus | INV045 | Inverter | Inverter startup/shutdown status
EVT_INV045_PowerCurtailmentStatus | INV045_PowerCurtailmentStatus | INV045 | Inverter | Power Curtailment Status
EVT_INV045_RemoteOFFStatus | INV045_RemoteOFFStatus | INV045 | Inverter | Remote ON/OFF Status
EVT_INV046_InverterGridConnectionStatus | INV046_InverterGridConnectionStatus | INV046 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV046_InverterStartupShutdownStatus | INV046_InverterStartupShutdownStatus | INV046 | Inverter | Inverter startup/shutdown status
EVT_INV046_PowerCurtailmentStatus | INV046_PowerCurtailmentStatus | INV046 | Inverter | Power Curtailment Status
EVT_INV046_RemoteOFFStatus | INV046_RemoteOFFStatus | INV046 | Inverter | Remote ON/OFF Status
EVT_INV047_InverterGridConnectionStatus | INV047_InverterGridConnectionStatus | INV047 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV047_InverterStartupShutdownStatus | INV047_InverterStartupShutdownStatus | INV047 | Inverter | Inverter startup/shutdown status
EVT_INV047_PowerCurtailmentStatus | INV047_PowerCurtailmentStatus | INV047 | Inverter | Power Curtailment Status
EVT_INV047_RemoteOFFStatus | INV047_RemoteOFFStatus | INV047 | Inverter | Remote ON/OFF Status
EVT_INV048_InverterGridConnectionStatus | INV048_InverterGridConnectionStatus | INV048 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV048_InverterStartupShutdownStatus | INV048_InverterStartupShutdownStatus | INV048 | Inverter | Inverter startup/shutdown status
EVT_INV048_PowerCurtailmentStatus | INV048_PowerCurtailmentStatus | INV048 | Inverter | Power Curtailment Status
EVT_INV048_RemoteOFFStatus | INV048_RemoteOFFStatus | INV048 | Inverter | Remote ON/OFF Status
EVT_INV049_InverterGridConnectionStatus | INV049_InverterGridConnectionStatus | INV049 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV049_InverterStartupShutdownStatus | INV049_InverterStartupShutdownStatus | INV049 | Inverter | Inverter startup/shutdown status
EVT_INV049_PowerCurtailmentStatus | INV049_PowerCurtailmentStatus | INV049 | Inverter | Power Curtailment Status
EVT_INV049_RemoteOFFStatus | INV049_RemoteOFFStatus | INV049 | Inverter | Remote ON/OFF Status
EVT_INV050_InverterGridConnectionStatus | INV050_InverterGridConnectionStatus | INV050 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV050_InverterStartupShutdownStatus | INV050_InverterStartupShutdownStatus | INV050 | Inverter | Inverter startup/shutdown status
EVT_INV050_PowerCurtailmentStatus | INV050_PowerCurtailmentStatus | INV050 | Inverter | Power Curtailment Status
EVT_INV050_RemoteOFFStatus | INV050_RemoteOFFStatus | INV050 | Inverter | Remote ON/OFF Status
EVT_INV051_InverterGridConnectionStatus | INV051_InverterGridConnectionStatus | INV051 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV051_InverterStartupShutdownStatus | INV051_InverterStartupShutdownStatus | INV051 | Inverter | Inverter startup/shutdown status
EVT_INV051_PowerCurtailmentStatus | INV051_PowerCurtailmentStatus | INV051 | Inverter | Power Curtailment Status
EVT_INV051_RemoteOFFStatus | INV051_RemoteOFFStatus | INV051 | Inverter | Remote ON/OFF Status
EVT_INV052_InverterGridConnectionStatus | INV052_InverterGridConnectionStatus | INV052 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV052_InverterStartupShutdownStatus | INV052_InverterStartupShutdownStatus | INV052 | Inverter | Inverter startup/shutdown status
EVT_INV052_PowerCurtailmentStatus | INV052_PowerCurtailmentStatus | INV052 | Inverter | Power Curtailment Status
EVT_INV052_RemoteOFFStatus | INV052_RemoteOFFStatus | INV052 | Inverter | Remote ON/OFF Status
EVT_INV053_InverterGridConnectionStatus | INV053_InverterGridConnectionStatus | INV053 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV053_InverterStartupShutdownStatus | INV053_InverterStartupShutdownStatus | INV053 | Inverter | Inverter startup/shutdown status
EVT_INV053_PowerCurtailmentStatus | INV053_PowerCurtailmentStatus | INV053 | Inverter | Power Curtailment Status
EVT_INV053_RemoteOFFStatus | INV053_RemoteOFFStatus | INV053 | Inverter | Remote ON/OFF Status
EVT_INV054_InverterGridConnectionStatus | INV054_InverterGridConnectionStatus | INV054 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV054_InverterStartupShutdownStatus | INV054_InverterStartupShutdownStatus | INV054 | Inverter | Inverter startup/shutdown status
EVT_INV054_PowerCurtailmentStatus | INV054_PowerCurtailmentStatus | INV054 | Inverter | Power Curtailment Status
EVT_INV054_RemoteOFFStatus | INV054_RemoteOFFStatus | INV054 | Inverter | Remote ON/OFF Status
EVT_INV055_InverterGridConnectionStatus | INV055_InverterGridConnectionStatus | INV055 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV055_InverterStartupShutdownStatus | INV055_InverterStartupShutdownStatus | INV055 | Inverter | Inverter startup/shutdown status
EVT_INV055_PowerCurtailmentStatus | INV055_PowerCurtailmentStatus | INV055 | Inverter | Power Curtailment Status
EVT_INV055_RemoteOFFStatus | INV055_RemoteOFFStatus | INV055 | Inverter | Remote ON/OFF Status
EVT_INV056_InverterGridConnectionStatus | INV056_InverterGridConnectionStatus | INV056 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV056_InverterStartupShutdownStatus | INV056_InverterStartupShutdownStatus | INV056 | Inverter | Inverter startup/shutdown status
EVT_INV056_PowerCurtailmentStatus | INV056_PowerCurtailmentStatus | INV056 | Inverter | Power Curtailment Status
EVT_INV056_RemoteOFFStatus | INV056_RemoteOFFStatus | INV056 | Inverter | Remote ON/OFF Status
EVT_INV057_InverterGridConnectionStatus | INV057_InverterGridConnectionStatus | INV057 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV057_InverterStartupShutdownStatus | INV057_InverterStartupShutdownStatus | INV057 | Inverter | Inverter startup/shutdown status
EVT_INV057_PowerCurtailmentStatus | INV057_PowerCurtailmentStatus | INV057 | Inverter | Power Curtailment Status
EVT_INV057_RemoteOFFStatus | INV057_RemoteOFFStatus | INV057 | Inverter | Remote ON/OFF Status
EVT_INV058_InverterGridConnectionStatus | INV058_InverterGridConnectionStatus | INV058 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV058_InverterStartupShutdownStatus | INV058_InverterStartupShutdownStatus | INV058 | Inverter | Inverter startup/shutdown status
EVT_INV058_PowerCurtailmentStatus | INV058_PowerCurtailmentStatus | INV058 | Inverter | Power Curtailment Status
EVT_INV058_RemoteOFFStatus | INV058_RemoteOFFStatus | INV058 | Inverter | Remote ON/OFF Status
EVT_INV059_InverterGridConnectionStatus | INV059_InverterGridConnectionStatus | INV059 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV059_InverterStartupShutdownStatus | INV059_InverterStartupShutdownStatus | INV059 | Inverter | Inverter startup/shutdown status
EVT_INV059_PowerCurtailmentStatus | INV059_PowerCurtailmentStatus | INV059 | Inverter | Power Curtailment Status
EVT_INV059_RemoteOFFStatus | INV059_RemoteOFFStatus | INV059 | Inverter | Remote ON/OFF Status
EVT_INV060_InverterGridConnectionStatus | INV060_InverterGridConnectionStatus | INV060 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV060_InverterStartupShutdownStatus | INV060_InverterStartupShutdownStatus | INV060 | Inverter | Inverter startup/shutdown status
EVT_INV060_PowerCurtailmentStatus | INV060_PowerCurtailmentStatus | INV060 | Inverter | Power Curtailment Status
EVT_INV060_RemoteOFFStatus | INV060_RemoteOFFStatus | INV060 | Inverter | Remote ON/OFF Status
EVT_INV061_InverterGridConnectionStatus | INV061_InverterGridConnectionStatus | INV061 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV061_InverterStartupShutdownStatus | INV061_InverterStartupShutdownStatus | INV061 | Inverter | Inverter startup/shutdown status
EVT_INV061_PowerCurtailmentStatus | INV061_PowerCurtailmentStatus | INV061 | Inverter | Power Curtailment Status
EVT_INV061_RemoteOFFStatus | INV061_RemoteOFFStatus | INV061 | Inverter | Remote ON/OFF Status
EVT_INV062_InverterGridConnectionStatus | INV062_InverterGridConnectionStatus | INV062 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV062_InverterStartupShutdownStatus | INV062_InverterStartupShutdownStatus | INV062 | Inverter | Inverter startup/shutdown status
EVT_INV062_PowerCurtailmentStatus | INV062_PowerCurtailmentStatus | INV062 | Inverter | Power Curtailment Status
EVT_INV062_RemoteOFFStatus | INV062_RemoteOFFStatus | INV062 | Inverter | Remote ON/OFF Status
EVT_INV063_InverterGridConnectionStatus | INV063_InverterGridConnectionStatus | INV063 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV063_InverterStartupShutdownStatus | INV063_InverterStartupShutdownStatus | INV063 | Inverter | Inverter startup/shutdown status
EVT_INV063_PowerCurtailmentStatus | INV063_PowerCurtailmentStatus | INV063 | Inverter | Power Curtailment Status
EVT_INV063_RemoteOFFStatus | INV063_RemoteOFFStatus | INV063 | Inverter | Remote ON/OFF Status
EVT_INV064_InverterGridConnectionStatus | INV064_InverterGridConnectionStatus | INV064 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV064_InverterStartupShutdownStatus | INV064_InverterStartupShutdownStatus | INV064 | Inverter | Inverter startup/shutdown status
EVT_INV064_PowerCurtailmentStatus | INV064_PowerCurtailmentStatus | INV064 | Inverter | Power Curtailment Status
EVT_INV064_RemoteOFFStatus | INV064_RemoteOFFStatus | INV064 | Inverter | Remote ON/OFF Status
EVT_INV065_InverterGridConnectionStatus | INV065_InverterGridConnectionStatus | INV065 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV065_InverterStartupShutdownStatus | INV065_InverterStartupShutdownStatus | INV065 | Inverter | Inverter startup/shutdown status
EVT_INV065_PowerCurtailmentStatus | INV065_PowerCurtailmentStatus | INV065 | Inverter | Power Curtailment Status
EVT_INV065_RemoteOFFStatus | INV065_RemoteOFFStatus | INV065 | Inverter | Remote ON/OFF Status
EVT_INV066_InverterGridConnectionStatus | INV066_InverterGridConnectionStatus | INV066 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV066_InverterStartupShutdownStatus | INV066_InverterStartupShutdownStatus | INV066 | Inverter | Inverter startup/shutdown status
EVT_INV066_PowerCurtailmentStatus | INV066_PowerCurtailmentStatus | INV066 | Inverter | Power Curtailment Status
EVT_INV066_RemoteOFFStatus | INV066_RemoteOFFStatus | INV066 | Inverter | Remote ON/OFF Status
EVT_INV067_InverterGridConnectionStatus | INV067_InverterGridConnectionStatus | INV067 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV067_InverterStartupShutdownStatus | INV067_InverterStartupShutdownStatus | INV067 | Inverter | Inverter startup/shutdown status
EVT_INV067_PowerCurtailmentStatus | INV067_PowerCurtailmentStatus | INV067 | Inverter | Power Curtailment Status
EVT_INV067_RemoteOFFStatus | INV067_RemoteOFFStatus | INV067 | Inverter | Remote ON/OFF Status
EVT_INV068_InverterGridConnectionStatus | INV068_InverterGridConnectionStatus | INV068 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV068_InverterStartupShutdownStatus | INV068_InverterStartupShutdownStatus | INV068 | Inverter | Inverter startup/shutdown status
EVT_INV068_PowerCurtailmentStatus | INV068_PowerCurtailmentStatus | INV068 | Inverter | Power Curtailment Status
EVT_INV068_RemoteOFFStatus | INV068_RemoteOFFStatus | INV068 | Inverter | Remote ON/OFF Status
EVT_INV069_InverterGridConnectionStatus | INV069_InverterGridConnectionStatus | INV069 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV069_InverterStartupShutdownStatus | INV069_InverterStartupShutdownStatus | INV069 | Inverter | Inverter startup/shutdown status
EVT_INV069_PowerCurtailmentStatus | INV069_PowerCurtailmentStatus | INV069 | Inverter | Power Curtailment Status
EVT_INV069_RemoteOFFStatus | INV069_RemoteOFFStatus | INV069 | Inverter | Remote ON/OFF Status
EVT_INV070_InverterGridConnectionStatus | INV070_InverterGridConnectionStatus | INV070 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV070_InverterStartupShutdownStatus | INV070_InverterStartupShutdownStatus | INV070 | Inverter | Inverter startup/shutdown status
EVT_INV070_PowerCurtailmentStatus | INV070_PowerCurtailmentStatus | INV070 | Inverter | Power Curtailment Status
EVT_INV070_RemoteOFFStatus | INV070_RemoteOFFStatus | INV070 | Inverter | Remote ON/OFF Status
EVT_INV071_InverterGridConnectionStatus | INV071_InverterGridConnectionStatus | INV071 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV071_InverterStartupShutdownStatus | INV071_InverterStartupShutdownStatus | INV071 | Inverter | Inverter startup/shutdown status
EVT_INV071_PowerCurtailmentStatus | INV071_PowerCurtailmentStatus | INV071 | Inverter | Power Curtailment Status
EVT_INV071_RemoteOFFStatus | INV071_RemoteOFFStatus | INV071 | Inverter | Remote ON/OFF Status
EVT_INV072_InverterGridConnectionStatus | INV072_InverterGridConnectionStatus | INV072 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV072_InverterStartupShutdownStatus | INV072_InverterStartupShutdownStatus | INV072 | Inverter | Inverter startup/shutdown status
EVT_INV072_PowerCurtailmentStatus | INV072_PowerCurtailmentStatus | INV072 | Inverter | Power Curtailment Status
EVT_INV072_RemoteOFFStatus | INV072_RemoteOFFStatus | INV072 | Inverter | Remote ON/OFF Status
EVT_INV073_InverterGridConnectionStatus | INV073_InverterGridConnectionStatus | INV073 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV073_InverterStartupShutdownStatus | INV073_InverterStartupShutdownStatus | INV073 | Inverter | Inverter startup/shutdown status
EVT_INV073_PowerCurtailmentStatus | INV073_PowerCurtailmentStatus | INV073 | Inverter | Power Curtailment Status
EVT_INV073_RemoteOFFStatus | INV073_RemoteOFFStatus | INV073 | Inverter | Remote ON/OFF Status
EVT_INV074_InverterGridConnectionStatus | INV074_InverterGridConnectionStatus | INV074 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV074_InverterStartupShutdownStatus | INV074_InverterStartupShutdownStatus | INV074 | Inverter | Inverter startup/shutdown status
EVT_INV074_PowerCurtailmentStatus | INV074_PowerCurtailmentStatus | INV074 | Inverter | Power Curtailment Status
EVT_INV074_RemoteOFFStatus | INV074_RemoteOFFStatus | INV074 | Inverter | Remote ON/OFF Status
EVT_INV075_InverterGridConnectionStatus | INV075_InverterGridConnectionStatus | INV075 | Inverter | Inverter Grid Connection Status (Connected / Disconnected)
EVT_INV075_InverterStartupShutdownStatus | INV075_InverterStartupShutdownStatus | INV075 | Inverter | Inverter startup/shutdown status
EVT_INV075_PowerCurtailmentStatus | INV075_PowerCurtailmentStatus | INV075 | Inverter | Power Curtailment Status
EVT_INV075_RemoteOFFStatus | INV075_RemoteOFFStatus | INV075 | Inverter | Remote ON/OFF Status
EVT_PR001_CircuitBreakerClosePosition | PR001_CircuitBreakerClosePosition | PR001 | Protection Relay | Circuit breaker close position
EVT_PR001_CircuitBreakerOpenPosition | PR001_CircuitBreakerOpenPosition | PR001 | Protection Relay | Circuit breaker open position
EVT_PR001_EarthSwitchClosePosition | PR001_EarthSwitchClosePosition | PR001 | Protection Relay | Earth switch close position (1)
EVT_PR001_EarthSwitchOpenPosition | PR001_EarthSwitchOpenPosition | PR001 | Protection Relay | Earth switch open position (1)
EVT_PR001_RemoteLocalControlStatus | PR001_RemoteLocalControlStatus | PR001 | Protection Relay | Remote/local control status
EVT_PR001_RemoteLocalControlStatusR129_02 | PR001_RemoteLocalControlStatusR129_02 | PR001 | Protection Relay | Remote/local control status
EVT_PR001_TestServicePositionStatus | PR001_TestServicePositionStatus | PR001 | Protection Relay | Test/service position status
EVT_PR002_CircuitBreakerClosePosition | PR002_CircuitBreakerClosePosition | PR002 | Protection Relay | Circuit breaker close position
EVT_PR002_CircuitBreakerOpenPosition | PR002_CircuitBreakerOpenPosition | PR002 | Protection Relay | Circuit breaker open position
EVT_PR002_EarthSwitchClosePosition | PR002_EarthSwitchClosePosition | PR002 | Protection Relay | Earth switch close position (1)
EVT_PR002_EarthSwitchOpenPosition | PR002_EarthSwitchOpenPosition | PR002 | Protection Relay | Earth switch open position (1)
EVT_PR002_RemoteLocalControlStatus | PR002_RemoteLocalControlStatus | PR002 | Protection Relay | Remote/local control status
EVT_PR002_RemoteLocalControlStatusR129_02 | PR002_RemoteLocalControlStatusR129_02 | PR002 | Protection Relay | Remote/local control status
EVT_PR002_TestServicePositionStatus | PR002_TestServicePositionStatus | PR002 | Protection Relay | Test/service position status
EVT_PR003_CircuitBreakerClosePosition | PR003_CircuitBreakerClosePosition | PR003 | Protection Relay | Circuit breaker close position
EVT_PR003_CircuitBreakerOpenPosition | PR003_CircuitBreakerOpenPosition | PR003 | Protection Relay | Circuit breaker open position
EVT_PR003_EarthSwitchClosePosition | PR003_EarthSwitchClosePosition | PR003 | Protection Relay | Earth switch close position (1)
EVT_PR003_EarthSwitchOpenPosition | PR003_EarthSwitchOpenPosition | PR003 | Protection Relay | Earth switch open position (1)
EVT_PR003_RemoteLocalControlStatus | PR003_RemoteLocalControlStatus | PR003 | Protection Relay | Remote/local control status
EVT_PR003_RemoteLocalControlStatusR129_02 | PR003_RemoteLocalControlStatusR129_02 | PR003 | Protection Relay | Remote/local control status
EVT_PR003_TestServicePositionStatus | PR003_TestServicePositionStatus | PR003 | Protection Relay | Test/service position status
EVT_PR004_CircuitBreakerClosePosition | PR004_CircuitBreakerClosePosition | PR004 | Protection Relay | Circuit breaker close position
EVT_PR004_CircuitBreakerOpenPosition | PR004_CircuitBreakerOpenPosition | PR004 | Protection Relay | Circuit breaker open position
EVT_PR004_EarthSwitchClosePosition | PR004_EarthSwitchClosePosition | PR004 | Protection Relay | Earth switch close position (1)
EVT_PR004_EarthSwitchOpenPosition | PR004_EarthSwitchOpenPosition | PR004 | Protection Relay | Earth switch open position (1)
EVT_PR004_RemoteLocalControlStatus | PR004_RemoteLocalControlStatus | PR004 | Protection Relay | Remote/local control status
EVT_PR004_RemoteLocalControlStatusR129_02 | PR004_RemoteLocalControlStatusR129_02 | PR004 | Protection Relay | Remote/local control status
EVT_PR004_TestServicePositionStatus | PR004_TestServicePositionStatus | PR004 | Protection Relay | Test/service position status
EVT_PR005_CircuitBreakerClosePosition | PR005_CircuitBreakerClosePosition | PR005 | Protection Relay | Circuit breaker close position
EVT_PR005_CircuitBreakerOpenPosition | PR005_CircuitBreakerOpenPosition | PR005 | Protection Relay | Circuit breaker open position
EVT_PR005_EarthSwitchClosePosition | PR005_EarthSwitchClosePosition | PR005 | Protection Relay | Earth switch close position (1)
EVT_PR005_EarthSwitchOpenPosition | PR005_EarthSwitchOpenPosition | PR005 | Protection Relay | Earth switch open position (1)
EVT_PR005_RemoteLocalControlStatus | PR005_RemoteLocalControlStatus | PR005 | Protection Relay | Remote/local control status
EVT_PR005_RemoteLocalControlStatusR129_02 | PR005_RemoteLocalControlStatusR129_02 | PR005 | Protection Relay | Remote/local control status
EVT_PR005_TestServicePositionStatus | PR005_TestServicePositionStatus | PR005 | Protection Relay | Test/service position status
EVT_PR006_CircuitBreakerClosePosition | PR006_CircuitBreakerClosePosition | PR006 | Protection Relay | Circuit breaker close position
EVT_PR006_CircuitBreakerOpenPosition | PR006_CircuitBreakerOpenPosition | PR006 | Protection Relay | Circuit breaker open position
EVT_PR006_EarthSwitchClosePosition | PR006_EarthSwitchClosePosition | PR006 | Protection Relay | Earth switch close position (1)
EVT_PR006_EarthSwitchOpenPosition | PR006_EarthSwitchOpenPosition | PR006 | Protection Relay | Earth switch open position (1)
EVT_PR006_RemoteLocalControlStatus | PR006_RemoteLocalControlStatus | PR006 | Protection Relay | Remote/local control status
EVT_PR006_RemoteLocalControlStatusR129_02 | PR006_RemoteLocalControlStatusR129_02 | PR006 | Protection Relay | Remote/local control status
EVT_PR006_TestServicePositionStatus | PR006_TestServicePositionStatus | PR006 | Protection Relay | Test/service position status
EVT_PR007_CircuitBreakerClosePosition | PR007_CircuitBreakerClosePosition | PR007 | Protection Relay | Circuit breaker close position
EVT_PR007_CircuitBreakerOpenPosition | PR007_CircuitBreakerOpenPosition | PR007 | Protection Relay | Circuit breaker open position
EVT_PR007_EarthSwitchClosePosition | PR007_EarthSwitchClosePosition | PR007 | Protection Relay | Earth switch close position (1)
EVT_PR007_EarthSwitchOpenPosition | PR007_EarthSwitchOpenPosition | PR007 | Protection Relay | Earth switch open position (1)
EVT_PR007_RemoteLocalControlStatus | PR007_RemoteLocalControlStatus | PR007 | Protection Relay | Remote/local control status
EVT_PR007_RemoteLocalControlStatusR129_02 | PR007_RemoteLocalControlStatusR129_02 | PR007 | Protection Relay | Remote/local control status
EVT_PR007_TestServicePositionStatus | PR007_TestServicePositionStatus | PR007 | Protection Relay | Test/service position status
EVT_PR008_CircuitBreakerClosePosition | PR008_CircuitBreakerClosePosition | PR008 | Protection Relay | Circuit breaker close position
EVT_PR008_CircuitBreakerOpenPosition | PR008_CircuitBreakerOpenPosition | PR008 | Protection Relay | Circuit breaker open position
EVT_PR008_EarthSwitchClosePosition | PR008_EarthSwitchClosePosition | PR008 | Protection Relay | Earth switch close position (1)
EVT_PR008_EarthSwitchOpenPosition | PR008_EarthSwitchOpenPosition | PR008 | Protection Relay | Earth switch open position (1)
EVT_PR008_RemoteLocalControlStatus | PR008_RemoteLocalControlStatus | PR008 | Protection Relay | Remote/local control status
EVT_PR008_RemoteLocalControlStatusR129_02 | PR008_RemoteLocalControlStatusR129_02 | PR008 | Protection Relay | Remote/local control status
EVT_PR008_TestServicePositionStatus | PR008_TestServicePositionStatus | PR008 | Protection Relay | Test/service position status
EVT_PR009_CircuitBreakerClosePosition | PR009_CircuitBreakerClosePosition | PR009 | Protection Relay | Circuit breaker close position
EVT_PR009_CircuitBreakerOpenPosition | PR009_CircuitBreakerOpenPosition | PR009 | Protection Relay | Circuit breaker open position
EVT_PR009_EarthSwitchClosePosition | PR009_EarthSwitchClosePosition | PR009 | Protection Relay | Earth switch close position (1)
EVT_PR009_EarthSwitchOpenPosition | PR009_EarthSwitchOpenPosition | PR009 | Protection Relay | Earth switch open position (1)
EVT_PR009_RemoteLocalControlStatus | PR009_RemoteLocalControlStatus | PR009 | Protection Relay | Remote/local control status
EVT_PR009_RemoteLocalControlStatusR129_02 | PR009_RemoteLocalControlStatusR129_02 | PR009 | Protection Relay | Remote/local control status
EVT_PR009_TestServicePositionStatus | PR009_TestServicePositionStatus | PR009 | Protection Relay | Test/service position status
EVT_PR010_CircuitBreakerClosePosition | PR010_CircuitBreakerClosePosition | PR010 | Protection Relay | Circuit breaker close position
EVT_PR010_CircuitBreakerOpenPosition | PR010_CircuitBreakerOpenPosition | PR010 | Protection Relay | Circuit breaker open position
EVT_PR010_EarthSwitchClosePosition | PR010_EarthSwitchClosePosition | PR010 | Protection Relay | Earth switch close position (1)
EVT_PR010_EarthSwitchOpenPosition | PR010_EarthSwitchOpenPosition | PR010 | Protection Relay | Earth switch open position (1)
EVT_PR010_RemoteLocalControlStatus | PR010_RemoteLocalControlStatus | PR010 | Protection Relay | Remote/local control status
EVT_PR010_RemoteLocalControlStatusR129_02 | PR010_RemoteLocalControlStatusR129_02 | PR010 | Protection Relay | Remote/local control status
EVT_PR010_TestServicePositionStatus | PR010_TestServicePositionStatus | PR010 | Protection Relay | Test/service position status
EVT_PR011_CircuitBreakerClosePosition | PR011_CircuitBreakerClosePosition | PR011 | Protection Relay | Circuit breaker close position
EVT_PR011_CircuitBreakerOpenPosition | PR011_CircuitBreakerOpenPosition | PR011 | Protection Relay | Circuit breaker open position
EVT_PR011_EarthSwitchClosePosition | PR011_EarthSwitchClosePosition | PR011 | Protection Relay | Earth switch close position (1)
EVT_PR011_EarthSwitchOpenPosition | PR011_EarthSwitchOpenPosition | PR011 | Protection Relay | Earth switch open position (1)
EVT_PR011_RemoteLocalControlStatus | PR011_RemoteLocalControlStatus | PR011 | Protection Relay | Remote/local control status
EVT_PR011_RemoteLocalControlStatusR129_02 | PR011_RemoteLocalControlStatusR129_02 | PR011 | Protection Relay | Remote/local control status
EVT_PR011_TestServicePositionStatus | PR011_TestServicePositionStatus | PR011 | Protection Relay | Test/service position status
EVT_PR012_CircuitBreakerClosePosition | PR012_CircuitBreakerClosePosition | PR012 | Protection Relay | Circuit breaker close position
EVT_PR012_CircuitBreakerOpenPosition | PR012_CircuitBreakerOpenPosition | PR012 | Protection Relay | Circuit breaker open position
EVT_PR012_EarthSwitchClosePosition | PR012_EarthSwitchClosePosition | PR012 | Protection Relay | Earth switch close position (1)
EVT_PR012_EarthSwitchOpenPosition | PR012_EarthSwitchOpenPosition | PR012 | Protection Relay | Earth switch open position (1)
EVT_PR012_RemoteLocalControlStatus | PR012_RemoteLocalControlStatus | PR012 | Protection Relay | Remote/local control status
EVT_PR012_RemoteLocalControlStatusR129_02 | PR012_RemoteLocalControlStatusR129_02 | PR012 | Protection Relay | Remote/local control status
EVT_PR012_TestServicePositionStatus | PR012_TestServicePositionStatus | PR012 | Protection Relay | Test/service position status
EVT_PR013_CircuitBreakerClosePosition | PR013_CircuitBreakerClosePosition | PR013 | Protection Relay | Circuit breaker close position
EVT_PR013_CircuitBreakerOpenPosition | PR013_CircuitBreakerOpenPosition | PR013 | Protection Relay | Circuit breaker open position
EVT_PR013_EarthSwitchClosePosition | PR013_EarthSwitchClosePosition | PR013 | Protection Relay | Earth switch close position (1)
EVT_PR013_EarthSwitchOpenPosition | PR013_EarthSwitchOpenPosition | PR013 | Protection Relay | Earth switch open position (1)
EVT_PR013_RemoteLocalControlStatus | PR013_RemoteLocalControlStatus | PR013 | Protection Relay | Remote/local control status
EVT_PR013_RemoteLocalControlStatusR129_02 | PR013_RemoteLocalControlStatusR129_02 | PR013 | Protection Relay | Remote/local control status
EVT_PR013_TestServicePositionStatus | PR013_TestServicePositionStatus | PR013 | Protection Relay | Test/service position status
EVT_PR014_CircuitBreakerClosePosition | PR014_CircuitBreakerClosePosition | PR014 | Protection Relay | Circuit breaker close position
EVT_PR014_CircuitBreakerOpenPosition | PR014_CircuitBreakerOpenPosition | PR014 | Protection Relay | Circuit breaker open position
EVT_PR014_EarthSwitchClosePosition | PR014_EarthSwitchClosePosition | PR014 | Protection Relay | Earth switch close position (1)
EVT_PR014_EarthSwitchOpenPosition | PR014_EarthSwitchOpenPosition | PR014 | Protection Relay | Earth switch open position (1)
EVT_PR014_RemoteLocalControlStatus | PR014_RemoteLocalControlStatus | PR014 | Protection Relay | Remote/local control status
EVT_PR014_RemoteLocalControlStatusR129_02 | PR014_RemoteLocalControlStatusR129_02 | PR014 | Protection Relay | Remote/local control status
EVT_PR014_TestServicePositionStatus | PR014_TestServicePositionStatus | PR014 | Protection Relay | Test/service position status

## Historian
Historian Data List
Recommended historian configuration. Analog points are periodic. Historian on MS SQL Server For 1 year
Tag Name | Device ID | Device Type | Signal Description | Point Type | Engineering Unit | Archive Mode | Sample / Trigger | Compression / Deadband | Retention
EM001_ActivePower | EM001 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM001_ApparentPower | EM001 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM001_Frequency | EM001 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM001_PhaseACurrent | EM001 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM001_PhaseBCurrent | EM001 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM001_PhaseCCurrent | EM001 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM001_PowerFactor | EM001 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM001_ReactivePower | EM001 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM001_TotalExportVarh | EM001 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM001_TotalExportWh | EM001 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM001_TotalImportVarh | EM001 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM001_TotalImportWh | EM001 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM002_ActivePower | EM002 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM002_ApparentPower | EM002 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM002_Frequency | EM002 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM002_PhaseACurrent | EM002 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM002_PhaseBCurrent | EM002 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM002_PhaseCCurrent | EM002 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM002_PowerFactor | EM002 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM002_ReactivePower | EM002 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM002_TotalExportVarh | EM002 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM002_TotalExportWh | EM002 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM002_TotalImportVarh | EM002 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM002_TotalImportWh | EM002 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM003_ActivePower | EM003 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM003_ApparentPower | EM003 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM003_Frequency | EM003 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM003_PhaseACurrent | EM003 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM003_PhaseBCurrent | EM003 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM003_PhaseCCurrent | EM003 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM003_PowerFactor | EM003 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM003_ReactivePower | EM003 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM003_TotalExportVarh | EM003 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM003_TotalExportWh | EM003 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM003_TotalImportVarh | EM003 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM003_TotalImportWh | EM003 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM004_ActivePower | EM004 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM004_ApparentPower | EM004 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM004_Frequency | EM004 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM004_PhaseACurrent | EM004 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM004_PhaseBCurrent | EM004 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM004_PhaseCCurrent | EM004 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM004_PowerFactor | EM004 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM004_ReactivePower | EM004 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM004_TotalExportVarh | EM004 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM004_TotalExportWh | EM004 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM004_TotalImportVarh | EM004 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM004_TotalImportWh | EM004 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM005_ActivePower | EM005 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM005_ApparentPower | EM005 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM005_Frequency | EM005 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM005_PhaseACurrent | EM005 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM005_PhaseBCurrent | EM005 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM005_PhaseCCurrent | EM005 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM005_PowerFactor | EM005 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM005_ReactivePower | EM005 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM005_TotalExportVarh | EM005 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM005_TotalExportWh | EM005 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM005_TotalImportVarh | EM005 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM005_TotalImportWh | EM005 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM006_ActivePower | EM006 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM006_ApparentPower | EM006 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM006_Frequency | EM006 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM006_PhaseACurrent | EM006 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM006_PhaseBCurrent | EM006 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM006_PhaseCCurrent | EM006 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM006_PowerFactor | EM006 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM006_ReactivePower | EM006 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM006_TotalExportVarh | EM006 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM006_TotalExportWh | EM006 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM006_TotalImportVarh | EM006 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM006_TotalImportWh | EM006 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM007_ActivePower | EM007 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM007_ApparentPower | EM007 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM007_Frequency | EM007 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM007_PhaseACurrent | EM007 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM007_PhaseBCurrent | EM007 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM007_PhaseCCurrent | EM007 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM007_PowerFactor | EM007 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM007_ReactivePower | EM007 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM007_TotalExportVarh | EM007 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM007_TotalExportWh | EM007 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM007_TotalImportVarh | EM007 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM007_TotalImportWh | EM007 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM008_ActivePower | EM008 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM008_ApparentPower | EM008 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM008_Frequency | EM008 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM008_PhaseACurrent | EM008 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM008_PhaseBCurrent | EM008 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM008_PhaseCCurrent | EM008 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM008_PowerFactor | EM008 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM008_ReactivePower | EM008 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM008_TotalExportVarh | EM008 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM008_TotalExportWh | EM008 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM008_TotalImportVarh | EM008 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM008_TotalImportWh | EM008 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM009_ActivePower | EM009 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM009_ApparentPower | EM009 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM009_Frequency | EM009 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM009_PhaseACurrent | EM009 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM009_PhaseBCurrent | EM009 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM009_PhaseCCurrent | EM009 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM009_PowerFactor | EM009 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM009_ReactivePower | EM009 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM009_TotalExportVarh | EM009 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM009_TotalExportWh | EM009 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM009_TotalImportVarh | EM009 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM009_TotalImportWh | EM009 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM010_ActivePower | EM010 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM010_ApparentPower | EM010 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM010_Frequency | EM010 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM010_PhaseACurrent | EM010 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM010_PhaseBCurrent | EM010 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM010_PhaseCCurrent | EM010 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM010_PowerFactor | EM010 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM010_ReactivePower | EM010 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM010_TotalExportVarh | EM010 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM010_TotalExportWh | EM010 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM010_TotalImportVarh | EM010 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM010_TotalImportWh | EM010 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM011_ActivePower | EM011 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM011_ApparentPower | EM011 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM011_Frequency | EM011 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM011_PhaseACurrent | EM011 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM011_PhaseBCurrent | EM011 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM011_PhaseCCurrent | EM011 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM011_PowerFactor | EM011 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM011_ReactivePower | EM011 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM011_TotalExportVarh | EM011 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM011_TotalExportWh | EM011 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM011_TotalImportVarh | EM011 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM011_TotalImportWh | EM011 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM012_ActivePower | EM012 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM012_ApparentPower | EM012 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM012_Frequency | EM012 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM012_PhaseACurrent | EM012 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM012_PhaseBCurrent | EM012 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM012_PhaseCCurrent | EM012 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM012_PowerFactor | EM012 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM012_ReactivePower | EM012 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM012_TotalExportVarh | EM012 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM012_TotalExportWh | EM012 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM012_TotalImportVarh | EM012 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM012_TotalImportWh | EM012 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM013_ActivePower | EM013 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM013_ApparentPower | EM013 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM013_Frequency | EM013 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM013_PhaseACurrent | EM013 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM013_PhaseBCurrent | EM013 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM013_PhaseCCurrent | EM013 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM013_PowerFactor | EM013 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM013_ReactivePower | EM013 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM013_TotalExportVarh | EM013 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM013_TotalExportWh | EM013 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM013_TotalImportVarh | EM013 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM013_TotalImportWh | EM013 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM014_ActivePower | EM014 | Energy Meter | Active power | Analog | kW | Periodic | 60 s | 0.1 | 1 years
EM014_ApparentPower | EM014 | Energy Meter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
EM014_Frequency | EM014 | Energy Meter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
EM014_PhaseACurrent | EM014 | Energy Meter | Phase A Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM014_PhaseBCurrent | EM014 | Energy Meter | Phase B Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM014_PhaseCCurrent | EM014 | Energy Meter | Phase C Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
EM014_PowerFactor | EM014 | Energy Meter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
EM014_ReactivePower | EM014 | Energy Meter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
EM014_TotalExportVarh | EM014 | Energy Meter | Total export varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM014_TotalExportWh | EM014 | Energy Meter | Total export Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
EM014_TotalImportVarh | EM014 | Energy Meter | Total import varh | Analog | varh | Periodic | 300 s | 1.0 | 1 years
EM014_TotalImportWh | EM014 | Energy Meter | Total import Wh | Analog | Wh | Periodic | 300 s | 1.0 | 1 years
INV001_ACCurrent | INV001 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV001_ACVoltage | INV001 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV001_ActivePower | INV001 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV001_ApparentPower | INV001 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV001_DCCurrent | INV001 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV001_DCPower | INV001 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV001_DCVoltage | INV001 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV001_DailyEnergyYield | INV001 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV001_Frequency | INV001 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV001_InverterEfficiency | INV001 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV001_InverterRunningStopped | INV001 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV001_PowerFactor | INV001 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV001_ReactivePower | INV001 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV001_TotalEnergyYield | INV001 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV002_ACCurrent | INV002 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV002_ACVoltage | INV002 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV002_ActivePower | INV002 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV002_ApparentPower | INV002 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV002_DCCurrent | INV002 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV002_DCPower | INV002 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV002_DCVoltage | INV002 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV002_DailyEnergyYield | INV002 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV002_Frequency | INV002 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV002_InverterEfficiency | INV002 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV002_InverterRunningStopped | INV002 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV002_PowerFactor | INV002 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV002_ReactivePower | INV002 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV002_TotalEnergyYield | INV002 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV003_ACCurrent | INV003 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV003_ACVoltage | INV003 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV003_ActivePower | INV003 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV003_ApparentPower | INV003 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV003_DCCurrent | INV003 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV003_DCPower | INV003 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV003_DCVoltage | INV003 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV003_DailyEnergyYield | INV003 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV003_Frequency | INV003 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV003_InverterEfficiency | INV003 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV003_InverterRunningStopped | INV003 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV003_PowerFactor | INV003 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV003_ReactivePower | INV003 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV003_TotalEnergyYield | INV003 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV004_ACCurrent | INV004 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV004_ACVoltage | INV004 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV004_ActivePower | INV004 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV004_ApparentPower | INV004 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV004_DCCurrent | INV004 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV004_DCPower | INV004 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV004_DCVoltage | INV004 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV004_DailyEnergyYield | INV004 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV004_Frequency | INV004 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV004_InverterEfficiency | INV004 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV004_InverterRunningStopped | INV004 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV004_PowerFactor | INV004 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV004_ReactivePower | INV004 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV004_TotalEnergyYield | INV004 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV005_ACCurrent | INV005 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV005_ACVoltage | INV005 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV005_ActivePower | INV005 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV005_ApparentPower | INV005 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV005_DCCurrent | INV005 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV005_DCPower | INV005 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV005_DCVoltage | INV005 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV005_DailyEnergyYield | INV005 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV005_Frequency | INV005 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV005_InverterEfficiency | INV005 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV005_InverterRunningStopped | INV005 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV005_PowerFactor | INV005 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV005_ReactivePower | INV005 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV005_TotalEnergyYield | INV005 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV006_ACCurrent | INV006 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV006_ACVoltage | INV006 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV006_ActivePower | INV006 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV006_ApparentPower | INV006 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV006_DCCurrent | INV006 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV006_DCPower | INV006 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV006_DCVoltage | INV006 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV006_DailyEnergyYield | INV006 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV006_Frequency | INV006 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV006_InverterEfficiency | INV006 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV006_InverterRunningStopped | INV006 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV006_PowerFactor | INV006 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV006_ReactivePower | INV006 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV006_TotalEnergyYield | INV006 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV007_ACCurrent | INV007 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV007_ACVoltage | INV007 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV007_ActivePower | INV007 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV007_ApparentPower | INV007 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV007_DCCurrent | INV007 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV007_DCPower | INV007 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV007_DCVoltage | INV007 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV007_DailyEnergyYield | INV007 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV007_Frequency | INV007 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV007_InverterEfficiency | INV007 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV007_InverterRunningStopped | INV007 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV007_PowerFactor | INV007 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV007_ReactivePower | INV007 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV007_TotalEnergyYield | INV007 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV008_ACCurrent | INV008 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV008_ACVoltage | INV008 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV008_ActivePower | INV008 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV008_ApparentPower | INV008 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV008_DCCurrent | INV008 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV008_DCPower | INV008 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV008_DCVoltage | INV008 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV008_DailyEnergyYield | INV008 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV008_Frequency | INV008 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV008_InverterEfficiency | INV008 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV008_InverterRunningStopped | INV008 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV008_PowerFactor | INV008 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV008_ReactivePower | INV008 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV008_TotalEnergyYield | INV008 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV009_ACCurrent | INV009 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV009_ACVoltage | INV009 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV009_ActivePower | INV009 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV009_ApparentPower | INV009 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV009_DCCurrent | INV009 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV009_DCPower | INV009 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV009_DCVoltage | INV009 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV009_DailyEnergyYield | INV009 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV009_Frequency | INV009 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV009_InverterEfficiency | INV009 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV009_InverterRunningStopped | INV009 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV009_PowerFactor | INV009 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV009_ReactivePower | INV009 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV009_TotalEnergyYield | INV009 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV010_ACCurrent | INV010 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV010_ACVoltage | INV010 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV010_ActivePower | INV010 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV010_ApparentPower | INV010 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV010_DCCurrent | INV010 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV010_DCPower | INV010 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV010_DCVoltage | INV010 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV010_DailyEnergyYield | INV010 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV010_Frequency | INV010 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV010_InverterEfficiency | INV010 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV010_InverterRunningStopped | INV010 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV010_PowerFactor | INV010 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV010_ReactivePower | INV010 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV010_TotalEnergyYield | INV010 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV011_ACCurrent | INV011 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV011_ACVoltage | INV011 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV011_ActivePower | INV011 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV011_ApparentPower | INV011 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV011_DCCurrent | INV011 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV011_DCPower | INV011 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV011_DCVoltage | INV011 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV011_DailyEnergyYield | INV011 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV011_Frequency | INV011 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV011_InverterEfficiency | INV011 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV011_InverterRunningStopped | INV011 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV011_PowerFactor | INV011 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV011_ReactivePower | INV011 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV011_TotalEnergyYield | INV011 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV012_ACCurrent | INV012 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV012_ACVoltage | INV012 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV012_ActivePower | INV012 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV012_ApparentPower | INV012 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV012_DCCurrent | INV012 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV012_DCPower | INV012 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV012_DCVoltage | INV012 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV012_DailyEnergyYield | INV012 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV012_Frequency | INV012 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV012_InverterEfficiency | INV012 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV012_InverterRunningStopped | INV012 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV012_PowerFactor | INV012 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV012_ReactivePower | INV012 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV012_TotalEnergyYield | INV012 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV013_ACCurrent | INV013 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV013_ACVoltage | INV013 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV013_ActivePower | INV013 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV013_ApparentPower | INV013 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV013_DCCurrent | INV013 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV013_DCPower | INV013 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV013_DCVoltage | INV013 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV013_DailyEnergyYield | INV013 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV013_Frequency | INV013 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV013_InverterEfficiency | INV013 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV013_InverterRunningStopped | INV013 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV013_PowerFactor | INV013 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV013_ReactivePower | INV013 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV013_TotalEnergyYield | INV013 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV014_ACCurrent | INV014 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV014_ACVoltage | INV014 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV014_ActivePower | INV014 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV014_ApparentPower | INV014 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV014_DCCurrent | INV014 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV014_DCPower | INV014 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV014_DCVoltage | INV014 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV014_DailyEnergyYield | INV014 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV014_Frequency | INV014 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV014_InverterEfficiency | INV014 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV014_InverterRunningStopped | INV014 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV014_PowerFactor | INV014 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV014_ReactivePower | INV014 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV014_TotalEnergyYield | INV014 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV015_ACCurrent | INV015 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV015_ACVoltage | INV015 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV015_ActivePower | INV015 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV015_ApparentPower | INV015 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV015_DCCurrent | INV015 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV015_DCPower | INV015 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV015_DCVoltage | INV015 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV015_DailyEnergyYield | INV015 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV015_Frequency | INV015 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV015_InverterEfficiency | INV015 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV015_InverterRunningStopped | INV015 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV015_PowerFactor | INV015 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV015_ReactivePower | INV015 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV015_TotalEnergyYield | INV015 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV016_ACCurrent | INV016 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV016_ACVoltage | INV016 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV016_ActivePower | INV016 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV016_ApparentPower | INV016 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV016_DCCurrent | INV016 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV016_DCPower | INV016 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV016_DCVoltage | INV016 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV016_DailyEnergyYield | INV016 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV016_Frequency | INV016 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV016_InverterEfficiency | INV016 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV016_InverterRunningStopped | INV016 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV016_PowerFactor | INV016 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV016_ReactivePower | INV016 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV016_TotalEnergyYield | INV016 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV017_ACCurrent | INV017 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV017_ACVoltage | INV017 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV017_ActivePower | INV017 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV017_ApparentPower | INV017 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV017_DCCurrent | INV017 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV017_DCPower | INV017 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV017_DCVoltage | INV017 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV017_DailyEnergyYield | INV017 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV017_Frequency | INV017 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV017_InverterEfficiency | INV017 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV017_InverterRunningStopped | INV017 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV017_PowerFactor | INV017 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV017_ReactivePower | INV017 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV017_TotalEnergyYield | INV017 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV018_ACCurrent | INV018 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV018_ACVoltage | INV018 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV018_ActivePower | INV018 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV018_ApparentPower | INV018 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV018_DCCurrent | INV018 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV018_DCPower | INV018 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV018_DCVoltage | INV018 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV018_DailyEnergyYield | INV018 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV018_Frequency | INV018 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV018_InverterEfficiency | INV018 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV018_InverterRunningStopped | INV018 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV018_PowerFactor | INV018 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV018_ReactivePower | INV018 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV018_TotalEnergyYield | INV018 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV019_ACCurrent | INV019 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV019_ACVoltage | INV019 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV019_ActivePower | INV019 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV019_ApparentPower | INV019 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV019_DCCurrent | INV019 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV019_DCPower | INV019 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV019_DCVoltage | INV019 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV019_DailyEnergyYield | INV019 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV019_Frequency | INV019 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV019_InverterEfficiency | INV019 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV019_InverterRunningStopped | INV019 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV019_PowerFactor | INV019 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV019_ReactivePower | INV019 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV019_TotalEnergyYield | INV019 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV020_ACCurrent | INV020 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV020_ACVoltage | INV020 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV020_ActivePower | INV020 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV020_ApparentPower | INV020 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV020_DCCurrent | INV020 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV020_DCPower | INV020 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV020_DCVoltage | INV020 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV020_DailyEnergyYield | INV020 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV020_Frequency | INV020 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV020_InverterEfficiency | INV020 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV020_InverterRunningStopped | INV020 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV020_PowerFactor | INV020 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV020_ReactivePower | INV020 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV020_TotalEnergyYield | INV020 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV021_ACCurrent | INV021 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV021_ACVoltage | INV021 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV021_ActivePower | INV021 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV021_ApparentPower | INV021 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV021_DCCurrent | INV021 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV021_DCPower | INV021 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV021_DCVoltage | INV021 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV021_DailyEnergyYield | INV021 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV021_Frequency | INV021 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV021_InverterEfficiency | INV021 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV021_InverterRunningStopped | INV021 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV021_PowerFactor | INV021 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV021_ReactivePower | INV021 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV021_TotalEnergyYield | INV021 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV022_ACCurrent | INV022 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV022_ACVoltage | INV022 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV022_ActivePower | INV022 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV022_ApparentPower | INV022 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV022_DCCurrent | INV022 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV022_DCPower | INV022 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV022_DCVoltage | INV022 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV022_DailyEnergyYield | INV022 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV022_Frequency | INV022 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV022_InverterEfficiency | INV022 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV022_InverterRunningStopped | INV022 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV022_PowerFactor | INV022 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV022_ReactivePower | INV022 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV022_TotalEnergyYield | INV022 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV023_ACCurrent | INV023 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV023_ACVoltage | INV023 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV023_ActivePower | INV023 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV023_ApparentPower | INV023 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV023_DCCurrent | INV023 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV023_DCPower | INV023 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV023_DCVoltage | INV023 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV023_DailyEnergyYield | INV023 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV023_Frequency | INV023 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV023_InverterEfficiency | INV023 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV023_InverterRunningStopped | INV023 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV023_PowerFactor | INV023 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV023_ReactivePower | INV023 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV023_TotalEnergyYield | INV023 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV024_ACCurrent | INV024 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV024_ACVoltage | INV024 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV024_ActivePower | INV024 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV024_ApparentPower | INV024 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV024_DCCurrent | INV024 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV024_DCPower | INV024 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV024_DCVoltage | INV024 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV024_DailyEnergyYield | INV024 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV024_Frequency | INV024 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV024_InverterEfficiency | INV024 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV024_InverterRunningStopped | INV024 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV024_PowerFactor | INV024 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV024_ReactivePower | INV024 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV024_TotalEnergyYield | INV024 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV025_ACCurrent | INV025 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV025_ACVoltage | INV025 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV025_ActivePower | INV025 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV025_ApparentPower | INV025 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV025_DCCurrent | INV025 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV025_DCPower | INV025 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV025_DCVoltage | INV025 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV025_DailyEnergyYield | INV025 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV025_Frequency | INV025 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV025_InverterEfficiency | INV025 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV025_InverterRunningStopped | INV025 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV025_PowerFactor | INV025 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV025_ReactivePower | INV025 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV025_TotalEnergyYield | INV025 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV026_ACCurrent | INV026 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV026_ACVoltage | INV026 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV026_ActivePower | INV026 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV026_ApparentPower | INV026 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV026_DCCurrent | INV026 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV026_DCPower | INV026 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV026_DCVoltage | INV026 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV026_DailyEnergyYield | INV026 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV026_Frequency | INV026 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV026_InverterEfficiency | INV026 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV026_InverterRunningStopped | INV026 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV026_PowerFactor | INV026 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV026_ReactivePower | INV026 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV026_TotalEnergyYield | INV026 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV027_ACCurrent | INV027 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV027_ACVoltage | INV027 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV027_ActivePower | INV027 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV027_ApparentPower | INV027 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV027_DCCurrent | INV027 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV027_DCPower | INV027 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV027_DCVoltage | INV027 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV027_DailyEnergyYield | INV027 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV027_Frequency | INV027 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV027_InverterEfficiency | INV027 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV027_InverterRunningStopped | INV027 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV027_PowerFactor | INV027 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV027_ReactivePower | INV027 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV027_TotalEnergyYield | INV027 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV028_ACCurrent | INV028 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV028_ACVoltage | INV028 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV028_ActivePower | INV028 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV028_ApparentPower | INV028 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV028_DCCurrent | INV028 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV028_DCPower | INV028 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV028_DCVoltage | INV028 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV028_DailyEnergyYield | INV028 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV028_Frequency | INV028 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV028_InverterEfficiency | INV028 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV028_InverterRunningStopped | INV028 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV028_PowerFactor | INV028 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV028_ReactivePower | INV028 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV028_TotalEnergyYield | INV028 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV029_ACCurrent | INV029 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV029_ACVoltage | INV029 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV029_ActivePower | INV029 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV029_ApparentPower | INV029 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV029_DCCurrent | INV029 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV029_DCPower | INV029 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV029_DCVoltage | INV029 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV029_DailyEnergyYield | INV029 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV029_Frequency | INV029 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV029_InverterEfficiency | INV029 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV029_InverterRunningStopped | INV029 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV029_PowerFactor | INV029 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV029_ReactivePower | INV029 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV029_TotalEnergyYield | INV029 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV030_ACCurrent | INV030 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV030_ACVoltage | INV030 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV030_ActivePower | INV030 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV030_ApparentPower | INV030 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV030_DCCurrent | INV030 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV030_DCPower | INV030 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV030_DCVoltage | INV030 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV030_DailyEnergyYield | INV030 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV030_Frequency | INV030 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV030_InverterEfficiency | INV030 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV030_InverterRunningStopped | INV030 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV030_PowerFactor | INV030 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV030_ReactivePower | INV030 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV030_TotalEnergyYield | INV030 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV031_ACCurrent | INV031 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV031_ACVoltage | INV031 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV031_ActivePower | INV031 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV031_ApparentPower | INV031 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV031_DCCurrent | INV031 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV031_DCPower | INV031 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV031_DCVoltage | INV031 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV031_DailyEnergyYield | INV031 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV031_Frequency | INV031 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV031_InverterEfficiency | INV031 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV031_InverterRunningStopped | INV031 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV031_PowerFactor | INV031 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV031_ReactivePower | INV031 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV031_TotalEnergyYield | INV031 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV032_ACCurrent | INV032 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV032_ACVoltage | INV032 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV032_ActivePower | INV032 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV032_ApparentPower | INV032 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV032_DCCurrent | INV032 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV032_DCPower | INV032 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV032_DCVoltage | INV032 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV032_DailyEnergyYield | INV032 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV032_Frequency | INV032 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV032_InverterEfficiency | INV032 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV032_InverterRunningStopped | INV032 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV032_PowerFactor | INV032 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV032_ReactivePower | INV032 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV032_TotalEnergyYield | INV032 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV033_ACCurrent | INV033 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV033_ACVoltage | INV033 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV033_ActivePower | INV033 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV033_ApparentPower | INV033 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV033_DCCurrent | INV033 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV033_DCPower | INV033 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV033_DCVoltage | INV033 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV033_DailyEnergyYield | INV033 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV033_Frequency | INV033 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV033_InverterEfficiency | INV033 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV033_InverterRunningStopped | INV033 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV033_PowerFactor | INV033 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV033_ReactivePower | INV033 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV033_TotalEnergyYield | INV033 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV034_ACCurrent | INV034 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV034_ACVoltage | INV034 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV034_ActivePower | INV034 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV034_ApparentPower | INV034 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV034_DCCurrent | INV034 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV034_DCPower | INV034 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV034_DCVoltage | INV034 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV034_DailyEnergyYield | INV034 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV034_Frequency | INV034 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV034_InverterEfficiency | INV034 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV034_InverterRunningStopped | INV034 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV034_PowerFactor | INV034 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV034_ReactivePower | INV034 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV034_TotalEnergyYield | INV034 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV035_ACCurrent | INV035 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV035_ACVoltage | INV035 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV035_ActivePower | INV035 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV035_ApparentPower | INV035 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV035_DCCurrent | INV035 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV035_DCPower | INV035 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV035_DCVoltage | INV035 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV035_DailyEnergyYield | INV035 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV035_Frequency | INV035 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV035_InverterEfficiency | INV035 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV035_InverterRunningStopped | INV035 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV035_PowerFactor | INV035 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV035_ReactivePower | INV035 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV035_TotalEnergyYield | INV035 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV036_ACCurrent | INV036 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV036_ACVoltage | INV036 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV036_ActivePower | INV036 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV036_ApparentPower | INV036 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV036_DCCurrent | INV036 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV036_DCPower | INV036 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV036_DCVoltage | INV036 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV036_DailyEnergyYield | INV036 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV036_Frequency | INV036 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV036_InverterEfficiency | INV036 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV036_InverterRunningStopped | INV036 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV036_PowerFactor | INV036 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV036_ReactivePower | INV036 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV036_TotalEnergyYield | INV036 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV037_ACCurrent | INV037 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV037_ACVoltage | INV037 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV037_ActivePower | INV037 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV037_ApparentPower | INV037 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV037_DCCurrent | INV037 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV037_DCPower | INV037 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV037_DCVoltage | INV037 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV037_DailyEnergyYield | INV037 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV037_Frequency | INV037 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV037_InverterEfficiency | INV037 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV037_InverterRunningStopped | INV037 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV037_PowerFactor | INV037 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV037_ReactivePower | INV037 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV037_TotalEnergyYield | INV037 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV038_ACCurrent | INV038 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV038_ACVoltage | INV038 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV038_ActivePower | INV038 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV038_ApparentPower | INV038 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV038_DCCurrent | INV038 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV038_DCPower | INV038 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV038_DCVoltage | INV038 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV038_DailyEnergyYield | INV038 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV038_Frequency | INV038 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV038_InverterEfficiency | INV038 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV038_InverterRunningStopped | INV038 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV038_PowerFactor | INV038 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV038_ReactivePower | INV038 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV038_TotalEnergyYield | INV038 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV039_ACCurrent | INV039 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV039_ACVoltage | INV039 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV039_ActivePower | INV039 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV039_ApparentPower | INV039 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV039_DCCurrent | INV039 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV039_DCPower | INV039 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV039_DCVoltage | INV039 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV039_DailyEnergyYield | INV039 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV039_Frequency | INV039 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV039_InverterEfficiency | INV039 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV039_InverterRunningStopped | INV039 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV039_PowerFactor | INV039 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV039_ReactivePower | INV039 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV039_TotalEnergyYield | INV039 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV040_ACCurrent | INV040 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV040_ACVoltage | INV040 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV040_ActivePower | INV040 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV040_ApparentPower | INV040 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV040_DCCurrent | INV040 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV040_DCPower | INV040 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV040_DCVoltage | INV040 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV040_DailyEnergyYield | INV040 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV040_Frequency | INV040 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV040_InverterEfficiency | INV040 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV040_InverterRunningStopped | INV040 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV040_PowerFactor | INV040 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV040_ReactivePower | INV040 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV040_TotalEnergyYield | INV040 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV041_ACCurrent | INV041 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV041_ACVoltage | INV041 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV041_ActivePower | INV041 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV041_ApparentPower | INV041 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV041_DCCurrent | INV041 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV041_DCPower | INV041 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV041_DCVoltage | INV041 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV041_DailyEnergyYield | INV041 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV041_Frequency | INV041 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV041_InverterEfficiency | INV041 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV041_InverterRunningStopped | INV041 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV041_PowerFactor | INV041 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV041_ReactivePower | INV041 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV041_TotalEnergyYield | INV041 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV042_ACCurrent | INV042 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV042_ACVoltage | INV042 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV042_ActivePower | INV042 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV042_ApparentPower | INV042 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV042_DCCurrent | INV042 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV042_DCPower | INV042 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV042_DCVoltage | INV042 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV042_DailyEnergyYield | INV042 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV042_Frequency | INV042 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV042_InverterEfficiency | INV042 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV042_InverterRunningStopped | INV042 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV042_PowerFactor | INV042 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV042_ReactivePower | INV042 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV042_TotalEnergyYield | INV042 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV043_ACCurrent | INV043 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV043_ACVoltage | INV043 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV043_ActivePower | INV043 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV043_ApparentPower | INV043 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV043_DCCurrent | INV043 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV043_DCPower | INV043 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV043_DCVoltage | INV043 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV043_DailyEnergyYield | INV043 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV043_Frequency | INV043 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV043_InverterEfficiency | INV043 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV043_InverterRunningStopped | INV043 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV043_PowerFactor | INV043 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV043_ReactivePower | INV043 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV043_TotalEnergyYield | INV043 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV044_ACCurrent | INV044 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV044_ACVoltage | INV044 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV044_ActivePower | INV044 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV044_ApparentPower | INV044 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV044_DCCurrent | INV044 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV044_DCPower | INV044 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV044_DCVoltage | INV044 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV044_DailyEnergyYield | INV044 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV044_Frequency | INV044 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV044_InverterEfficiency | INV044 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV044_InverterRunningStopped | INV044 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV044_PowerFactor | INV044 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV044_ReactivePower | INV044 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV044_TotalEnergyYield | INV044 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV045_ACCurrent | INV045 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV045_ACVoltage | INV045 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV045_ActivePower | INV045 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV045_ApparentPower | INV045 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV045_DCCurrent | INV045 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV045_DCPower | INV045 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV045_DCVoltage | INV045 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV045_DailyEnergyYield | INV045 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV045_Frequency | INV045 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV045_InverterEfficiency | INV045 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV045_InverterRunningStopped | INV045 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV045_PowerFactor | INV045 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV045_ReactivePower | INV045 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV045_TotalEnergyYield | INV045 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV046_ACCurrent | INV046 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV046_ACVoltage | INV046 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV046_ActivePower | INV046 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV046_ApparentPower | INV046 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV046_DCCurrent | INV046 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV046_DCPower | INV046 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV046_DCVoltage | INV046 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV046_DailyEnergyYield | INV046 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV046_Frequency | INV046 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV046_InverterEfficiency | INV046 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV046_InverterRunningStopped | INV046 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV046_PowerFactor | INV046 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV046_ReactivePower | INV046 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV046_TotalEnergyYield | INV046 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV047_ACCurrent | INV047 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV047_ACVoltage | INV047 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV047_ActivePower | INV047 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV047_ApparentPower | INV047 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV047_DCCurrent | INV047 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV047_DCPower | INV047 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV047_DCVoltage | INV047 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV047_DailyEnergyYield | INV047 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV047_Frequency | INV047 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV047_InverterEfficiency | INV047 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV047_InverterRunningStopped | INV047 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV047_PowerFactor | INV047 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV047_ReactivePower | INV047 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV047_TotalEnergyYield | INV047 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV048_ACCurrent | INV048 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV048_ACVoltage | INV048 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV048_ActivePower | INV048 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV048_ApparentPower | INV048 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV048_DCCurrent | INV048 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV048_DCPower | INV048 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV048_DCVoltage | INV048 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV048_DailyEnergyYield | INV048 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV048_Frequency | INV048 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV048_InverterEfficiency | INV048 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV048_InverterRunningStopped | INV048 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV048_PowerFactor | INV048 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV048_ReactivePower | INV048 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV048_TotalEnergyYield | INV048 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV049_ACCurrent | INV049 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV049_ACVoltage | INV049 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV049_ActivePower | INV049 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV049_ApparentPower | INV049 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV049_DCCurrent | INV049 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV049_DCPower | INV049 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV049_DCVoltage | INV049 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV049_DailyEnergyYield | INV049 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV049_Frequency | INV049 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV049_InverterEfficiency | INV049 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV049_InverterRunningStopped | INV049 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV049_PowerFactor | INV049 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV049_ReactivePower | INV049 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV049_TotalEnergyYield | INV049 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV050_ACCurrent | INV050 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV050_ACVoltage | INV050 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV050_ActivePower | INV050 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV050_ApparentPower | INV050 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV050_DCCurrent | INV050 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV050_DCPower | INV050 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV050_DCVoltage | INV050 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV050_DailyEnergyYield | INV050 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV050_Frequency | INV050 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV050_InverterEfficiency | INV050 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV050_InverterRunningStopped | INV050 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV050_PowerFactor | INV050 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV050_ReactivePower | INV050 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV050_TotalEnergyYield | INV050 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV051_ACCurrent | INV051 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV051_ACVoltage | INV051 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV051_ActivePower | INV051 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV051_ApparentPower | INV051 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV051_DCCurrent | INV051 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV051_DCPower | INV051 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV051_DCVoltage | INV051 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV051_DailyEnergyYield | INV051 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV051_Frequency | INV051 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV051_InverterEfficiency | INV051 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV051_InverterRunningStopped | INV051 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV051_PowerFactor | INV051 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV051_ReactivePower | INV051 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV051_TotalEnergyYield | INV051 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV052_ACCurrent | INV052 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV052_ACVoltage | INV052 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV052_ActivePower | INV052 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV052_ApparentPower | INV052 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV052_DCCurrent | INV052 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV052_DCPower | INV052 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV052_DCVoltage | INV052 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV052_DailyEnergyYield | INV052 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV052_Frequency | INV052 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV052_InverterEfficiency | INV052 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV052_InverterRunningStopped | INV052 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV052_PowerFactor | INV052 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV052_ReactivePower | INV052 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV052_TotalEnergyYield | INV052 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV053_ACCurrent | INV053 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV053_ACVoltage | INV053 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV053_ActivePower | INV053 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV053_ApparentPower | INV053 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV053_DCCurrent | INV053 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV053_DCPower | INV053 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV053_DCVoltage | INV053 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV053_DailyEnergyYield | INV053 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV053_Frequency | INV053 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV053_InverterEfficiency | INV053 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV053_InverterRunningStopped | INV053 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV053_PowerFactor | INV053 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV053_ReactivePower | INV053 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV053_TotalEnergyYield | INV053 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV054_ACCurrent | INV054 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV054_ACVoltage | INV054 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV054_ActivePower | INV054 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV054_ApparentPower | INV054 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV054_DCCurrent | INV054 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV054_DCPower | INV054 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV054_DCVoltage | INV054 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV054_DailyEnergyYield | INV054 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV054_Frequency | INV054 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV054_InverterEfficiency | INV054 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV054_InverterRunningStopped | INV054 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV054_PowerFactor | INV054 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV054_ReactivePower | INV054 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV054_TotalEnergyYield | INV054 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV055_ACCurrent | INV055 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV055_ACVoltage | INV055 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV055_ActivePower | INV055 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV055_ApparentPower | INV055 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV055_DCCurrent | INV055 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV055_DCPower | INV055 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV055_DCVoltage | INV055 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV055_DailyEnergyYield | INV055 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV055_Frequency | INV055 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV055_InverterEfficiency | INV055 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV055_InverterRunningStopped | INV055 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV055_PowerFactor | INV055 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV055_ReactivePower | INV055 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV055_TotalEnergyYield | INV055 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV056_ACCurrent | INV056 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV056_ACVoltage | INV056 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV056_ActivePower | INV056 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV056_ApparentPower | INV056 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV056_DCCurrent | INV056 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV056_DCPower | INV056 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV056_DCVoltage | INV056 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV056_DailyEnergyYield | INV056 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV056_Frequency | INV056 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV056_InverterEfficiency | INV056 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV056_InverterRunningStopped | INV056 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV056_PowerFactor | INV056 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV056_ReactivePower | INV056 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV056_TotalEnergyYield | INV056 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV057_ACCurrent | INV057 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV057_ACVoltage | INV057 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV057_ActivePower | INV057 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV057_ApparentPower | INV057 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV057_DCCurrent | INV057 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV057_DCPower | INV057 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV057_DCVoltage | INV057 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV057_DailyEnergyYield | INV057 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV057_Frequency | INV057 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV057_InverterEfficiency | INV057 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV057_InverterRunningStopped | INV057 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV057_PowerFactor | INV057 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV057_ReactivePower | INV057 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV057_TotalEnergyYield | INV057 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV058_ACCurrent | INV058 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV058_ACVoltage | INV058 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV058_ActivePower | INV058 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV058_ApparentPower | INV058 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV058_DCCurrent | INV058 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV058_DCPower | INV058 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV058_DCVoltage | INV058 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV058_DailyEnergyYield | INV058 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV058_Frequency | INV058 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV058_InverterEfficiency | INV058 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV058_InverterRunningStopped | INV058 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV058_PowerFactor | INV058 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV058_ReactivePower | INV058 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV058_TotalEnergyYield | INV058 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV059_ACCurrent | INV059 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV059_ACVoltage | INV059 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV059_ActivePower | INV059 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV059_ApparentPower | INV059 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV059_DCCurrent | INV059 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV059_DCPower | INV059 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV059_DCVoltage | INV059 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV059_DailyEnergyYield | INV059 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV059_Frequency | INV059 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV059_InverterEfficiency | INV059 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV059_InverterRunningStopped | INV059 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV059_PowerFactor | INV059 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV059_ReactivePower | INV059 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV059_TotalEnergyYield | INV059 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV060_ACCurrent | INV060 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV060_ACVoltage | INV060 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV060_ActivePower | INV060 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV060_ApparentPower | INV060 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV060_DCCurrent | INV060 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV060_DCPower | INV060 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV060_DCVoltage | INV060 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV060_DailyEnergyYield | INV060 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV060_Frequency | INV060 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV060_InverterEfficiency | INV060 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV060_InverterRunningStopped | INV060 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV060_PowerFactor | INV060 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV060_ReactivePower | INV060 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV060_TotalEnergyYield | INV060 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV061_ACCurrent | INV061 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV061_ACVoltage | INV061 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV061_ActivePower | INV061 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV061_ApparentPower | INV061 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV061_DCCurrent | INV061 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV061_DCPower | INV061 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV061_DCVoltage | INV061 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV061_DailyEnergyYield | INV061 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV061_Frequency | INV061 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV061_InverterEfficiency | INV061 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV061_InverterRunningStopped | INV061 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV061_PowerFactor | INV061 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV061_ReactivePower | INV061 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV061_TotalEnergyYield | INV061 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV062_ACCurrent | INV062 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV062_ACVoltage | INV062 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV062_ActivePower | INV062 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV062_ApparentPower | INV062 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV062_DCCurrent | INV062 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV062_DCPower | INV062 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV062_DCVoltage | INV062 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV062_DailyEnergyYield | INV062 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV062_Frequency | INV062 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV062_InverterEfficiency | INV062 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV062_InverterRunningStopped | INV062 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV062_PowerFactor | INV062 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV062_ReactivePower | INV062 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV062_TotalEnergyYield | INV062 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV063_ACCurrent | INV063 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV063_ACVoltage | INV063 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV063_ActivePower | INV063 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV063_ApparentPower | INV063 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV063_DCCurrent | INV063 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV063_DCPower | INV063 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV063_DCVoltage | INV063 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV063_DailyEnergyYield | INV063 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV063_Frequency | INV063 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV063_InverterEfficiency | INV063 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV063_InverterRunningStopped | INV063 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV063_PowerFactor | INV063 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV063_ReactivePower | INV063 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV063_TotalEnergyYield | INV063 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV064_ACCurrent | INV064 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV064_ACVoltage | INV064 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV064_ActivePower | INV064 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV064_ApparentPower | INV064 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV064_DCCurrent | INV064 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV064_DCPower | INV064 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV064_DCVoltage | INV064 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV064_DailyEnergyYield | INV064 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV064_Frequency | INV064 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV064_InverterEfficiency | INV064 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV064_InverterRunningStopped | INV064 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV064_PowerFactor | INV064 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV064_ReactivePower | INV064 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV064_TotalEnergyYield | INV064 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV065_ACCurrent | INV065 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV065_ACVoltage | INV065 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV065_ActivePower | INV065 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV065_ApparentPower | INV065 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV065_DCCurrent | INV065 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV065_DCPower | INV065 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV065_DCVoltage | INV065 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV065_DailyEnergyYield | INV065 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV065_Frequency | INV065 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV065_InverterEfficiency | INV065 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV065_InverterRunningStopped | INV065 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV065_PowerFactor | INV065 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV065_ReactivePower | INV065 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV065_TotalEnergyYield | INV065 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV066_ACCurrent | INV066 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV066_ACVoltage | INV066 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV066_ActivePower | INV066 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV066_ApparentPower | INV066 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV066_DCCurrent | INV066 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV066_DCPower | INV066 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV066_DCVoltage | INV066 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV066_DailyEnergyYield | INV066 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV066_Frequency | INV066 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV066_InverterEfficiency | INV066 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV066_InverterRunningStopped | INV066 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV066_PowerFactor | INV066 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV066_ReactivePower | INV066 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV066_TotalEnergyYield | INV066 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV067_ACCurrent | INV067 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV067_ACVoltage | INV067 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV067_ActivePower | INV067 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV067_ApparentPower | INV067 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV067_DCCurrent | INV067 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV067_DCPower | INV067 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV067_DCVoltage | INV067 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV067_DailyEnergyYield | INV067 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV067_Frequency | INV067 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV067_InverterEfficiency | INV067 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV067_InverterRunningStopped | INV067 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV067_PowerFactor | INV067 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV067_ReactivePower | INV067 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV067_TotalEnergyYield | INV067 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV068_ACCurrent | INV068 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV068_ACVoltage | INV068 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV068_ActivePower | INV068 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV068_ApparentPower | INV068 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV068_DCCurrent | INV068 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV068_DCPower | INV068 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV068_DCVoltage | INV068 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV068_DailyEnergyYield | INV068 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV068_Frequency | INV068 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV068_InverterEfficiency | INV068 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV068_InverterRunningStopped | INV068 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV068_PowerFactor | INV068 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV068_ReactivePower | INV068 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV068_TotalEnergyYield | INV068 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV069_ACCurrent | INV069 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV069_ACVoltage | INV069 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV069_ActivePower | INV069 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV069_ApparentPower | INV069 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV069_DCCurrent | INV069 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV069_DCPower | INV069 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV069_DCVoltage | INV069 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV069_DailyEnergyYield | INV069 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV069_Frequency | INV069 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV069_InverterEfficiency | INV069 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV069_InverterRunningStopped | INV069 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV069_PowerFactor | INV069 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV069_ReactivePower | INV069 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV069_TotalEnergyYield | INV069 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV070_ACCurrent | INV070 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV070_ACVoltage | INV070 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV070_ActivePower | INV070 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV070_ApparentPower | INV070 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV070_DCCurrent | INV070 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV070_DCPower | INV070 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV070_DCVoltage | INV070 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV070_DailyEnergyYield | INV070 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV070_Frequency | INV070 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV070_InverterEfficiency | INV070 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV070_InverterRunningStopped | INV070 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV070_PowerFactor | INV070 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV070_ReactivePower | INV070 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV070_TotalEnergyYield | INV070 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV071_ACCurrent | INV071 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV071_ACVoltage | INV071 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV071_ActivePower | INV071 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV071_ApparentPower | INV071 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV071_DCCurrent | INV071 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV071_DCPower | INV071 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV071_DCVoltage | INV071 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV071_DailyEnergyYield | INV071 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV071_Frequency | INV071 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV071_InverterEfficiency | INV071 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV071_InverterRunningStopped | INV071 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV071_PowerFactor | INV071 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV071_ReactivePower | INV071 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV071_TotalEnergyYield | INV071 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV072_ACCurrent | INV072 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV072_ACVoltage | INV072 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV072_ActivePower | INV072 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV072_ApparentPower | INV072 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV072_DCCurrent | INV072 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV072_DCPower | INV072 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV072_DCVoltage | INV072 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV072_DailyEnergyYield | INV072 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV072_Frequency | INV072 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV072_InverterEfficiency | INV072 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV072_InverterRunningStopped | INV072 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV072_PowerFactor | INV072 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV072_ReactivePower | INV072 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV072_TotalEnergyYield | INV072 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV073_ACCurrent | INV073 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV073_ACVoltage | INV073 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV073_ActivePower | INV073 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV073_ApparentPower | INV073 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV073_DCCurrent | INV073 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV073_DCPower | INV073 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV073_DCVoltage | INV073 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV073_DailyEnergyYield | INV073 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV073_Frequency | INV073 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV073_InverterEfficiency | INV073 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV073_InverterRunningStopped | INV073 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV073_PowerFactor | INV073 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV073_ReactivePower | INV073 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV073_TotalEnergyYield | INV073 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV074_ACCurrent | INV074 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV074_ACVoltage | INV074 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV074_ActivePower | INV074 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV074_ApparentPower | INV074 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV074_DCCurrent | INV074 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV074_DCPower | INV074 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV074_DCVoltage | INV074 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV074_DailyEnergyYield | INV074 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV074_Frequency | INV074 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV074_InverterEfficiency | INV074 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV074_InverterRunningStopped | INV074 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV074_PowerFactor | INV074 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV074_ReactivePower | INV074 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV074_TotalEnergyYield | INV074 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV075_ACCurrent | INV075 | Inverter | AC Current (per phase) | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV075_ACVoltage | INV075 | Inverter | AC Voltage (L-L or L-N) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV075_ActivePower | INV075 | Inverter | Active Power (per inverter and total) | Analog | kW | Periodic | 60 s | 0.1 | 1 years
INV075_ApparentPower | INV075 | Inverter | Apparent Power | Analog | kVA | Periodic | 60 s | 0.1 | 1 years
INV075_DCCurrent | INV075 | Inverter | DC Current | Analog | A | Periodic | 60 s | 0.1 | 1 years
INV075_DCPower | INV075 | Inverter | DC Power | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV075_DCVoltage | INV075 | Inverter | DC Voltage ( String Level) | Analog | V | Periodic | 60 s | 0.1 | 1 years
INV075_DailyEnergyYield | INV075 | Inverter | Daily Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
INV075_Frequency | INV075 | Inverter | Frequency | Analog | Hz | Periodic | 60 s | 0.1 | 1 years
INV075_InverterEfficiency | INV075 | Inverter | Inverter Efficiency | Analog | % | Periodic | 60 s | 0.1 | 1 years
INV075_InverterRunningStopped | INV075 | Inverter | Inverter Running / Stopped | Analog |  | Periodic | 60 s | 0.1 | 1 years
INV075_PowerFactor | INV075 | Inverter | Power Factor | Analog | p.u. | Periodic | 60 s | 0.1 | 1 years
INV075_ReactivePower | INV075 | Inverter | Reactive Power | Analog | kvar | Periodic | 60 s | 0.1 | 1 years
INV075_TotalEnergyYield | INV075 | Inverter | Total Energy Yield | Analog | kWh | Periodic | 300 s | 1.0 | 1 years
PLANT_TotalActivePower | PLANT | Plant | Total Active Power | Analog | kW | Periodic | 300 s | 1.0 | 1 years
WS001_AmbientHumidity | WS001 | Weather Station | Ambient Humidity | Analog | % | Periodic | 60 s | 0.1 | 1 years
WS001_AmbientTemperature | WS001 | Weather Station | Ambient temperature | Analog | °C | Periodic | 60 s | 0.1 | 1 years
WS001_CumulativeValueDirectRadiation | WS001 | Weather Station | Cumulative value of direct radiation | Analog | Accumulated | Periodic | 300 s | 1.0 | 1 years
WS001_CumulativeValuePhotosynthetic | WS001 | Weather Station | Cumulative value of photosynthetic | Analog |  | Periodic | 300 s | 1.0 | 1 years
WS001_CumulativeValueScatteredRadiation | WS001 | Weather Station | Cumulative value of scattered radiation | Analog | Accumulated | Periodic | 300 s | 1.0 | 1 years
WS001_CumulativeValueSunshineDuration | WS001 | Weather Station | Cumulative value of sunshine duration | Analog | h | Periodic | 300 s | 1.0 | 1 years
WS001_CumulativeValueTotalRadiation1 | WS001 | Weather Station | Cumulative value of total radiation 1 | Analog | Accumulated | Periodic | 300 s | 1.0 | 1 years
WS001_DailyCumulativeValueDirectRadiation | WS001 | Weather Station | Daily cumulative value of direct radiation | Analog | Accumulated | Periodic | 300 s | 1.0 | 1 years
WS001_DailyCumulativeValueNetRadiation | WS001 | Weather Station | Daily cumulative value of net radiation | Analog | Accumulated | Periodic | 300 s | 1.0 | 1 years
WS001_DailyCumulativeValuePhotosyntheticRadiation | WS001 | Weather Station | Daily cumulative value of photosynthetic radiation | Analog | Accumulated | Periodic | 300 s | 1.0 | 1 years
WS001_DailyCumulativeValueScatteredRadiation | WS001 | Weather Station | Daily cumulative value of scattered radiation | Analog | Accumulated | Periodic | 300 s | 1.0 | 1 years
WS001_DailyCumulativeValueTotalRadiation1 | WS001 | Weather Station | Daily cumulative value of total radiation 1 | Analog | Accumulated | Periodic | 300 s | 1.0 | 1 years
WS001_DailySunshineDuration | WS001 | Weather Station | Daily sunshine duration | Analog | h | Periodic | 300 s | 1.0 | 1 years
WS001_DewPointTemperature | WS001 | Weather Station | Dew-point Temperature | Analog | °C | Periodic | 60 s | 0.1 | 1 years
WS001_InstantaneousValueTotalRadiation1 | WS001 | Weather Station | Instantaneous value of total radiation 1 | Analog | W/m² | Periodic | 300 s | 1.0 | 1 years
WS001_InstantaneousWindDirection | WS001 | Weather Station | Instantaneous wind direction | Analog | deg | Periodic | 60 s | 1 | 1 years
WS001_InstantaneousWindSpeed | WS001 | Weather Station | Instantaneous wind speed | Analog | m/s | Periodic | 60 s | 0.1 | 1 years
WS001_Temperature1 | WS001 | Weather Station | Temperature 1 (Bracket) | Analog | °C | Periodic | 60 s | 0.1 | 1 years
WS001_WindSpeed2Minutes | WS001 | Weather Station | Wind speed in 2 minutes | Analog | m/s | Periodic | 60 s | 0.1 | 1 years