## Change History
SmartLogger IEC104转发协议接口描述
修订记录
日期 | 版本 | 修改描述 | 备注
2014.12.15 | V1.0 | Newly Generated File | c00304059
2014.12.15 | V1.1 | Add the total number of radiation days to the EMI. | c00304059
2014.12.15 | V1.2 | Add the output switch status to the AC combiner box. | c00304059
2014.12.31 | V1.3 | Add the SUN8000 alarm remote communication signal and inverter running status telemetry signal. | c00304059
2015.02.02 | V1.4 | The power-on and power-off commands of the SmartLogger and inverter are combined into one remote signal point. | c00304059
2015.05.12 | V1.5 | Active power percentage and reactive power factor adjustment are added to the SmartLogger remote adjustment. | c00304059
2015.06.19 | V1.6 | Alarms (37 and 38) and inverter status (0700) are added to the 33-40KTL inverter. | c00304059
2015.06.25 | V1.7 | 33-40KTL Inverter Alarm (39) | c00304059
2015.08.15 | V1.8 | Compatible with remote power-on/off sub-register control | c00304059
2015.08.28 | V1.9 | The SmartLogger alarms (10 to 20) are added for 50 KTL models. | c00304059
2015.09.09 | V2.0 | Adding a PID Device | c00304059
2015.09.17 | V2.1 | The DLT615 meter is added. | c00304059
2015.12.03 | V2.3 | The SmartLogger alarm "Device Address Conflict" is added. | c00304059
2015.12.28 | V2.4 | 50KTL Remote Indication Alarm Usage Merges New Alarms | c00304059
2016.01.07 | V2.5 | Four statuses are added to be sent to the inverter through remote communication. | c00304059
2016.03.16 | V2.6 | Remove the combiner box information and restore the old alarm remote communication in 50KTL mode. | c00304059
2016.04.06 | V2.7 | Retain the invalid remote signal and add the description of the inverter status. | c00304059
2016.04.23 | V2.8 | Four new telemetry signals are added to the EMI, and remarks are added. | c00304059
2016.05.17 | V2.9 | Added the SPD fault alarm and eight user-defined alarms to the SmartLogger. Only the SmartLogger V2 supports this function. | c00304059
2016.06.29 | V3.0 | Network-wide power-on and power-off status remote notification is added to the SmartLogger. | c00304059
2016.08.09 | V3.1 | Added the 1500 V inverter model. | c00304059
2016.08.23 | V3.2 | Added the parameters and description of the PID2.0 model. | c00304059
2016.10.18 | V3.3 | The alarm "24 V Power Fault" is added to the SmartLogger. | c00304059
2016.12.08 | V3.4 | Six status remote communication options are added for the V2 inverter, and enumerated values of the inverter running status are deleted. | c00304059
2017.06.15 | V3.5 | Six status remote notification functions are added to the V1 inverter. | c00304059
2017.08.02 | V3.6 | Added information about V3 models. | c00304059
2017.08.14 | V3.7 | Added eight electric energy telemeters for the DLT645 electric meter. | c00304059
2017.11.06 | V3.8 | Added the inverter disclaimer. | c00304059
2017.12.12 | V3.9 | Add 10 customized telemeters for Modbus meters. | c00304059
2018.01.05 | V4.0 | Increase the weekly, monthly, and annual power output at the plant level. Increase the monthly and annual power output of V2 and V3 inverters. | l00323023
2018.03.20 | V4.1 | Added the daily energy yield duration, rated PV array capacity, PV array inverter status (Xinjiang and Ningxia), and power grid line voltage for SmartLogger telemetry. | c00304059
2018.09.25 | V4.2 | Add the forwarding table of Huawei box-type transformer equipment. | c00304059
2018.11.09 | V4.3 | Adding the Subarray Inverter Status for Remote Signaling (Qinghai) | c00304059
2019.01.07 | V4.4 | Change the name of the Note sheet to Change History. Added the description of inverter power models. The forwarding table is differentiated by VRC version. | c00304059
2019.03.27 | V4.5 | The remote communication alarm is added for the PV-12/PV-18 model. Added the description of the forwarding table of three Huawei box-type transformer models. Add the forwarding table of the PV-20. The license expiration alarm is added. | c00304059
2019.04.28 | V4.6 | Added telemetry for PV-12/PV-18/PV-20: inverter running status (Tianjin) | c00304059
2020.12.29 | V4.7 | Added the function of adjusting the status of the SmartLogger. | l00323023
2021.1.15 | V4.8 | 1. Modify the existing signal names of the SmartLogger as follows: · Total DC input current ==> PV DC current · Total DC input power ==> PV input power · Total output active power = > Active power · Total output reactive power = > reactive power · Total C02 emission reduction ==> C02 emission reduction · Power grid BC line voltage = > Power grid CA line voltage · Rated subarray capacity = > Rated subarray power · Daily energy yield, weekly energy yield, monthly energy yield, annual energy yield, and daily energy yield duration = > Daily energy yield, weekly energy yield, monthly energy yield, annual energy yield, and daily energy yield 2. Add energy storage-related signals, including: 2.1 SmartLogger telemetry: charge cut-off SOC, discharge cut-off SOC, discharge upper limit, charge upper limit, SOC, maximum charge power, maximum discharge power, accumulated charge power, accumulated discharge power, charge power of the day, and discharge power of the day 1. Rechargeable power, dischargeable power, absorbed power of the day, accumulated absorbed power, maximum power charging available time, maximum power discharging available time, rated capacity of energy storage, and number of PCS; 2.2 SmartLogger remote communication: battery charging, battery discharging, battery shutdown, battery standby, battery fault, array fault flag, and array exception flag; 2.3 CMU telemetry: DC side bus voltage, DC side bus current, rated capacity, rated power. 3. Deleted the following invalid signals from the CMU: average temperature in the battery compartment and average humidity in the battery compartment. | j00335310
2022.2.21 | V4.9 | Updated the BCU remote communication list and ESS alarm names. (For details, see the Modbus Standard Interfaces for Connecting Huawei Devices to Huawei Energy Storage Devices.xlsx.) | j00335310
2022.3.24 | V5.0 | To eliminate ambiguity, the SmartLogger telemetry signal generation duration of the current day is renamed PV generation duration of the current day. | j00335310
2022.3.31 | V5.1 | Added SmartLogger telemetry signals for Hainan Wenchang energy storage project: number of available PCS. SmartLogger teleindication signal: energy storage charge lockout and energy storage discharge lockout. The telemetry reserved signal (14) of the PCS is changed to DC side total power. | j00335310
2022.3.31 | V5.2 | 1. Added SmartLogger telemetry signals: PV active power, PV reactive power, energy storage active power, energy storage reactive power, PV rated power, energy storage rated power, maximum value of energy storage reactive power adjustment, and minimum value of energy storage reactive power adjustment. 1. The PV array is in the black start state. 2. Added the SmartLogger remote control signals: PV power-off, PV power-on, energy storage power-off, and energy storage power-on. 3. Added the SmartLogger remote adjustment signals: VSG synchronous control voltage adjustment, VSG synchronous control frequency adjustment, PV array black start, PV active power fixed value adjustment, PV active power percentage adjustment, energy storage active power fixed value adjustment, and storage. Active power percentage adjustment, fixed value adjustment of PV reactive power, fixed value adjustment of energy storage reactive power, and PCS working mode. 4. Added the SUN2000 PV-28 sheet for the 23 A HAV5 inverter. 5. The Huawei STS-9000K tab page is added for the 23A self-developed STS box-type transformer. 6. The remote communication signal is added to the PCS: off-grid operation. 7. The remote signal of the CMU is changed, 7.1 Modify the existing teleindication signals (No. 1 - 4 and No. 7 - 24) to be consistent with the CMU. 7.2 Added missing CMU alarm signals (No. 26 to No. 69). 7.3 Added the communication fault signal between the SmartLogger and CMU. 8. BCU remote signal supplementation: battery module auxiliary source fault, ESS version inconsistency, ESS version inconsistency, ESS version inconsistency, ESS version inconsistency, cluster controller external DC auxiliary source fault, cluster controller external fan fault, cluster controller temperature detection exception, and battery module Optimization unit undertemperature, EPO emergency shutdown, version inconsistency between the cluster controller and battery module, version inconsistency between the cluster controller and battery module, communication disconnection between the cluster controller and PCS, and communication failure between the BCU and SmartLogger. 9. The teleadjusting signals are added to BCU: cluster system 1 - charging cut-off SOC, cluster system 1 - discharging cut-off SOC, cluster system 2 - charging cut-off SOC, and cluster system 2 - discharging cut-off SOC." | j00335310
2022.4.11 | V5.3 | 1. The PV array capability is reported, including the SOH, SOE, and rated Ah battery capacity of the battery. | j00335310
2022.5.30 | V5.4 | Auxiliary meter signals are added to the CMU: auxiliary meter phase A voltage, auxiliary meter phase B voltage, auxiliary meter phase C voltage, auxiliary meter phase A active power, auxiliary meter phase B active power, auxiliary meter phase C active power, and auxiliary Active power of the meter, reactive power of the auxiliary meter, power factor of the auxiliary meter, and total active power of the auxiliary meter | j00335310
2022.6.15 | V5.5 | 1. Divide the signals of the PCS, CMU, and BCU based on the commercial storage container and industrial and commercial energy storage cabinet. 2. Changed the "fire extinguishing system" of the CMU to "fire suppression system" based on the 21B CCB decision. 3. Added the enumerated definitions of CMU and BCU statuses. 4. Change "battery compartment" to "energy storage compartment" and "power distribution compartment" to "integrated control compartment" based on the names of telemetry signals on the CMU. | j00335310
2022.7.20 | V5.6 | 根据STS Modbus信号刷新STS-3000K-H1、STS-6000K-H1和STS-9000K-H0的104信号，具体为， 1. 增加STS-3000K-H1遥测信号免维护吸湿器湿度等，序号从60到81； 2. 增加STS-3000K-H1遥信信号免维护吸湿器故障等，序号从66到96； 3. STS-3000K-H1原遥信信号EPO操作更名为EPO急停按钮操作； 4. STS-6000K-H1的改动点同STS-3000K-H1； 5. STS-9000K-H0型号更名为JUPITER-9000K-H0，其中压侧电压Ua、变压器中压侧电压Ub和变压器中压侧电压Uc三个遥测信号改成变压器中压侧电压Uab、变压器中压侧电压Ubc和变压器中压侧电压Uca。 | j00335310
2022.9.1 | V5.7 | 1. To facilitate the controller to obtain the array control capability, the following SmartLogger telemetry signals are added: lower limit of active power adjustment, maximum value of active power adjustment, maximum value of reactive power adjustment, and minimum value of reactive power adjustment. | j00335310
2022.9.19 | V5.8 | Added the interface for reporting the subarray adjustment capability: Added telemetry points 63 to 66 on the SmartLogger. | j00335310
2022.12.13 | V5.9 | 1. Break down the SmartLogger based on the optical, storage, and optical storage scenarios. 2. Added the 14-channel PV inverter model and the corresponding signal table. | j00335310
2022.12.22 | V6.0 | 1. Provide remarks and precision information for SmartLogger signals. 2. Added two signals: "Maximum charging power in steady state" and "Maximum discharging power in steady state". | j00335310
2023.01.06 | V6.1 | 1. Changed the name of the PID remote communication alarm "AC-to-ground Impedance Abnormal" to "System-to-ground Impedance Abnormal". 2. Two PID remote signal signals are added: System Ground Impedance Abnormal Warning and License Expired. | j00335310
2023.01.11 | V6.2 | 1. The PCS does not have inverter efficiency-related signals and is reserved. 2. Modified the description of the SmartLogger. 3. Changed the name of the temperature and humidity signal for the energy storage compartment of the CMU. 4. The BCU is changed to ESC, which is consistent with the customer interface. 5. Optimize the data based on the feedback from external projects and supplement the data scope. | j00335310
2023.01.29 | V6.3 | 1. Deleted the alarm "Leakage Current Abnormal" of the original PID telesignal. 2. Added the following self-developed box-type transformer models: JUPITER-3000K-H1, JUPITER-6000K-H1, and JUPITER-9000K-H1. JUPITER-6000K-H1 and JUPITER-9000K-H1 use the same point table. 3. Added the single-level inverter model and corresponding points. 4. Modified the description of the value range of signals related to power scheduling. 5. Added the list of medium- and three-phase SUN2000 PV-8 models. 6. Added PCS remote signal "Parallel communication abnormal", "Local access certificate not valid", "Local access certificate is about to expire", "Local access certificate has expired", "Inverted phase sequence on the AC side", and "String short circuit to ground". Communication link failure protection, AC terminal temperature exception, DC terminal temperature exception, black start failure, black start command sequence exception, PCS parallel CAN communication disconnection, and DC input exception. 7. Supplement the PCS working mode telemetry signals of the subarray and PCS. | j00335310
2023.05.25 | V6.4 | Added the following information in the SmartLogger-Optical Storage Scenario: 1. Remote control signal 8: The PCS of the PV array is shut down. 2. Remote control signal 9: The PCS of the PV array is started. 3. Remote adjustment signal 15: microgrid adaptability of PV inverters in subarrays | z00559171
2023.05.25 | V6.5 | Deleted 44-Low-voltage cabinet A IMD warning and 46-Low-voltage cabinet B IMD warning in JUPITER-9000K-H0/JUPITER-9000K(6000K)-H1. | z00559171
2023.08.16 | V6.6 | Updated the new teleindication signals of the 24A STS, modified the names of some telemetry devices, and added JUPITER-3000K-H1-AC(GF), JUPITER-6000K-H1-AC, and JUPITER-9000K (4000K, 6000K)-H1. | c00815720
2023.09.06 | V6.7 | PV plant C93: new PV array high and low pass-through settings and PV inverter status (Hubei) | c00815720
2023.09.11 | V6.8 | The grid-tied switch status is added to the remote adjustment signal in the 24 A power plant and optical storage and pure storage scenarios. | d00838062
2023.09.13 | V6.9 | 1. The power plant is 24 A. In the optical storage scenario and pure storage scenario, the remote adjustment signal is added. The actual SOC of the PV array is added. 2. The description "Charging cut-off SOC and discharging cut-off SOC take effect only in grid-tied operation" is added to ESC. | z00559171
2023.10.08 | V7.0 | 1. The following telemetry signals are added for the 24 A power plant in the optical storage scenario and pure storage scenario: steady-state chargeable battery capacity and steady-state discharge capacity of the battery cluster in the battery array 2. The name of the subarray SOC signal is changed to the real-time subarray SOC, and the name of the actual subarray SOC signal is changed to the steady-state subarray SOC. 3. The rechargeable battery capacity of the subarray battery cluster is renamed as the real-time rechargeable battery capacity of the subarray battery cluster, and the dischargeable battery capacity of the subarray battery cluster is renamed as the real-time dischargeable battery capacity of the subarray battery cluster. 4. Add a note to the above signal to explain the calculation logic 5. Add PV inverter status (Tianjin) | c00815720
2023.10.12 | V7.1 | The remote control signal is added: illumination estimation of the subarray. Telemetry signal: estimated illumination status and estimated active power of subarray illumination | j00448282
2023.10.19 | V7.2 | 1. In the optical storage scenario and pure storage scenario, the control signal is added: one-click black start of the PV array. 2. In the optical storage scenario and pure storage scenario, the PV array black start is renamed the PV array black start. | d00838062
2023.10.23 | V7.3 | Added SUN2000_200KTL_H4 and SUN2000_125KTL_NHM0 to the device model description. | z00559171
2023.11.06 | V7.4 | "New 1. In the optical storage scenario and pure storage scenario, the subarray charging cutoff SOC and subarray discharging cutoff SOC are added. | z00559171
2023.11.06 | V7.4 | Add 1. In the optical storage scenario and pure storage scenario, the subarray charge cut-off SOC and subarray discharge cut-off SOC are added. | d00838062
2023.12.22 | V7.5 | Add 1. Optical storage scenario and pure storage scenario: The subarray PCS microgrid adaptability and subarray PCS microgrid adaptability triggering status are added. 2. Working mode and microgrid adaptation triggering status of PV inverters in PV storage and pure solar scenarios 3. Optical storage and pure storage scenarios: new Charged battery capacity of the subarray in the current month Discharge capacity of subarray batteries in the current month Charging capacity of subarray energy storage batteries in the current year Discharge capacity of energy storage batteries in subarrays in the current year Total power absorbed by the PCS of the subarray in the current month Total power absorbed by the PCS of the subarray in the current year Total power discharged by the PCS of the PV array on the current day Total power released by the PCS of the PV array in the current month Total power released by the PCS of the PV array in the current year Total power discharged by the PCS of the subarray | d00838062
2023.12.22 | V7.6 | Updated the following information in the pure storage scenario: 1. Remote control signal 8: The PCS of the PV array is shut down. 2. Remote control signal 9: The subarray energy storage PCS is started. | d00838062
2023.12.25 | V7.7 | Deleted the CO2 emission reduction of the telemetry signal array in the SmartLogger-optical storage and SmartLogger-pure storage scenarios. | z00559171
2024.02.22 | V7.8 | Added the ESS (Industrial and Commercial N+1 Generation Energy Storage Cabinet) sheet. | j00448282
2024.03.06 | V7.9 | ESS (industrial and commercial N+1 generation energy storage cabinet) 1. The following information is added: 1 communication failure, 2 standby, 3 running, 4 shutdown, 5 spot check, 6 reserved, 7 normal operation, 8 power limit and derating, 9 self-derating, 10 locked, 11 hot backup, 12 reserved, 13 normal shutdown, 14 Abnormal shutdown, 15 Power-limited shutdown, 16 Reserved 2. The original remote signal serial number increases from 17. 3. Added remote control: 3. Power-on/power-off control | j00448282
2024.03.07 | V8.0 | Add 1. In the pure storage scenario, a control signal is added to allow co-control. | z00829955
2024.03.22 | V8.1 | Add 1. The PCS (Plant N+1 Energy Storage) sheet is added. | d00838062
2024.04.01 | V8.2 | Add 1. The SUN2000 PV-21 tab page is added. 2. On the General Description tab page, the description about the use of public addresses is added. | d00838062
2024.04.15 | V8.3 | "New Active power of the PV array (fast) Subarray PV inverter active power (fast) Total active power of subarray energy storage PCS (fast)" | d00838062
2024.04.23 | V8.4 | The N+1 PCS tab page of the PV plant is modified, and the power-on and power-off status signal point is changed to reserved. | d00838062
2024.05.27 | V8.5 | Remote communication is added to the ESS (industrial and commercial N+1 generation energy storage cabinet): 1. The power frequency is abnormal. 2. The outdoor low temperature alarm is generated. 3. The liquid cooling unit expires. 4. The certificate is about to expire. 5. The certificate has expired. 6. The condenser outlet pressure sensor is faulty. 7. The condenser outlet temperature sensor is faulty. 8. The dehumidification temperature sensor is faulty. 9. The outdoor heat exchanger temperature sensor is faulty. 10. The fan is faulty. 11. The battery pack is faulty. Power supply failure12. RPCB fan alarm13. ISO insulation detection alarm on the battery side14. Inconsistency of software versions of cluster components15. Inconsistency of software versions of equalization modules16. Inconsistency between cluster device access and configuration17. Abnormal battery sampling18. Overtemperature of battery passive equalization resistor19. Battery voltage consistency Large deviation 20; Large deviation of battery temperature consistency 21; DCDC module short circuit protection 22; DCDC module bus overvoltage fault 23; PCS DC bus short circuit | z00635737
2024.06.20 | V8.6 | Modified the N+1 CMU and BCUTab sheets of the plant. | d00838062
2024.06.29 | V8.7 | Modified the content and description of the 104 information table of the N+1 CMU and BCU in the plant based on the latest energy storage point table. | d00838062
2024.07.22 | V8.8 | The status of Sichuan province adjustment is added to the SmartLogger. | c00815720
2024.07.29 | V8.9 | Modified the meanings of the remote control point table in the SmartLogger-only optical storage, pure storage, and optical storage scenarios. Changed the value 0 to both 0 and 1 for power-on and power-off. | d00838062
2024.08.12 | V9.0 | The running status of cold backup is added to the PCS (commercial storage container and industrial and commercial energy storage cabinet). | d00838062

## General Description
1. Payload Base Address Range
Category | Base Address | Specifications | ASDU ID
Teleindication | 0001H--2000H | 8192 | <1>: = Single point information
Telemetry | 4001H--6000H | 8192 | <13>: = Measurement value, short floating point number
Telecontrol | 6001H--6200H | 512 | <45>: = Single point command <46>: = Double point command
Teleadjust | 6201H--6400H | 512 | <50>: = Set-point value command, short floating point number
2. Configuration of the Number of Bytes
Category | Configuration Mode
Number of bytes for the public address | 2
Number of bytes for the transmission cause | 2
Number of bytes for the payload address | 3
3. Forwarding Device Configuration (Example)
Device Name | Slave Device Address | Teleindication Signal No. (1~8192) |  | Telemetry Signal No. (1~8192) |  | Telecontrol Signal No. (1~512) |  | Teleadjust Signal No. (1~512)
|  | Start | End | Start | End | Start | End | Start | End
Logger | 0 | 1 | 50 | 1 | 50 | 1 | 10 | 1 | 10
SUN2000 (1-1) connected | 1 | 51 | 100 | 51 | 100 | 11 | 15 | 11 | 15
SUN2000 (1-2) connected | 2 | 101 | 150 | 101 | 150 | 16 | 20 | 16 | 20
SUN2000 (1-3) connected | 3 | 151 | 200 | 151 | 200 | 21 | 25 | 21 | 25
SUN2000 (1-4) new | 4 | 201 | 250 | 201 | 250 | 26 | 30 | 26 | 30
SUN2000 (1-5) new | 5 | 251 | 300 | 251 | 300 | 31 | 35 | 31 | 35
Customized device 1 (1–6) new | 6 | 301 | 350 | 301 | 350 | 36 | 40 | 36 | 40
4. Configuration Table Description
1. Configure the preceding parameters under Transfer table configuration of the SmartLogger WebUI. Configure the signal address ranges of telemetry, teleindication, telecontrol, and teleadjust of each forwarding device in the IEC104 forwarding queue. For description about each signal address allocated to each device, see the appropriate device sheet. Data of Huawei devices and supported devices such as power meters and environmental monitoring instruments (EMIs) are all provided in this document. If a third-party device connects to the SmartLogger as a customized device, the site technical support configures the signal addresses. 2. If you do not configure signal addresses, only the data of the Logger array is forwarded by default. The teleindication signal address number ranges from 1 to 50, the telemetry address number ranges from 1 to 50, the telecontrol signal address number ranges from 1 to 10, and the teleadjust signal address number ranges from 1 to 10. All the parameters of other devices are 0–0 by default. 3. If you use the default configuration, signal addresses are automatically allocated based on the slave device addresses. By default, the signal address number ranges of the Logger are the same as what described in item 2, and for other devices, the teleindication signal address number ranges from 1 to 50, the telemetry address number ranges from 1 to 50, the telecontrol signal address number ranges from 1 to 5, and the teleadjust signal address number ranges from 1 to 5. 4. Signal Address Calculation Method Teleindication: (0x0001 – 1) + (Start teleindication signal address – 1) + Teleindication No. Telemetry: (0x4001 – 1) + (Start telemetry signal address – 1) + Telemetry No. Telecontrol: (0x6001 – 1) + (Start telecontrol signal address – 1) + Telecontrol No. Teleadjust: (0x6201 – 1) + (Start teleadjust signal address – 1) + Teleadjust No. 5. A telecontrol command must be preset first, and then executed. 6. If the number of teleindication or telemetry information points exceeds 50, you need to modify the default teleindication segment or telemetry segment if you want to use the default configuration of the SmartLogger to set the forwarding table. Enables the default range of teleindication or telemetry to include the number of teleindication or telemetry information points of the equipment. 7. The SmartLogger supports a maximum of 8192 teleindication points and 8192 telemetry points. If the total number of teleindication or telemetry points of all devices exceeds 8192, you need to manually reduce the number of points on some or all devices to ensure that the total number is less than or equal to 8192. 8. When the teleindication is Grid-tied, if the inverter is in Inspecting... or I-V scanning... state, the response time for receiving power grid scheduling will be delayed compared with that in normal grid-tied state. 9.The public address in the northbound IEC104 packet must be the same as the configured value. Broadcast 65535 is not supported.

## SUN2000 PV-8
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | Inverter startup/shutdown status | 0: Shutdown 1: Startup | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | High string input voltage | 0: Normal 1: Faulty
5 | PV5 voltage | V | 5 | DC Arc Fault | 0: Normal 1: Faulty
6 | PV6 voltage | V | 6 | String Reverse Connection | 0: Normal 1: Faulty
7 | PV7 voltage | V | 7 | String current backfeed | 0: Normal 1: Faulty
8 | PV8 voltage | V | 8 | Abnormal String Power | 0: Normal 1: Faulty
9 | PV1 current | A | 9 | AFCI Self-Check Failure | 0: Normal 1: Faulty
10 | PV2 current | A | 10 | Phase Wire Short-Circuited to PE | 0: Normal 1: Faulty
11 | PV3 current | A | 11 | Grid Loss | 0: Normal 1: Faulty
12 | PV4 current | A | 12 | Grid Undervoltage | 0: Normal 1: Faulty
13 | PV5 current | A | 13 | Grid Overvoltage | 0: Normal 1: Faulty
14 | PV6 current | A | 14 | Grid Voltage Imbalance | 0: Normal 1: Faulty
15 | PV7 current | A | 15 | Grid Overfrequency | 0: Normal 1: Faulty
16 | PV8 current | A | 16 | Grid Underfrequency | 0: Normal 1: Faulty
17 | AB Line voltage | V | 17 | Unstable Grid Frequency | 0: Normal 1: Faulty
18 | BC Line voltage | V | 18 | Output Overcurrent | 0: Normal 1: Faulty
19 | CA Line voltage | V | 19 | Output DC Component Overhigh | 0: Normal 1: Faulty
20 | Phase A voltage | V | 20 | Abnormal Residual Current | 0: Normal 1: Faulty
21 | Phase B voltage | V | 21 | Abnormal Grounding | 0: Normal 1: Faulty
22 | Phase C voltage | V | 22 | Low Insulation Resistance | 0: Normal 1: Faulty
23 | Phase A current | A | 23 | Cabinet Overtemperature | 0: Normal 1: Faulty
24 | Phase B current | A | 24 | Device Fault | 0: Normal 1: Faulty
25 | Phase C current | A | 25 | Upgrade Failed | 0: Normal 1: Faulty
26 | Grid frequency | Hz | 26 | License Expired | 0: Normal 1: Faulty
27 | Active power | kW | 27 | Faulty Monitoring Unit | 0: Normal 1: Faulty
28 | Reactive power | kVar | 28 | Faulty Power Collector | 0: Normal 1: Faulty
29 | Power factor | / | 29 | ESS Abnormal | 0: No error 1: Error
30 | Total input power | kW | 30 | Active Islanding | 0: Normal 1: Faulty
31 | Cabinet temperature | ℃ | 31 | Passive Islanding | 0: Normal 1: Faulty
32 | Inverter efficiency | % | 32 | Transient AC Overvoltage | 0: Normal 1: Faulty
33 | Daily energy yield | kWh | 33 | Peripheral port short circuit | 0: Normal 1: Faulty
34 | Total energy yield | kWh | 34 | Off-grid output overload | 0: Normal 1: Faulty
35 | Reduced CO2 emission | kg | 35 | Abnormal PV module configuration | 0: Normal 1: Faulty
36 | Inverter Operating Status | / | 36 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
37 | Startup time | / | 37 | On-grid
38 | Shutdown time | / | 38 | Normal grid connection
39 | Monthly energy yield | kWh | 39 | Grid connection with derating due to power rationing
40 | Yearly energy yield | kWh | 40 | Grid connection with derating due to inverter internal causes
41 | Inverter Operating Status (Tianjin, China) | / | 41 | Normal shutdown
42 | Reserved | / | 42 | Faulty
43 | Reserved | / | 43 | Shutdown due to power rationing
44 | Reserved | / | 44 | Shutdown
45 | Reserved | / | 45 | Spot-check
46 | Reserved | / | 46 | Optimizer fault | 0: Normal 1: Faulty
47 | Reserved | / | 47 | Built-in PID operation abnormal | 0: Normal 1: Faulty
48 | Reserved | / | 48 | High input string voltage to ground | 0: Normal 1: Faulty
49 | Inverter running status (Hubei) | / | 49 | External fan abnormal | 0: Normal 1: Faulty | <-Note: | Inverter running status (Tianjin)
|  |  | 50 | Battery Reverse Connection | 0: No error 1: Error |  | 0: Grid-tied
|  |  | 51 | Grid-tied/Off-grid controller abnormal | 0: Normal 1: Faulty |  | 1: Standby
|  |  | 52 | PV String Loss | 0: Normal 1: Faulty |  | 2: Power limiting
|  |  | 53 | Reserved | 0: Normal 1: Faulty |  | 3: Shut down (including shutdown due to faults)
|  |  | 54 | Reserved | 0: Normal 1: Faulty
|  |  | 55 | Reserved | 0: Normal 1: Faulty
|  |  | 56 | Reserved | 0: Normal 1: Faulty
|  |  | 57 | Reserved | 0: Normal 1: Faulty
|  |  | 58 | Reserved | 0: Normal 1: Faulty
|  |  | 59 | Reserved | 0: Normal 1: Faulty
|  |  | 60 | Reserved | 0: Normal 1: Faulty
|  |  | 61 | Reserved | 0: Normal 1: Faulty
|  |  | 62 | Reserved | /
|  |  | 63 | Reserved | /
|  |  | 64 | Reserved | /
|  |  | 65 | Reserved | /
|  |  | 66 | Reserved | /
|  |  | 67 | Reserved | /
|  |  | 68 | Reserved | /
|  |  | 69 | Reserved | /
|  |  | 70 | Reserved | /
|  |  | 71 | Reserved | /
|  |  | 72 | Reserved | /
|  |  | 73 | Reserved | /
|  |  | 74 | Reserved | /
|  |  | 75 | Reserved | /
|  |  | 76 | Reserved | /
|  |  | 77 | Reserved | /
|  |  | 78 | Reserved | /
|  |  | 79 | Reserved | /
|  |  | 80 | Reserved | /
|  |  | 81 | Reserved | /
|  |  | 82 | Reserved | /
|  |  | 83 | Reserved | /
|  |  | 84 | Indicates the enabling status of the high voltage ride through function. | 0: disabled; 1: enabled
|  |  | 85 | Indicates the enabling status of the bottom pressure traversal function. | 0: disabled; 1: enabled

## Devices Type Description
SmartLogger | SUN2000 V100R001CXX | SUN2000 V200R001CXX | SUN2000 V200R002C00 | SUN2000 V200R002C20 | SUN2000HA V100R001CXX | SUN2000 PV-8 | SUN2000 PV-12 | SUN2000 PV-14 | SUN2000 PV-18 | SUN2000 PV-20 | SUN2000 PV-21 | SUN2000 PV-28 | SUN8000 V100R001C00 | SUN2000HB Series | PCS | BCU | CMU
SmartLogger3000 | SUN2000-20KTL | SUN2000-33KTL | SUN2000-50KTL-C1 | SUN2000-40KTL-US | SUN2000-60KTL-HV-D1 | SUN2000-15KTL-M3 | SUN2000-70KTL-C1 | SUN2000-196KTL-H3 | SUN2000-175KTL-H0 | SUN2000-100KTL-M0 | SUN2000-150K-MG0-ZH | SUN2000-300KTL-H0 | SUN8000-500KTL | SUN2000-250KTL-H0 | LUNA2000-200KTL-H0 | ESC360KW-F | LUNA2000-2.0MWH-1H0
| SUN2000-17KTL | SUN2000-40KTL | SUN2000-42KTL | SUN2000-33KTL-US | SUN2000-45KTL-US-HV-D0 | SUN2000-17KTL-M3 | SUN2000-65KTL-M0 | SUN2000-200KTL-H3 | SUN2000-185KTL-INH0 | SUN2000-100KTL-M1 |  | SUN2000-280KTL-H0 |  | SUN2000-286KTL-H0 | LUNA2000-100KTL-M0 |  | LUNA2000-2.0MWH-2H0
| SUN2000-15KTL | SUN2000-25KTL-US | SUN2000-36KTL | SUN2000-36KTL-US | SUN2000-55KTL-HV-D1 | SUN2000-20KTL-M3 | SUN2000-70KTL-INM0 | SUN2000-215KTL-H3 | SUN2000-168KTL-H1 | SUN2000-100KTL-INM0 |  |  |  | SUN2000-125KTL-M5 | LUNA2000-200KTL-H1
| SUN2000-12KTL | SUN2000-30KTL-US | SUN2000-33KTL-JP |  | SUN2000-55KTL-IN-HV-D1 | SUN2000-23KTL-M3 | SUN2000-50KTL-M0 |  | SUN2000-185KTL-H1 | SUN2000-110KTL-M0 |  |  |  | SUN2000-62.5KTL-NHM0 | LUNA2000-100KTL-NHH1
| SUN2000-10KTL | SUN2000-30KTL-A | SUN2000-40KTL-JP |  | SUN2000-55KTL-HV-D1-001 | SUN2000-24.5KTL-M3 | SUN2000-63KTL-JPM0 |  | SUN2000-193KTL-H0 | SUN2000-125KTL-M0 |  |  |  | SUN2000_200KTL_H4 | LUNA2000-100KTL-M1
| SUN2000-8KTL | SUN2000-22KTL-US | SUN2000-50KTL |  | SUN2000-60KTL-HV-D1-001 | SUN2000-25KTL-NAM3 | SUN2000-50KTL-JPM0 |  | SUN2000-196KTL-H0 | SUN2000-111KTL-NHM0 |  |  |  | SUN2000_125KTL_NHM0
| SUN2000-24.5KTL | SUN2000-33KTL-E001 | SUN2000-43KTL-IN-C1 |  |  | SUN2000-28KTL-M3 | SUN2000-65KTL-C1 |  | SUN2000-196KTL-H1 | SUN2000-75KTL-M1
| SUN2000-23KTL |  | SUN2000-24.7KTL-JP |  |  | SUN2000-29.9KTL-M3 | SUN2000-60KTL-M0 |  | SUN2000-200KTL-H2 | SUN2000-110KTL-M2
| SUN2000-28KTL |  | SUN2000-33KTL-A |  |  | SUN2000-30KTL-M3 | SUN2000-75KTL-C1 |  | SUN2000-215KTL-H0 | SUN2000-125KTL-M2
|  |  | SUN2000-29.9KTL |  |  | SUN2000-36KTL-M3 | SUN2000-70KTL-INM1 |  | SUN2000-125KTL-JPH0 | SUN2000-100KTL-M2
[6 empty] | SUN2000-40KTL-M3 | SUN2000-65KTL-M1 |  | SUN2000-125KTL-JPH1 | SUN2000-111KTL-NHM2
[6 empty] | SUN2000-42KTL-M3 | SUN2000-50KTL-JPM1
[6 empty] | SUN2000-44KTL-M3 | SUN2000-100KTL-USH0
[6 empty] | SUN2000-50KTL-M3 | SUN2000-100KTL-H1
[6 empty] | SUN2000-30KTL-NAM3 | SUN2000-100KTL-H0
[6 empty] | SUN2000-33KTL-NAM3 | SUN2000-90KTL-H1
[6 empty] | SUN2000-36KTL-NAM3 | SUN2000-95KTL-INH0
[6 empty] | SUN2000-40KTL-NAM3 | SUN2000-90KTL-H0
[6 empty] | SUN2000-43KTL-INM3 | SUN2000-63KTL-JPH0
[6 empty] | SUN2000-33KTL-NHM3 | SUN2000-105KTL-H0
[6 empty] | SUN2000-40KTL-NHM3 | SUN2000-100KTL-H2
[6 empty] | SUN2000-20KTL-M3 | SUN2000-105KTL-H1
[6 empty] | SUN2000-29.9KTL-M3 | SUN2000-105KTL-USH0
[6 empty] | SUN2000-30KTL-M3 | SUN2000-90KTL-H2
[6 empty] | SUN2000-36KTL-M3 | SUN2000-95KTL-INH1
SUN2000-36KTL-M3
SUN2000-30KTL-M3
SUN2000-50KTL-ZHM3
SUN2000-50KTL-NHM3
Note: The first line is the label name, and the following is the SmartLogger or inverter model. Find the corresponding label based on the inverter model and click to view the forwarding content. | [14 empty] | Update Date: 2022.03.27

## SmartLogger-PVESS
Telemetry | [5 empty] | Teleindication |  |  |  | Telecontrol |  |  |  | Teleadjust
No. | Signal Name | Unit | Precision | Range | Remarks | No. | Signal Name | Status | Remarks | No. | Signal Name | Command | Remarks | No. | Signal Name | Unit | Precision | Range | Remarks
1 | Total PV DC current | A | 0.1 | [-3.4E+38, 3.4E+38] | Total input current from PV modules (string 1.0) and MPPT combiner boxes (string 2.0) on the DC side of PV inverters in the array. | 1 | Array locking status | 0: Locked 1: Unlocked | If all inverters/PCSs in the array are locked, the array status is locked. Otherwise, the array status is unlocked. In locked state, the output of a power device is not subject to the control of the SmartLogger. Note: Value 0 indicates the locked state. | 1 | Array startup control | 0: Startup 1: Invalid | Starts up all PV inverters and ESS devices in the array if the value is 0. | 1 | Array active power adjustment (exact power value) | kW | 0.1 |  | Controls the active power output of the inverters/PCSs in the array using an absolute value.
2 | Total PV input power | kW | 0.001 | [-3.4E+38, 3.4E+38] | Total active power of PV modules (string 1.0) and MPPT combiner boxes (string 2.0) on the DC side of PV inverters in the array. | 2 | DI1 status | 0: Off 1: On | DI1 input status. | 2 | Array shutdown control | 0: Shutdown 1: Invalid | Shuts down all PV inverters and ESS devices in the array if the value is 0. | 2 | Array reactive power adjustment (exact power value) | kVar | 0.1 |  | Controls the reactive power output of the inverters/PCSs in the array using an absolute value.
3 | Phase A current of array | A | 1 | [-3.4E+38, 3.4E+38] |  | 3 | DI2 status | 0: Off 1: On | DI2 input status. | 3 | Array startup/shutdown control | 0: Shutdown 1: Startup | Shuts down all PV inverters and ESS devices in the array if the value is 0, and starts up them if the value is 1. Do not use this signal with "Array startup control" or "Array shutdown control". | 3 | Array active power adjustment (in percentage) | % | 0.1 |  | Controls the active power output of the inverters/PCSs in the array using a percentage.
4 | Phase B current of array | A | 1 | [-3.4E+38, 3.4E+38] |  | 4 | DI3 status | 0: Off 1: On | DI3 input status. | 4 | PV inverters shutdown in array | 0: Shutdown 1: Invalid | Shuts down all PV inverters in the array if the value is 0. | 4 | Array reactive power adjustment (power factor) | NA | 0.001 |  | Controls the reactive power output of the inverters/PCSs in the array using a power factor.
5 | Phase C current of array | A | 1 | [-3.4E+38, 3.4E+38] |  | 5 | DI4 status | 0: Off 1: On | DI4 input status. | 5 | PV inverters startup in array | 0: Startup 1: Invalid | Starts up all PV inverters in the array if the value is 0. | 5 | Voltage adjustment value for VSG synchronous control of array | % | 0.01
6 | Array active power | kW | 0.001 | [-3.4E+38, 3.4E+38] | Total output active power of PV inverters and PCSs in the array. | 6 | DI5 status | 0: Off 1: On | DI5 input status. Not applicable to SmartLogger3000. | 6 | ESSs shutdown in array | 0: Shutdown 1: Invalid | Shuts down all ESS devices in the array if the value is 0. | 6 | Frequency adjustment value for VSG synchronous control of array | % | 0.01
7 | Array reactive power | kVar | 0.001 | [-3.4E+38, 3.4E+38] | Total output reactive power of PV inverters and PCSs in the array. | 7 | DI6 status | 0: Off 1: On | DI6 input status. Not applicable to SmartLogger3000. | 7 | ESSs startup in array | 0: Startup 1: Invalid | Starts up all ESS devices in the array if the value is 0. | 7 | Array black start | NA | 0: Disabled 1: Black start preparation 2: Black start voltage establishment
8 | Array power factor | / | 0.001 | (-1,1] |  | 8 | DI7 status | 0: Off 1: On | DI7 input status. Not applicable to SmartLogger3000. | 8 | PCSs shutdown in array | 0: Shutdown 1: Invalid | Shuts down all PCSs devices in the array if the value is 0. | 8 | Active PV inverter power adjustment of array in fixed value | kW | 0.1 |  | Controls the active power output of the inverters in the array using an absolute value.
9 | Array yield today | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array on the current day (starting from 00:00:00). | 9 | DI8 status | 0: Off 1: On | DI8 input status. Not applicable to SmartLogger3000. | 9 | PCSs startup in array | 0: Startup 1: Invalid | Starts up all PCSs devices in the array if the value is 0. | 9 | Active PV inverter power adjustment of array in percentage | % | 0.1 |  | Controls the active power output of the inverters in the array using a percentage.
10 | Total array yield | kWh | 1 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array. | 10 | Active power scheduling instruction error 1 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 10 | Active ESS PCS power adjustment of array in fixed value | kW | 0.1 |  | Controls the active power output of the PCSs in the array using an absolute value.
11 | PV inverter efficiency of array | % | 0.01 | [0, 100.0] | Ratio of the total AC active output power to the total DC input power of PV inverters in the array. | 11 | Active power scheduling instruction error 2 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 11 | Active ESS PCS power adjustment of array in percentage | % | 0.1 |  | Controls the active power output of the PCSs in the array using a percentage.
12 | CO2 reduction of array | kg | 1 | [0, 3.4E+38] |  | 12 | Active power scheduling instruction error 3 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 12 | Reactive PV inverter power adjustment of array in fixed value | kVar | 0.1 |  | Controls the reactive power output of the inverters in the array using an absolute value.
13 | Array active power scheduling feedback | kW | 0.001 | [-3.4E+38, 3.4E+38] | Active power scheduling value of the array. | 13 | Active power scheduling instruction error 4 | 0: No error 1: Error | The active power is in the "Active power scheduling via DI port" mode, and invalid instruction combinations are read from the four DI ports. |  |  |  |  | 13 | Reactive ESS PCS power adjustment of array in fixed value | kVar | 0.1 |  | Controls the reactive power output of the PCSs in the array using an absolute value.
14 | Array reactive power scheduling feedback | kVar/ | 0.001 | [-3.4E+38, 3.4E+38] or (–1, 1] | Reactive power scheduling value (kVar) or scheduled power factor of the array. | 14 | Reactive power scheduling instruction error 1 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 14 | Working mode of PCSs in array | NA | 0: PQ 1: VSG | 0: PQ 1: VSG
15 | Upper limit of array active power adjustment | kW | 0.001 | [0, 3.4E+38] | Total maximum configurable active power of PV inverters and PCSs in the array. | 15 | Reactive power scheduling instruction error 2 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 15 | Microgrid compatibility of PV inverter in array | NA | 1 | 0: Disable 1: Enable
16 | Upper limit of array reactive power adjustment | kVar | 0.001 | [0, 3.4E+38] | Total maximum configurable inductive reactive power of PV inverters and PCSs in the array. | 16 | Reactive power scheduling instruction error 3 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted.
17 | Lower limit of array reactive power adjustment | kVar | 0.001 | [-3.4E+38, 0] | Total maximum configurable capacitive reactive power of PV inverters and PCSs in the array. | 17 | Reactive power scheduling instruction error 4 | 0: No error 1: Error | The reactive power is in the "Reactive power scheduling via DI port" mode, and invalid instruction combinations are read from the four DI ports.
18 | Array yield this week | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array in this week (starting from 00:00:00 on Monday). | 18 | Power meter data feedback error | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted.
19 | Array yield this month | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array in this month (starting from 00:00:00 on the first day of the month). | 19 | Main Circuit Breaker Disconnected Alarm | 0: No alarm 1: Alarm | If the circuit breaker at the grid-connection point of the array is OFF, the value is "Error". Otherwise, the value is "No error".
20 | Array yield this year | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array in this year (starting from 00:00:00 on the first day of January). | 20 | Abnormal Cubicle | 0: No error 1: Error | If the Cubicle device has detected an exception at the grid connection point, the value is "Error". Otherwise, the value is "No error".
21 | Today's PV power generation hours of array | hour | 0.1 | [0, 24] | Longest power generation hours of PV inverters in the array from 00:00 of the current day. | 21 | Device Address Conflict | 0: No conflict 1: Conflict | If the communication address of the current device conflicts with that of the device to be connected, the value is "Error". Otherwise, the value is "No error".
22 | Rated array power | kW | 0.001 | [0, 3.4E+38] | Total rated power of PV inverters and PCSs in the array. | 22 | SPD fault | 0: No alarm 1: Alarm | If the SPD in the Smart Array Controller is faulty, the value is 1. Otherwise, the value is 0. Applicable only to SmartLogger2000.
23 | PV inverter status of array (Xinjiang) | / | / | 0: Standby 1: Power generation 2: Power generation at self-derated power 3: Power generation at derated power due to curtailment 4: Shut down as planned 5: Shut down due to curtailment 6: Shut down due to faults 7: Communication interruption | 0: Standby 1: Power generation 2: Power generation at self-derated power 3: Power generation at derated power due to curtailment 4: Shut down as planned 5: Shut down due to curtailment 6: Shut down due to faults 7: Communication interruption | 23 | Custom alarm 1 | 0: No alarm 1: Alarm | Custom alarms can be created. If the dry contact signal from the external device to the corresponding DI port on the SmartLogger is abnormal, the value is 1.
24 | PV inverter status of array (Ningxia) | / | / | 1: In operation 2: Shut down 3: Under maintenance/Communication interruption 4: Standby | 1: In operation 2: Shut down 3: Under maintenance/Communication interruption 4: Standby | 24 | Custom alarm 2 | 0: No alarm 1: Alarm
25 | A-B line voltage of array | V | 0.1 | [0, 6553] |  | 25 | Custom alarm 3 | 0: No alarm 1: Alarm
26 | B-C line voltage of array | V | 0.1 | [0, 6553] |  | 26 | Custom alarm 4 | 0: No alarm 1: Alarm
27 | C-A line voltage of array | V | 0.1 | [0, 6553] |  | 27 | Custom alarm 5 | 0: No alarm 1: Alarm
28 | PV inverter status of array (Qinghai) | / | / | 1: Running without restrictions 2: Running with restrictions 3: Standby 4: Unavailable (faulty or under maintenance) 5: Communication failure | 1: Running without restrictions 2: Running with restrictions 3: Standby 4: Unavailable (faulty or under maintenance) 5: Communication failure | 28 | Custom alarm 6 | 0: No alarm 1: Alarm
29 | PV inverter status of array (Qinghai 2019) | / | / | 1: In operation 2: Standby 3: Unavailable 4: Communication interruption | 1: In operation 2: Standby 3: Unavailable 4: Communication interruption | 29 | Custom alarm 7 | 0: No alarm 1: Alarm
30 | PV inverter status of array (Shaanxi) | / | / | 1: In operation 2: Standby 3: Unavailable or restricted 4: Communication interruption | 1: In operation 2: Standby 3: Unavailable or restricted 4: Communication interruption | 30 | Custom alarm 8 | 0: No alarm 1: Alarm
31 | Array end-of-charge SOC | % | 0.1 | [0, 100] |  | 31 | Array in operation | 0: Not in operation 1: In operation | An array is regarded in operation if any inverter or PCS in the array is in operation.
32 | Array end-of-discharge SOC | % | 0.1 | [0, 100] |  | 32 | Array shut down | 0: Not shut down 1: Shut down | An array is regarded shut down only when all inverters and PCSs in the array are shut down (including all not-in-operation states, such as faulty, standby, and shut down).
33 | Dischargeable array capacity (ESS, Dezhou, Shandong) | % | 0.1 | [0, 100] | Difference between "Array SOC" and "Array end-of-discharge SOC". | 33 | 24 V Power Supply Fault | 0: No error 1: Error | If the 24V power supply in the Smart Array Controller is faulty, the value is 1. Otherwise, the value is 0. Applicable only to SmartLogger2000.
34 | Chargeable array capacity (ESS, Dezhou, Shandong) | % | 0.1 | [0, 100] | Difference between "Array end-of-charge SOC" and "Array SOC". | 34 | License Expired | 0: Not expired 1: Expired | If the license file has reached the expiration date, the license is expired. Otherwise, the license is not expired.
35 | Array SOC | % | 0.1 | [0, 100] |  | 35 | Array ESS charge | 0: Not charging/discharging 1: Charging | It is determined based on the total active power of all PCSs in the array. A negative value indicates charging.
36 | Highest real-time charge power of ESSs in array | kW | 0.001 | [0, 3.4E+38] | The power cables of ESS devices in the array are connected to different DC buses. The charge power of each DC bus is the total real-time adjustable charge power of the PCSs connected to the DC bus or the total chargeable power of battery racks, whichever is smaller. The value of this signal is the total charge power of all DC buses. | 36 | Array ESS discharge | 0: Not charging/discharging 1: Discharging | It is determined based on the total active power of all PCSs in the array. A positive value indicates discharging.
37 | Highest real-time discharge power of ESSs in array | kW | 0.001 | [0, 3.4E+38] | The power cables of ESS devices in the array are connected to different DC buses. The discharge power of each DC bus is the total real-time adjustable discharge power of the PCSs connected to the DC bus or the total dischargeable power of battery racks, whichever is smaller. The value of this signal is the total discharge power of all DC buses. | 37 | ESS PCS shutdown (ESS, Dezhou, Shandong) | 0: Not shut down 1: Shut down | All PCSs in the array are in shut down state.
38 | Total energy charged to ESSs in array | kWh | 0.01 | [0, 3.4E+38] |  | 38 | ESS PCS standby (ESS, Dezhou, Shandong) | 0: Not standby 1: Standby | All PCSs in the array are in standby mode.
39 | Total energy discharged from ESSs in array | kWh | 0.01 | [0, 3.4E+38] |  | 39 | ESS PCS faulty (ESS, Dezhou, Shandong) | 0: No error 1: Error | All PCSs in the array are faulty (shut down due to faults).
40 | Energy charged to ESSs in array today | kWh | 0.01 | [0, 3.4E+38] |  | 40 | Array fault identifier (ESS, Dezhou, Shandong) | 0: No error 1: Error | If a critical or major alarm exists in the array, the value is 1. Otherwise, the value is 0.
41 | Energy discharged from ESSs in array today | kWh | 0.01 | [0, 3.4E+38] |  | 41 | Array error identifier (ESS, Dezhou, Shandong) | 0: No error 1: Error | If a minor or warning alarm exists in the array, the value is 1. Otherwise, the value is 0.
42 | Chargeable capacity of ESSs in array | kWh | 0.001 | [0, 3.4E+38] |  | 42 | Charge locking of ESSs in array | 0: Locked 1: Unlocked | If the upper limit of charging is set to 0 for ESSs in the array, the charge function is locked. Note: Value 0 indicates the locked state.
43 | Dischargeable capacity of ESSs in array | kWh | 0.001 | [0, 3.4E+38] |  | 43 | Discharge locking of ESSs in array | 0: Locked 1: Unlocked | If the upper limit of discharging is set to 0 for ESSs in the array, the discharge function is locked. Note: Value 0 indicates the locked state.
44 | Today's power supply from grid to PCSs in array | kWh | 0.01 | [0, 3.4E+38] |  | 44 | PV inverter in operation in array | 0: Not in operation 1: In operation | At least one inverter in the array is in operation.
45 | Total power supply from grid to PCSs in array | kWh | 0.01 | [0, 3.4E+38] |  | 45 | PV inverter shut down in array | 0: Not shut down 1: Shut down | All inverters in the array are in shut down state (including all not-in-operation states, such as faulty, standby, and communication failure).
46 | Longest time for charging array to the end-of-charge SOC (ESS, Dezhou, Shandong) | min | 1 | [0, 65535] | Longest duration for ESS devices in the array to be charged to the end-of-charge SOC. | 46 | ESS PCS in operation in array | 0: Not in operation 1: In operation | At least one PCS in the array is in operation.
47 | Longest time for discharging array to the end-of-discharge SOC (ESS, Dezhou, Shandong) | min | 1 | [0, 65535] | Longest duration for ESS devices in the array to be discharged to the end-of-discharge SOC.
48 | Rated capacity of ESSs in array | kWh | 0.001 | [0, 3.4E+38]
49 | Quantity of PCSs in array | / | 1 | [0, 65535] | Quantity of PCSs in the array.
50 | Quantity of available PCSs in array | / | 1 | [0, 65535] | Quantity of running PCSs in the array.
51 | Active power of PV inverters in array | kW | 0.001 | [0, 3.4E+38]
52 | Reactive power of PV inverters in array | kVar | 0.001 | [-3.4E+38, 3.4E+38]
53 | Total active power of ESS PCSs | kW | 0.001 | [-3.4E+38, 3.4E+38]
54 | Total reactive power of ESS PCSs | kVar | 0.001 | [-3.4E+38, 3.4E+38]
55 | Rated power of PV inverters in array | kW | 0.001 | [0, 3.4E+38]
56 | Rated ESS PCS power | kW | 0.001 | [0, 3.4E+38]
57 | Maximum reactive ESS PCS power adjustment value | kVar | 0.001 | [0, 3.4E+38] | Total maximum output inductive reactive power of PCSs in the array.
58 | Minimum reactive ESS PCS power adjustment value | kVar | 0.001 | [-3.4E+38, 0] | Total maximum output capacitive reactive power of PCSs in the array.
59 | Array black start status | / | / | 0: Not started 1: Preparing for black start 2: Ready for black start 3: Establishing voltage for black start 4: Voltage established for black start 5: Black start failed | Black start status of the array, which can be: 0: Not started 1: Preparing for black start 2: Ready for black start 3: Establishing voltage for black start 4: Voltage established for black start 5: Black start failed
60 | Array SOH | % | 0.1 | [0, 100]
61 | Array SOE | % | 0.1 | [0, 100]
62 | Total rated capacity of ESS PCSs (Ah) | Ah | 0.1 | [0, 3.4E+38] | Total rated capacity (Ah) of battery racks in the array.
63 | Lower limit of array active power adjustment | kW | 0.001 | [-3.4E+38, 0] | Maximum charge power (negative value) supported by the ESS devices in the array. The value is 0 for the PV array.
64 | Maximum active power adjustment value for PV inverters in array | kW | 0.001 | [0, 3.4E+38] | Total maximum output active power of all PV inverters in the array.
65 | Maximum reactive power adjustment value for PV inverters in array | kVar | 0.001 | [0, 3.4E+38] | Total maximum output inductive reactive power of all PV inverters in the array.
66 | Minimum reactive power adjustment value for PV inverters in array | kVar | 0.001 | [-3.4E+38, 0] | Total maximum output capacitive reactive power of all PV inverters in the array.
67 | Highest stable charge power of ESSs in array | kW | 0.001 | [0, 3.4E+38] | Maximum charge rate of ESSs in the array. Compared with the value of "Highest real-time charge power of ESSs in array", the value of this signal also includes the charge power of battery racks bypassed due to full discharge.
68 | Highest stable discharge power of ESSs in array | kW | 0.001 | [0, 3.4E+38] | Maximum discharge rate of ESSs in the array. Compared with the value of "Highest real-time discharge power of ESSs in array", the value of this signal also includes the discharge power of battery racks bypassed due to full charge.
69 | Working mode of PCSs in array | / | / | 0: PQ 1: VSG
70 | Invalid | / | / | / | /
71 | Subarray steady-state SOC | % | 0.1 | [0, 100] | Σ(SOC cluster i x SOH cluster i x Rated power cluster i)/Σ(SOH cluster i x Rated power cluster i) Note: (1) SOC cluster i, SOH cluster i, and rated energy cluster i are reported by the BCU. 2) Sum range for all running and commanded shutdown battery clusters in the subarray. 3) The capacity dimension is Ah, and the SOC dimension is %. 4) The SOC here is used for display and is calculated in real time.
72 | Steady-state chargeable capacity of the storage battery in the array | kWh | 0.001 | [0, 3.4E+38] | Σ Chargeable power cluster i Note: 1. The chargeable battery level cluster is reported by the BCU. 2) Sum range for all operating and shutdown instruction battery clusters in the subarray. 3) The rechargeable capacity is controlled and calculated in real time.
73 | Steady-state discharge capacity of the batteries in the array | kWh | 0.001 | [0, 3.4E+38] | Σ Discharging capacity cluster i Note: 1. The dischargeable capacity cluster is reported by the BCU. 2) Summation range for all running and commanded shutdown battery clusters in the subarray. 3) The discharge capacity is used for control and is calculated in real time.
74 | Invalid | / | / | / | /
75 | Estimated Subarray Illumination Status | / | / | 0: not started 1: being estimated 2: estimated completion 3: estimation failure | If all inverters do not support light estimation or the estimation fails, a message is displayed indicating that the estimation fails.
76 | Estimated active power of the solar array | kW | 0.001 | [0, 3.4E+38] | ∑Rated power of all inverters in a subarray x ∑Estimated power of inverters that support illumination estimation in the subarray/∑Rated power of inverters that support illumination estimation in the subarray
77 | Current-month charge capacity of the battery in the array | kWh | 0.01 | [0, 3.4E+38]
78 | Current-month discharge capacity of batteries in the array | kWh | 0.01 | [0, 3.4E+38]
79 | Annual charging capacity of the sub-array energy storage battery | kWh | 0.01 | [0, 3.4E+38]
80 | Annual discharging capacity of the sub-array energy storage battery | kWh | 0.01 | [0, 3.4E+38]
81 | Total absorbed capacity of the sub-array PCS in the current month | kWh | 0.01 | [0, 3.4E+38]
82 | Total absorbed capacity of the sub-array PCS in the current year | kWh | 0.01 | [0, 3.4E+38]
83 | Total discharged capacity of the sub-array PCS in the current day | kWh | 0.01 | [0, 3.4E+38]
84 | Total discharged capacity of the sub-array PCS in the current month | kWh | 0.01 | [0, 3.4E+38]
85 | Total discharged capacity of the sub-array PCS in the current year | kWh | 0.01 | [0, 3.4E+38]
86 | Accumulated total discharged capacity of the sub-array PCS | kWh | 0.01 | [0, 3.4E+38]
87 | PV array active power (fast) | kWh | 0.01 | [0, 3.4E+38] | Indicates the total active output power of the PV inverters and PCSs in a subarray (fast port).
88 | Active power of the PV array inverter (fast) | kWh | 0.01 | [0, 3.4E+38] | Indicates the total active output power of the PV inverters in a subarray (fast port).
89 | Indicates the total active output power of the PV inverters in a subarray (fast port). | kWh | 0.01 | [0, 3.4E+38] | Total output active power of each PCS in the subarray (fast port)
Added "array" to some signals to help the EMS to distinguish device-level signals from array-level signals.
Note on J12: 作者: 苏安明对齐现网问题。
Note on J13: 作者: 苏安明对齐现网问题。
Note on J14: 作者: 苏安明对齐现网问题。
Note on J20: 作者: 标识删除该告警的版本

## SmartLogger-PV-Only
Telemetry | [5 empty] | Teleindication |  |  |  | Telecontrol | Signal Name | Command |  | Teleadjust
No. | Signal Name | Unit | Precision | Range | Remarks | No. | Signal Name | Status | Remarks | No. | Signal Name | Command | Remarks | No. | Signal Name | Unit | Precision | Remarks
1 | Total PV DC current | A | 0.1 | [-3.4E+38, 3.4E+38] | Total input current from PV modules (string 1.0) and MPPT combiner boxes (string 2.0) on the DC side of PV inverters in the array. | 1 | Array locking status | 0: Locked 1: Unlocked | If all inverters/PCSs in the array are locked, the array status is locked. Otherwise, the array status is unlocked. In locked state, the output of a power device is not subject to the control of the SmartLogger. Note: Value 0 indicates the locked state. | 1 | Array startup control | 0: Startup 1: Invalid | Starts up all PV inverters and ESS devices in the array if the value is 0. | 1 | Array active power adjustment (exact power value) | kW | 0.1 | Controls the active power output of the inverters/PCSs in the array using an absolute value.
2 | Total PV input power | kW | 0.001 | [-3.4E+38, 3.4E+38] | Total active power of PV modules (string 1.0) and MPPT combiner boxes (string 2.0) on the DC side of PV inverters in the array. | 2 | DI1 status | 0: Off 1: On | DI1 input status. | 2 | Array shutdown control | 0: Shutdown 1: Invalid | Shuts down all PV inverters and ESS devices in the array if the value is 0. | 2 | Array reactive power adjustment (exact power value) | kVar | 0.1 | Controls the reactive power output of the inverters/PCSs in the array using an absolute value.
3 | Phase A current of array | A | 1 | [-3.4E+38, 3.4E+38] |  | 3 | DI2 status | 0: Off 1: On | DI2 input status. | 3 | Array startup/shutdown control | 0: Shutdown 1: Startup | Shuts down all PV inverters and ESS devices in the array if the value is 0, and starts up them if the value is 1. Do not use this signal with "Array startup control" or "Array shutdown control". | 3 | Array active power adjustment (in percentage) | % | 0.1 | Controls the active power output of the inverters/PCSs in the array using a percentage.
4 | Phase B current of array | A | 1 | [-3.4E+38, 3.4E+38] |  | 4 | DI3 status | 0: Off 1: On | DI3 input status. | 4 | PV inverters shutdown in array | 0: Shutdown 1: Invalid | Shuts down all PV inverters in the array if the value is 0. | 4 | Array reactive power adjustment (power factor) | NA | 0.001 | Controls the reactive power output of the inverters/PCSs in the array using a power factor.
5 | Phase C current of array | A | 1 | [-3.4E+38, 3.4E+38] |  | 5 | DI4 status | 0: Off 1: On | DI4 input status. | 5 | PV inverters startup in array | 0: Startup 1: Invalid | Starts up all PV inverters in the array if the value is 0. | 5 | Invalid | / | / | /
6 | Array active power | kW | 0.001 | [-3.4E+38, 3.4E+38] | Total output active power of PV inverters and PCSs in the array. | 6 | DI5 status | 0: Off 1: On | DI5 input status. Not applicable to SmartLogger3000. | 6 | Invalid | / | / | 6 | Invalid | / | / | /
7 | Array reactive power | kVar | 0.001 | [-3.4E+38, 3.4E+38] | Total output reactive power of PV inverters and PCSs in the array. | 7 | DI6 status | 0: Off 1: On | DI6 input status. Not applicable to SmartLogger3000. | 7 | Invalid | / | / | 7 | Invalid | / | / | /
8 | Array power factor | / | 0.001 | (-1,1] |  | 8 | DI7 status | 0: Off 1: On | DI7 input status. Not applicable to SmartLogger3000. | 8 | Invalidation | / | / | 8 | Active PV inverter power adjustment of array in fixed value | kW | 0.1 | Controls the active power output of the inverters in the array using an absolute value.
9 | Array yield today | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array on the current day (starting from 00:00:00). | 9 | DI8 status | 0: Off 1: On | DI8 input status. Not applicable to SmartLogger3000. | 9 | Invalidation | / | / | 9 | Active PV inverter power adjustment of array in percentage | % | 0.1 | Controls the active power output of the inverters in the array using a percentage.
10 | Total array yield | kWh | 1 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array. | 10 | Active power scheduling instruction error 1 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. | 10 | Subarray PV Inverter HVRT | 0: disabled; 1: enabled | High penetration of all PV inverters in the control subarray | 10 | Invalid | / | / | /
11 | PV inverter efficiency of array | % | 0.01 | [0, 100.0] | Ratio of the total AC active output power to the total DC input power of PV inverters in the array. | 11 | Active power scheduling instruction error 2 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. | 11 | PV inverter LVRT | 0: disabled; 1: enabled | All PV inverters in the control subarray are underpassed. | 11 | Invalid | / | / | /
12 | CO2 reduction of array | kg | 1 | [0, 3.4E+38] |  | 12 | Active power scheduling instruction error 3 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. | 12 | Subarray illumination estimation | 0: enabled1: invalid | Controls all PV inverters in the array to perform illumination estimation. | 12 | Reactive PV inverter power adjustment of array in fixed value | kVar | 0.1 | Controls the reactive power output of the inverters in the array using an absolute value.
13 | Array active power scheduling feedback | kW | 0.001 | [-3.4E+38, 3.4E+38] | Active power scheduling value of the array. | 13 | Active power scheduling instruction error 4 | 0: No error 1: Error | The active power is in the "Active power scheduling via DI port" mode, and invalid instruction combinations are read from the four DI ports. | 13 | Invalidation | / | / | 13 | Invalid | / | / | /
14 | Array reactive power scheduling feedback | kVar/ | 0.001 | [-3.4E+38, 3.4E+38] or (–1, 1] | Reactive power scheduling value (kVar) or scheduled power factor of the array. | 14 | Reactive power scheduling instruction error 1 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. | 14 | Invalidation | / | / | 14 | Invalid | / | / | /
15 | Upper limit of array active power adjustment | kW | 0.001 | [0, 3.4E+38] | Total maximum configurable active power of PV inverters and PCSs in the array. | 15 | Reactive power scheduling instruction error 2 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 15 | Invalidation | / | / | / | /
16 | Upper limit of array reactive power adjustment | kVar | 0.001 | [0, 3.4E+38] | Total maximum configurable inductive reactive power of PV inverters and PCSs in the array. | 16 | Reactive power scheduling instruction error 3 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 16 | Invalidation | / | / | / | /
17 | Lower limit of array reactive power adjustment | kVar | 0.001 | [-3.4E+38, 0] | Total maximum configurable capacitive reactive power of PV inverters and PCSs in the array. | 17 | Reactive power scheduling instruction error 4 | 0: No error 1: Error | The reactive power is in the "Reactive power scheduling via DI port" mode, and invalid instruction combinations are read from the four DI ports. |  |  |  |  | 17 | Invalidation | / | / | / | /
18 | Array yield this week | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array in this week (starting from 00:00:00 on Monday). | 18 | Power meter data feedback error | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 18 | Invalidation | / | / | / | /
19 | Array yield this month | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array in this month (starting from 00:00:00 on the first day of the month). | 19 | Main Circuit Breaker Disconnected Alarm | 0: No alarm 1: Alarm | If the circuit breaker at the grid-connection point of the array is OFF, the value is "Error". Otherwise, the value is "No error". |  |  |  |  | 19 | Invalidation | / | / | / | /
20 | Array yield this year | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array in this year (starting from 00:00:00 on the first day of January). | 20 | Abnormal Cubicle | 0: No error 1: Error | If the Cubicle device has detected an exception at the grid connection point, the value is "Error". Otherwise, the value is "No error". |  |  |  |  | 20 | Subarray PV inverter working mode | NA | 0：PQ 1：VSG | 0：PQ 1：VSG | After the setting, the SmartLogger broadcasts the settings to all PV inverters.
21 | Today's PV power generation hours of array | hour | 0.1 | [0, 24] | Longest power generation hours of PV inverters in the array from 00:00 of the current day. | 21 | Device Address Conflict | 0: No conflict 1: Conflict | If the communication address of the current device conflicts with that of the device to be connected, the value is "Error". Otherwise, the value is "No error".
22 | Rated array power | kW | 0.001 | [0, 3.4E+38] | Total rated power of PV inverters and PCSs in the array. | 22 | SPD fault | 0: No alarm 1: Alarm | If the SPD in the Smart Array Controller is faulty, the value is 1. Otherwise, the value is 0. Applicable only to SmartLogger2000.
23 | PV inverter status of array (Xinjiang) | / | / | / | 0: Standby 1: Power generation 2: Power generation at self-derated power 3: Power generation at derated power due to curtailment 4: Shut down as planned 5: Shut down due to curtailment 6: Shut down due to faults 7: Communication interruption | 23 | Custom alarm 1 | 0: No alarm 1: Alarm | Custom alarms can be created. If the dry contact signal from the external device to the corresponding DI port on the SmartLogger is abnormal, the value is 1.
24 | PV inverter status of array (Ningxia) | / | / | / | 1: In operation 2: Shut down 3: Under maintenance/Communication interruption 4: Standby | 24 | Custom alarm 2 | 0: No alarm 1: Alarm
25 | A-B line voltage of array | V | 0.1 | [0, 6553] |  | 25 | Custom alarm 3 | 0: No alarm 1: Alarm
26 | B-C line voltage of array | V | 0.1 | [0, 6553] |  | 26 | Custom alarm 4 | 0: No alarm 1: Alarm
27 | C-A line voltage of array | V | 0.1 | [0, 6553] |  | 27 | Custom alarm 5 | 0: No alarm 1: Alarm
28 | PV inverter status of array (Qinghai) | / | / | / | 1: Running without restrictions 2: Running with restrictions 3: Standby 4: Unavailable (faulty or under maintenance) 5: Communication failure | 28 | Custom alarm 6 | 0: No alarm 1: Alarm
29 | PV inverter status of array (Qinghai 2019) | / | / | / | 1: In operation 2: Standby 3: Unavailable 4: Communication interruption | 29 | Custom alarm 7 | 0: No alarm 1: Alarm
30 | PV inverter status of array (Shaanxi) | / | / | / | 1: In operation 2: Standby 3: Unavailable or restricted 4: Communication interruption | 30 | Custom alarm 8 | 0: No alarm 1: Alarm
31 | Invalid | / | / | / | / | 31 | Array in operation | 0: Not in operation 1: In operation | An array is regarded in operation if any inverter or PCS in the array is in operation.
32 | Invalid | / | / | / | / | 32 | Array shut down | 0: Not shut down 1: Shut down | An array is regarded shut down only when all inverters and PCSs in the array are shut down (including all not-in-operation states, such as faulty, standby, and shut down).
33 | Invalid | / | / | / | / | 33 | 24 V Power Supply Fault | 0: No error 1: Error | If the 24V power supply in the Smart Array Controller is faulty, the value is 1. Otherwise, the value is 0. Applicable only to SmartLogger2000.
34 | Invalid | / | / | / | / | 34 | License Expired | 0: Not expired 1: Expired | If the license file has reached the expiration date, the license is expired. Otherwise, the license is not expired.
35 | Invalid | / | / | / | / | 35 | Invalid | / | /
36 | Invalid | / | / | / | / | 36 | Invalid | / | /
37 | Invalid | / | / | / | / | 37 | Invalid | / | /
38 | Invalid | / | / | / | / | 38 | Invalid | / | /
39 | Invalid | / | / | / | / | 39 | Invalid | / | /
40 | Invalid | / | / | / | / | 40 | Invalid | / | /
41 | Invalid | / | / | / | / | 41 | Invalid | / | /
42 | Invalid | / | / | / | / | 42 | Invalid | / | /
43 | Invalid | / | / | / | / | 43 | Invalid | / | /
44 | Invalid | / | / | / | / | 44 | PV inverters operation in array | 0: Not in operation 1: In operation | At least one inverter in the array is in operation.
45 | Invalid | / | / | / | / | 45 | PV inverters shutdown in array | 0: Not shut down 1: Shut down | All inverters in the array are in shut down state (including all not-in-operation states, such as faulty, standby, and communication failure).
46 | Invalid | / | / | / | / | 46 | Invalid | / | /
47 | Invalid | / | / | / | / | 47 | Microgrid Adaptability Triggering Status of Subarray PV Inverter | 0: not triggered 1: triggered | The microgrid adaptability of any PV inverter in the subarray is triggered, that is, the status is reported as triggered.
48 | Invalid | / | / | / | / | 48 | Invalidation | / | /
49 | Invalid | / | / | / | /
50 | Invalid | / | / | / | /
51 | Active power of PV inverters in array | kW | 0.001 | [0, 3.4E+38] | /
52 | Reactive power of PV inverters in array | kVar | 0.001 | [-3.4E+38, 3.4E+38] | /
53 | Invalid | / | / | / | /
54 | Invalid | / | / | / | /
55 | Rated power of PV inverters in array | kW | 0.001 | [0, 3.4E+38] | /
56 | Invalid | / | / | / | /
57 | Invalid | / | / | / | /
58 | Invalid | / | / | / | /
59 | Invalid | / | / | / | /
60 | Invalid | / | / | / | /
61 | Invalid | / | / | / | /
62 | Invalid | / | / | / | /
63 | Lower limit of array active power adjustment | kW | 0.001 | [-3.4E+38, 0] | Maximum charge power (negative value) supported by the ESS devices in the array. The value is 0 for the PV array.
64 | Maximum active power adjustment value for PV inverters in array | kW | 0.001 | [0, 3.4E+38] | Total maximum output active power of all PV inverters in the array.
65 | Maximum reactive power adjustment value for PV inverters in array | kVar | 0.001 | [0, 3.4E+38] | Total maximum output inductive reactive power of all PV inverters in the array.
66 | Minimum reactive power adjustment value for PV inverters in array | kVar | 0.001 | [-3.4E+38, 0] | Total maximum output capacitive reactive power of all PV inverters in the array.
67 | Highest stable charge power of ESSs in array | kW | 0.001 | [0, 3.4E+38] | Maximum charge rate of ESSs in the array. Compared with the value of "Highest real-time charge power of ESSs in array", the value of this signal also includes the charge power of battery racks bypassed due to full discharge.
68 | Highest stable discharge power of ESSs in array | kW | 0.001 | [0, 3.4E+38] | Maximum discharge rate of ESSs in the array. Compared with the value of "Highest real-time discharge power of ESSs in array", the value of this signal also includes the discharge power of battery racks bypassed due to full charge.
69 | Invalid | / | / | / | /
70 | PV Array Inverter Status (Hubei) | / | / | / | 1: normal running 2: controlled output 3: standby 4: suspended
71 | Invalid | / | / | / | /
72 | Invalid | / | / | / | /
73 | Invalid | / | / | / | /
74 | PV array PV inverter status (Tianjin) | / | / | / | 1. Normal power generation 2. Standby [No light] 3. Standby [High temperature] 4. Standby [snow cover] 5. Off-site restricted [power generation] 6. Off-site restricted [stop] 7. Limited in-field (power generation) 8. On-site restricted [stopping] 9. In-field limited (repair) 10. The communication is interrupted."
75 | Estimated Subarray Illumination Status | / | / | 0: not started 1: being estimated 2: estimated completion 3: estimation failure | If all inverters do not support light estimation or the estimation fails, a message is displayed indicating that the estimation fails.
76 | Estimated active power of the solar array | kW | 0.001 | [0, 3.4E+38] | ∑Rated power of all inverters in a subarray x ∑Estimated power of inverters that support illumination estimation in the subarray/∑Rated power of inverters that support illumination estimation in the subarray
77 | Invalid | / | / | / | /
78 | Invalid | / | / | / | /
79 | Invalid | / | / | / | /
80 | Invalid | / | / | / | /
81 | Invalid | / | / | / | /
82 | Invalid | / | / | / | /
83 | Invalid | / | / | / | /
84 | Invalid | / | / | / | /
85 | Invalid | / | / | / | /
86 | Invalid | / | / | / | /
87 | Invalid | / | / | / | /
88 | Active power of the PV array inverter (fast) | kWh | 0.01 | [0, 3.4E+38]
89 | Invalid | / | / | / | /
90 | Number of Subarray Standby Inverters (Sichuan) | / | 1 | [0,150] | Total number of inverters in the standby state in the subarray (Sichuan)
91 | Number of Inverters Stopped in the PV Array (Sichuan) | / | 1 | [0,150] | Summarize the number of inverters whose status is shutdown in the subarray (Sichuan).
92 | Number of solar inverters in controlled operation (Sichuan) | / | 1 | [0,150] | Indicates the number of inverters whose status is controlled in the subarray (Sichuan).
93 | Number of Inverters Running Properly in the PV Array (Sichuan) | / | 1 | [0,150] | Summarize the number of inverters whose status (Sichuan) is Running in the subarray.
Note on J12: 作者: 苏安明对齐现网问题。
Note on J13: 作者: 苏安明对齐现网问题。
Note on J14: 作者: 苏安明对齐现网问题。
Note on J20: 作者: 标识删除该告警的版本

## SmartLogger-ESS-Only
Telemetry | [5 empty] | Teleindication | Signal Name | Status |  | Telecontrol | Signal Name | Command |  | Teleadjust
No. | Signal Name | Unit | Precision | Range | Remarks | No. | Signal Name | Status | Remarks | No. | Signal Name | Command | Remarks | No. | Signal Name | Unit | Precision | Remarks
1 | Invalid | / | / | / | / | 1 | Array locking status | 0: Locked 1: Unlocked | If all inverters/PCSs in the array are locked, the array status is locked. Otherwise, the array status is unlocked. In locked state, the output of a power device is not subject to the control of the SmartLogger. Note: Value 0 indicates the locked state. | 1 | Array startup control | 0: Startup 1: Invalid | Starts up all PV inverters and ESS devices in the array if the value is 0. | 1 | Array active power adjustment (exact power value) | kW | 0.1 | Controls the active power output of the inverters/PCSs in the array using an absolute value.
2 | Invalid | / | / | / | / | 2 | DI1 status | 0: Off 1: On | DI1 input status. | 2 | Array shutdown control | 0: Shutdown 1: Invalid | Shuts down all PV inverters and ESS devices in the array if the value is 0. | 2 | Array reactive power adjustment (exact power value) | kVar | 0.1 | Controls the reactive power output of the inverters/PCSs in the array using an absolute value.
3 | Phase A current of array | A | 1 | [-3.4E+38, 3.4E+38] |  | 3 | DI2 status | 0: Off 1: On | DI2 input status. | 3 | Array startup/shutdown control | 0: Shutdown 1: Startup | Shuts down all PV inverters and ESS devices in the array if the value is 0, and starts up them if the value is 1. Do not use this signal with "Array startup control" or "Array shutdown control". | 3 | Array active power adjustment (in percentage) | % | 0.1 | Controls the active power output of the inverters/PCSs in the array using a percentage.
4 | Phase B current of array | A | 1 | [-3.4E+38, 3.4E+38] |  | 4 | DI3 status | 0: Off 1: On | DI3 input status. | 4 | Invalid | / | / | 4 | Array reactive power adjustment (power factor) | NA | 0.001 | Controls the reactive power output of the inverters/PCSs in the array using a power factor.
5 | Phase C current of array | A | 1 | [-3.4E+38, 3.4E+38] |  | 5 | DI4 status | 0: Off 1: On | DI4 input status. | 5 | Invalid | / | / | 5 | Voltage adjustment value for VSG synchronous control of array | % | 0.01
6 | Array active power | kW | 0.001 | [-3.4E+38, 3.4E+38] | Total output active power of PV inverters and PCSs in the array. | 6 | DI5 status | 0: Off 1: On | DI5 input status. Not applicable to SmartLogger3000. | 6 | ESSs shutdown in array | 0: Shutdown 1: Invalid | Shuts down all ESS devices in the array if the value is 0. | 6 | Frequency adjustment value for VSG synchronous control of array | % | 0.01
7 | Array reactive power | kVar | 0.001 | [-3.4E+38, 3.4E+38] | Total output reactive power of PV inverters and PCSs in the array. | 7 | DI6 status | 0: Off 1: On | DI6 input status. Not applicable to SmartLogger3000. | 7 | ESSs startup in array | 0: Startup 1: Invalid | Starts up all ESS devices in the array if the value is 0. | 7 | Array black start | NA | 0: Disabled 1: Black start preparation 2: Black start voltage establishment
8 | Array power factor | / | 0.001 | (-1,1] |  | 8 | DI7 status | 0: Off 1: On | DI7 input status. Not applicable to SmartLogger3000. | 8 | Sub-array PCS shutdown | 0: power off 1: invalid | Shuts down all energy storage PCSs in the PV array. | 8 | / | / | / | /
9 | Array yield today | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array on the current day (starting from 00:00:00). | 9 | DI8 status | 0: Off 1: On | DI8 input status. Not applicable to SmartLogger3000. | 9 | Sub-array PCS power on | 0: power-on 1: invalid | Sets the number of started energy storage units (ESSs) in an array to 0. | 9 | / | / | / | /
10 | Total array yield | kWh | 1 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array. | 10 | Active power scheduling instruction error 1 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. | 10 | Invalid | / | / | 10 | Active ESS PCS power adjustment of array in fixed value | kW | 0.1 | Controls the active power output of the PCSs in the array using an absolute value.
11 | Invalid | / | / | / | / | 11 | Active power scheduling instruction error 2 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. | 11 | Invalid | / | / | 11 | Active ESS PCS power adjustment of array in percentage | % | 0.1 | Controls the active power output of the PCSs in the array using a percentage.
12 | CO2 reduction of array | kg | 1 | [0, 3.4E+38] |  | 12 | Active power scheduling instruction error 3 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. | 12 | Invalid | / | / | 12 | / | / | / | /
13 | Array active power scheduling feedback | kW | 0.001 | [-3.4E+38, 3.4E+38] | Active power scheduling value of the array. | 13 | Active power scheduling instruction error 4 | 0: No error 1: Error | The active power is in the "Active power scheduling via DI port" mode, and invalid instruction combinations are read from the four DI ports. | 13 | One-click blackstart | 0: start 1: invalid | Starts all ESSs and PV modules in the PV array in one-click mode. | 13 | Reactive ESS PCS power adjustment of array in fixed value | kVar | 0.1 | Controls the reactive power output of the PCSs in the array using an absolute value.
14 | Array reactive power scheduling feedback | kVar/ | 0.001 | [-3.4E+38, 3.4E+38] or (–1, 1] | Reactive power scheduling value (kVar) or scheduled power factor of the array. | 14 | Reactive power scheduling instruction error 1 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. | 14 | Allow Coordinated Control | 0: disabled; 1: enabled | If this parameter is set to Enable, the SmartLogger receives the scheduling control instruction delivered by the northbound Goose. If this parameter is set to Disable, the SmartLogger blocks the scheduling control instruction delivered by the northbound Goose. This signal is used only when the SmartLogger connects to the NARI Relay Protection System (PMS) through the Goose northbound interface. | 14 | Working mode of PCSs in array | NA | 0: PQ 1: VSG
15 | Upper limit of array active power adjustment | kW | 0.001 | [0, 3.4E+38] | Total maximum configurable active power of PV inverters and PCSs in the array. | 15 | Reactive power scheduling instruction error 2 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 15 | Invalid | / | / | / | /
16 | Upper limit of array reactive power adjustment | kVar | 0.001 | [0, 3.4E+38] | Total maximum configurable inductive reactive power of PV inverters and PCSs in the array. | 16 | Reactive power scheduling instruction error 3 | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 16 | Grid-tied switch status | NA | 1 | 0: grid-tied 1: deregistered | After the setting, the SmartLogger broadcasts the setting to all PCSs.
17 | Lower limit of array reactive power adjustment | kVar | 0.001 | [-3.4E+38, 0] | Total maximum configurable capacitive reactive power of PV inverters and PCSs in the array. | 17 | Reactive power scheduling instruction error 4 | 0: No error 1: Error | The reactive power is in the "Reactive power scheduling via DI port" mode, and invalid instruction combinations are read from the four DI ports. |  |  |  |  | 17 | PV array charging cutoff SOC adjustment register | % | 1 | [90,100] | After the setting, the SmartLogger broadcasts the setting to all PCSs.
18 | Array yield this week | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array in this week (starting from 00:00:00 on Monday). | 18 | Power meter data feedback error | 0: No error 1: Error | The AI remote scheduling mode is no longer supported and is obsoleted. |  |  |  |  | 18 | PV array discharge end SOC adjustment | % | 1 | [0,15] | After the setting, the SmartLogger broadcasts the setting to all PCSs.
19 | Array yield this month | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array in this month (starting from 00:00:00 on the first day of the month). | 19 | Main Circuit Breaker Disconnected Alarm | 0: No alarm 1: Alarm | If the circuit breaker at the grid-connection point of the array is OFF, the value is "Error". Otherwise, the value is "No error". |  |  |  |  | 19 | PV array PCS microgrid adaptability | NA | 1 | 0: disabled 1: enabled | After the setting, the SmartLogger broadcasts the setting to all PCSs.
20 | Array yield this year | kWh | 0.01 | [0, 3.4E+38] | Total energy yield of PV inverters and PCSs in the array in this year (starting from 00:00:00 on the first day of January). | 20 | Abnormal Cubicle | 0: No error 1: Error | If the Cubicle device has detected an exception at the grid connection point, the value is "Error". Otherwise, the value is "No error". |  |  |  |  | 20 | Invalid | / | / | / | /
21 | Invalid | / | / | / | / | 21 | Device Address Conflict | 0: No conflict 1: Conflict | If the communication address of the current device conflicts with that of the device to be connected, the value is "Error". Otherwise, the value is "No error".
22 | Rated array power | kW | 0.001 | [0, 3.4E+38] | Total rated power of PV inverters and PCSs in the array. | 22 | SPD fault | 0: No alarm 1: Alarm | If the SPD in the Smart Array Controller is faulty, the value is 1. Otherwise, the value is 0. Applicable only to SmartLogger2000.
23 | Invalid | / | / | / | / | 23 | Custom alarm 1 | 0: No alarm 1: Alarm | Custom alarms can be created. If the dry contact signal from the external device to the corresponding DI port on the SmartLogger is abnormal, the value is 1.
24 | Invalid | / | / | / | / | 24 | Custom alarm 2 | 0: No alarm 1: Alarm
25 | A-B line voltage of array | V | 0.1 | [0, 6553] |  | 25 | Custom alarm 3 | 0: No alarm 1: Alarm
26 | B-C line voltage of array | V | 0.1 | [0, 6553] |  | 26 | Custom alarm 4 | 0: No alarm 1: Alarm
27 | C-A line voltage of array | V | 0.1 | [0, 6553] |  | 27 | Custom alarm 5 | 0: No alarm 1: Alarm
28 | Invalid | / | / | / | / | 28 | Custom alarm 6 | 0: No alarm 1: Alarm
29 | Invalid | / | / | / | / | 29 | Custom alarm 7 | 0: No alarm 1: Alarm
30 | Invalid | / | / | / | / | 30 | Custom alarm 8 | 0: No alarm 1: Alarm
31 | Array end-of-charge SOC | % | 0.1 | [0, 100] |  | 31 | Array in operation | 0: Not in operation 1: In operation | An array is regarded in operation if any inverter or PCS in the array is in operation.
32 | Array end-of-discharge SOC | % | 0.1 | [0, 100] |  | 32 | Array shut down | 0: Not shut down 1: Shut down | An array is regarded shut down only when all inverters and PCSs in the array are shut down (including all not-in-operation states, such as faulty, standby, and shut down).
33 | Dischargeable array capacity (ESS, Dezhou, Shandong) | % | 0.1 | [0, 100] | Difference between "Array SOC" and "Array end-of-discharge SOC". | 33 | 24 V Power Supply Fault | 0: No error 1: Error | If the 24V power supply in the Smart Array Controller is faulty, the value is 1. Otherwise, the value is 0. Applicable only to SmartLogger2000.
34 | Chargeable array capacity (ESS, Dezhou, Shandong) | % | 0.1 | [0, 100] | Difference between "Array end-of-charge SOC" and "Array SOC". | 34 | License Expired | 0: Not expired 1: Expired | If the license file has reached the expiration date, the license is expired. Otherwise, the license is not expired.
35 | Array SOC | % | 0.1 | [0, 100] |  | 35 | Array ESS charge | 0: Not charging/discharging 1: Charging | It is determined based on the total active power of all PCSs in the array. A negative value indicates charging.
36 | Highest real-time charge power of ESSs in array | kW | 0.001 | [0, 3.4E+38] | The power cables of ESS devices in the array are connected to different DC buses. The charge power of each DC bus is the total real-time adjustable charge power of the PCSs connected to the DC bus or the total chargeable power of battery racks, whichever is smaller. The value of this signal is the total charge power of all DC buses. | 36 | Array ESS discharge | 0: Not charging/discharging 1: Discharging | It is determined based on the total active power of all PCSs in the array. A negative value indicates discharging.
37 | Highest real-time discharge power of ESSs in array | kW | 0.001 | [0, 3.4E+38] | The power cables of ESS devices in the array are connected to different DC buses. The discharge power of each DC bus is the total real-time adjustable discharge power of the PCSs connected to the DC bus or the total dischargeable power of battery racks, whichever is smaller. The value of this signal is the total discharge power of all DC buses. | 37 | ESS PCS shutdown (ESS, Dezhou, Shandong) | 0: Not shut down 1: Shut down | All PCSs in the array are in shut down state.
38 | Total energy charged to ESSs in array | kWh | 0.01 | [0, 3.4E+38] |  | 38 | ESS PCS standby (ESS, Dezhou, Shandong) | 0: Not standby 1: Standby | All PCSs in the array are in standby mode.
39 | Total energy discharged from ESSs in array | kWh | 0.01 | [0, 3.4E+38] |  | 39 | ESS PCS faulty (ESS, Dezhou, Shandong) | 0: No error 1: Error | All PCSs in the array are faulty (shut down due to faults).
40 | Energy charged to ESSs in array today | kWh | 0.01 | [0, 3.4E+38] |  | 40 | Array fault identifier (ESS, Dezhou, Shandong) | 0: No error 1: Error | If a critical or major alarm exists in the array, the value is 1. Otherwise, the value is 0.
41 | Energy discharged from ESSs in array today | kWh | 0.01 | [0, 3.4E+38] |  | 41 | Array error identifier (ESS, Dezhou, Shandong) | 0: No error 1: Error | If a minor or warning alarm exists in the array, the value is 1. Otherwise, the value is 0.
42 | Chargeable capacity of ESSs in array | kWh | 0.001 | [0, 3.4E+38] |  | 42 | Charge locking of ESSs in array | 0: Locked 1: Unlocked | If the upper limit of charging is set to 0 for ESSs in the array, the charge function is locked. Note: Value 0 indicates the locked state.
43 | Dischargeable capacity of ESSs in array | kWh | 0.001 | [0, 3.4E+38] |  | 43 | Discharge locking of ESSs in array | 0: Locked 1: Unlocked | If the upper limit of discharging is set to 0 for ESSs in the array, the discharge function is locked. Note: Value 0 indicates the locked state.
44 | Today's power supply from grid to PCSs in array | kWh | 0.01 | [0, 3.4E+38] |  | 44 | Invalid | / | /
45 | Total power supply from grid to PCSs in array | kWh | 0.01 | [0, 3.4E+38] |  | 45 | Invalid | / | /
46 | Longest time for charging array to the end-of-charge SOC (ESS, Dezhou, Shandong) | min | 1 | [0, 65535] | Longest duration for ESS devices in the array to be charged to the end-of-charge SOC. | 46 | ESS PCS in operation | 0: Not in operation 1: In operation | At least one PCS in the array is in operation.
47 | Longest time for discharging array to the end-of-discharge SOC (ESS, Dezhou, Shandong) | min | 1 | [0, 65535] | Longest duration for ESS devices in the array to be discharged to the end-of-discharge SOC. | 47 | Invalid | / | /
48 | Rated capacity of ESSs in array | kWh | 0.001 | [0, 3.4E+38] |  | 48 | PV array PCS microgrid adaptability trigger status | 0: not triggered 1: triggered | Any PCS in the subarray is triggered by the microgrid adaptability. That is, the status is reported as triggered.
49 | Quantity of PCSs in array | / | 1 | [0, 65535] | Quantity of PCSs in the array.
50 | Quantity of available PCSs in array | / | 1 | [0, 65535] | Quantity of running PCSs in the array.
51 | Invalid | / | / | / | /
52 | Invalid | / | / | / | /
53 | Total active power of ESS PCSs | kW | 0.001 | [-3.4E+38, 3.4E+38]
54 | Total reactive power of ESS PCSs | kVar | 0.001 | [-3.4E+38, 3.4E+38]
55 | Invalid | / | / | / | /
56 | Rated ESS PCS power | kW | 0.001 | [0, 3.4E+38]
57 | Maximum reactive ESS PCS power adjustment value | kVar | 0.001 | [0, 3.4E+38] | Total maximum output inductive reactive power of PCSs in the array.
58 | Minimum reactive ESS PCS power adjustment value | kVar | 0.001 | [-3.4E+38, 0] | Total maximum output capacitive reactive power of PCSs in the array.
59 | Array black start status | / | / | / | Black start status of the array, which can be: 0: Not started 1: Preparing for black start 2: Ready for black start 3: Establishing voltage for black start 4: Voltage established for black start 5: Black start failed
60 | Array SOH | % | 0.1 | [0, 100]
61 | Array SOE | % | 0.1 | [0, 100]
62 | Total rated capacity of ESS PCSs (Ah) | Ah | 0.1 | [0, 3.4E+38] | Total rated capacity (Ah) of battery racks in the array.
63 | Lower limit of array active power adjustment | kW | 0.001 | [-3.4E+38, 0] | Maximum charge power (negative value) supported by the ESS devices in the array. The value is 0 for the PV array.
64 | Invalid | / | / | / | /
65 | Invalid | / | / | / | /
66 | Invalid | / | / | / | /
67 | Highest stable charge power of ESS | kW | 0.001 | [0, 3.4E+38] | Maximum charge rate of ESSs in the array. Compared with the value of "Highest real-time charge power of ESSs in array", the value of this signal also includes the charge power of battery racks bypassed due to full discharge.
68 | Highest stable discharge power of ESS | kW | 0.001 | [0, 3.4E+38] | Maximum discharge rate of ESSs in the array. Compared with the value of "Highest real-time discharge power of ESSs in array", the value of this signal also includes the discharge power of battery racks bypassed due to full charge.
69 | Working mode of PCSs in array | / | / | 0: PQ 1: VSG
70 | Invalid | / | / | / | /
71 | Subarray steady-state SOC | % | 0.1 | [0, 100] | Σ(SOC cluster i x SOH cluster i x Rated power cluster i)/Σ(SOH cluster i x Rated power cluster i) Note: (1) SOC cluster i, SOH cluster i, and rated energy cluster i are reported by the BCU. 2) Sum range for all running and commanded shutdown battery clusters in the subarray. 3) The capacity dimension is Ah, and the SOC dimension is %. 4) The SOC here is used for display and is calculated in real time.
72 | Steady-state chargeable capacity of the storage battery in the array | kWh | 0.001 | [0, 3.4E+38] | Σ Chargeable power cluster i Note: 1. The chargeable battery level cluster is reported by the BCU. 2) Sum range for all operating and shutdown instruction battery clusters in the subarray. 3) The rechargeable capacity is controlled and calculated in real time.
73 | Steady-state discharge capacity of the batteries in the array | kWh | 0.001 | [0, 3.4E+38] | Σ Discharging capacity cluster i Note: 1. The dischargeable capacity cluster is reported by the BCU. 2) Summation range for all running and commanded shutdown battery clusters in the subarray. 3) The discharge capacity is used for control and is calculated in real time.
74 | Invalid | / | / | / | /
75 | Invalid | / | / | / | /
76 | Invalid | / | / | / | /
77 | Current-month charge capacity of the battery in the array | kWh | 0.01 | [0, 3.4E+38]
78 | Current-month discharge capacity of batteries in the array | kWh | 0.01 | [0, 3.4E+38]
79 | Annual charging capacity of the sub-array energy storage battery | kWh | 0.01 | [0, 3.4E+38]
80 | Annual discharging capacity of the sub-array energy storage battery | kWh | 0.01 | [0, 3.4E+38]
81 | Total absorbed capacity of the sub-array PCS in the current month | kWh | 0.01 | [0, 3.4E+38]
82 | Total absorbed capacity of the sub-array PCS in the current year | kWh | 0.01 | [0, 3.4E+38]
83 | Total discharged capacity of the sub-array PCS in the current day | kWh | 0.01 | [0, 3.4E+38]
84 | Total discharged capacity of the sub-array PCS in the current month | kWh | 0.01 | [0, 3.4E+38]
85 | Total discharged capacity of the sub-array PCS in the current year | kWh | 0.01 | [0, 3.4E+38]
86 | Accumulated total discharged capacity of the sub-array PCS | kWh | 0.01 | [0, 3.4E+38]
87 | Invalid | / | / | / | /
88 | Invalid | / | / | / | /
89 | Total active power of PV array energy storage PCS (fast) | kWh | 0.01 | [0, 3.4E+38]
Note on J12: 作者: 苏安明对齐现网问题。
Note on J13: 作者: 苏安明对齐现网问题。
Note on J14: 作者: 苏安明对齐现网问题。
Note on J20: 作者: 标识删除该告警的版本

## SUN2000 V100R001CXX
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | ZVRT protection | 0: Normal 1: Protected | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | LVRT protection | 0: Normal 1: Protected
5 | PV5 voltage | V | 5 | Islanding protection | 0: Normal 1: Protected
6 | PV6 voltage | V | 6 | Inverter startup/shutdown status | 0: Shutdown 1: Startup
7 | PV1 current | A | 7 | Abnormal String 1 | 0: Normal 1: Faulty
8 | PV2 current | A | 8 | Abnormal String 2 | 0: Normal 1: Faulty
9 | PV3 current | A | 9 | Abnormal String 3 | 0: Normal 1: Faulty
10 | PV4 current | A | 10 | Abnormal String 4 | 0: Normal 1: Faulty
11 | PV5 current | A | 11 | Abnormal String 5 | 0: Normal 1: Faulty
12 | PV6 current | A | 12 | Abnormal String 6 | 0: Normal 1: Faulty
13 | AB Line voltage | V | 13 | Invalid
14 | BC Line voltage | V | 14 | Upgrade Failed | 0: Normal 1: Failed
15 | CA Line voltage | V | 15 | Flash Fault | 0: Normal 1: Faulty
16 | Phase A voltage | V | 16 | Low Insulation Resistance | 0: Normal 1: Faulty
17 | Phase B voltage | V | 17 | Abnormal Grounding | 0: Normal 1: Faulty
18 | Phase C voltage | V | 18 | Software Version Unmatch | 0: Normal 1: Faulty
19 | Phase A current | A | 19 | System Fault | 0: Normal 1: Faulty
20 | Phase B current | A | 20 | Abnormal Inverter Circuit | 0: Normal 1: Faulty
21 | Phase C current | A | 21 | Abnormal Residual Current | 0: Normal 1: Faulty
22 | Grid frequency | Hz | 22 | Cabinet Overtemperature | 0: Normal 1: Faulty
23 | Active power | kW | 23 | String 1 Reversed | 0: Normal 1: Faulty
24 | Reactive power | kVar | 24 | String 2 Reversed | 0: Normal 1: Faulty
25 | Power factor | / | 25 | String 3 Reversed | 0: Normal 1: Faulty
26 | Total input power | kW | 26 | String 4 Reversed | 0: Normal 1: Faulty
27 | Cabinet temperature | °C | 27 | String 5 Reversed | 0: Normal 1: Faulty
28 | Inverter efficiency | % | 28 | String 6 Reversed | 0: Normal 1: Faulty
29 | Daily energy yield | kWh | 29 | High DC Input Voltage | 0: Normal 1: Faulty
30 | Total energy yield | kWh | 30 | Abnormal DC Circuit | 0: Normal 1: Faulty
31 | Reduced CO2 emission | kg | 31 | Abnormal Grid Voltage | 0: Normal 1: Faulty
32 | Inverter Operating Status | / | 32 | Abnormal Grid Frequency | 0: Normal 1: Faulty
33 | Startup time | / | 33 | Abnormal Auxiliary Power | 0: Normal 1: Faulty
34 | Shutdown time | / | 34 | Invalid
|  |  | 35 | Invalid
|  |  | 36 | Abnormal SPI Communication | 0: Normal 1: Faulty
|  |  | 37 | AFCI Self-Check Failure | 0: Normal 1: Faulty
|  |  | 38 | DC Arc Fault | 0: Normal 1: Faulty
|  |  | 39 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
|  |  | 40 | On-grid
|  |  | 41 | Shutdown
|  |  | 42 | Faulty
|  |  | 43 | Normal grid connection
|  |  | 44 | Grid connection with derating due to power rationing
|  |  | 45 | Grid connection with derating due to inverter internal causes
|  |  | 46 | Normal shutdown
|  |  | 47 | Shutdown due to power rationing
|  |  | 48 | Spot-check

## SUN2000 V200R001CXX
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | ZVRT protection | 0: Normal 1: Protected | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | LVRT protection | 0: Normal 1: Protected
5 | PV5 voltage | V | 5 | Islanding protection | 0: Normal 1: Protected
6 | PV6 voltage | V | 6 | Inverter startup/shutdown status | 0: Shutdown 1: Startup
7 | PV1 current | A | 7 | Invalid
8 | PV2 current | A | 8 | Upgrade Failed | 0: Normal 1: Failed
9 | PV3 current | A | 9 | Flash Fault | 0: Normal 1: Faulty
10 | PV4 current | A | 10 | Invalid
11 | PV5 current | A | 11 | Abnormal SPI Communication | 0: Normal 1: Faulty
12 | PV6 current | A | 12 | Low Insulation Resistance | 0: Normal 1: Faulty
13 | AB Line voltage | V | 13 | Abnormal Auxiliary Power | 0: Normal 1: Faulty
14 | BC Line voltage | V | 14 | Abnormal Grounding | 0: Normal 1: Faulty
15 | CA Line voltage | V | 15 | Abnormal String 1 | 0: Normal 1: Faulty
16 | Phase A voltage | V | 16 | Abnormal String 2 | 0: Normal 1: Faulty
17 | Phase B voltage | V | 17 | Abnormal String 3 | 0: Normal 1: Faulty
18 | Phase C voltage | V | 18 | Abnormal String 4 | 0: Normal 1: Faulty
19 | Phase A current | A | 19 | Abnormal String 5 | 0: Normal 1: Faulty
20 | Phase B current | A | 20 | Abnormal String 6 | 0: Normal 1: Faulty
21 | Phase C current | A | 21 | Software Version Unmatch | 0: Normal 1: Faulty
22 | Grid frequency | Hz | 22 | System Fault | 0: Normal 1: Faulty
23 | Active power | kW | 23 | Abnormal Inverter Circuit | 0: Normal 1: Faulty
24 | Reactive power | kVar | 24 | Abnormal Residual Current | 0: Normal 1: Faulty
25 | Power factor | / | 25 | Cabinet Overtemperature | 0: Normal 1: Faulty
26 | Total input power | kW | 26 | String 1 Reversed | 0: Normal 1: Faulty
27 | Cabinet temperature | °C | 27 | String 2 Reversed | 0: Normal 1: Faulty
28 | Inverter efficiency | % | 28 | String 3 Reversed | 0: Normal 1: Faulty
29 | Daily energy yield | kWh | 29 | String 4 Reversed | 0: Normal 1: Faulty
30 | Total energy yield | kWh | 30 | String 5 Reversed | 0: Normal 1: Faulty
31 | Reduced CO2 emission | kg | 31 | String 6 Reversed | 0: Normal 1: Faulty
32 | Inverter Operating Status | / | 32 | High DC Input Voltage | 0: Normal 1: Faulty
33 | Startup time | / | 33 | Abnormal DC Circuit | 0: Normal 1: Faulty
34 | Shutdown time | / | 34 | Abnormal Grid Voltage | 0: Normal 1: Faulty
35 | Total DC input power | kWh | 35 | Abnormal Grid Frequency | 0: Normal 1: Faulty
36 | Monthly energy yield | kWh | 36 | Invalid
37 | Yearly energy yield | kWh | 37 | AFCI Self-Check Failure | 0: Normal 1: Faulty
|  |  | 38 | DC Arc Fault | 0: Normal 1: Faulty
|  |  | 39 | Invalid
|  |  | 40 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
|  |  | 41 | On-grid
|  |  | 42 | Shutdown
|  |  | 43 | Faulty
|  |  | 44 | Normal grid connection
|  |  | 45 | Grid connection with derating due to power rationing
|  |  | 46 | Grid connection with derating due to inverter internal causes
|  |  | 47 | Normal shutdown
|  |  | 48 | Shutdown due to power rationing
|  |  | 49 | Spot-check

## SUN2000 V200R002C00
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | ZVRT protection | 0: Normal 1: Protected | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | LVRT protection | 0: Normal 1: Protected
5 | PV5 voltage | V | 5 | Islanding protection | 0: Normal 1: Protected
6 | PV6 voltage | V | 6 | Inverter startup/shutdown status | 0: Shutdown 1: Startup
7 | PV7 voltage | V | 7 | Upgrade Failed | 0: Normal 1: Failed
8 | PV8 voltage | V | 8 | Flash Fault | 0: Normal 1: Faulty
9 | PV1 current | A | 9 | Fan Fault | 0: Normal 1: Faulty
10 | PV2 current | A | 10 | Abnormal SPI Communication | 0: Normal 1: Faulty
11 | PV3 current | A | 11 | Low Insulation Resistance | 0: Normal 1: Faulty
12 | PV4 current | A | 12 | AFCI Self-Check Failure | 0: Normal 1: Faulty
13 | PV5 current | A | 13 | DC Arc Fault | 0: Normal 1: Faulty
14 | PV6 current | A | 14 | Abnormal Auxiliary Power | 0: Normal 1: Faulty
15 | PV7 current | A | 15 | Islanding Protection | 0: Normal 1: Faulty
16 | PV8 current | A | 16 | Abnormal Grounding | 0: Normal 1: Faulty
17 | AB Line voltage | V | 17 | Abnormal String 1 | 0: Normal 1: Faulty
18 | BC Line voltage | V | 18 | Abnormal String 2 | 0: Normal 1: Faulty
19 | CA Line voltage | V | 19 | Abnormal String 3 | 0: Normal 1: Faulty
20 | Phase A voltage | V | 20 | Abnormal String 4 | 0: Normal 1: Faulty
21 | Phase B voltage | V | 21 | Abnormal String 5 | 0: Normal 1: Faulty
22 | Phase C voltage | V | 22 | Abnormal String 6 | 0: Normal 1: Faulty
23 | Phase A current | A | 23 | Abnormal String 7 | 0: Normal 1: Faulty
24 | Phase B current | A | 24 | Abnormal String 8 | 0: Normal 1: Faulty
25 | Phase C current | A | 25 | Software Version Unmatch | 0: Normal 1: Faulty
26 | Grid frequency | Hz | 26 | System Fault | 0: Normal 1: Faulty
27 | Active power | kW | 27 | Abnormal Inverter Circuit | 0: Normal 1: Faulty
28 | Reactive power | kVar | 28 | Abnormal Residual Current | 0: Normal 1: Faulty
29 | Power factor | / | 29 | Cabinet Overtemperature | 0: Normal 1: Faulty
30 | Total input power | kW | 30 | String 1 Reversed | 0: Normal 1: Faulty
31 | Cabinet temperature | °C | 31 | String 2 Reversed | 0: Normal 1: Faulty
32 | Inverter efficiency | % | 32 | String 3 Reversed | 0: Normal 1: Faulty
33 | Daily energy yield | kWh | 33 | String 4 Reversed | 0: Normal 1: Faulty
34 | Total energy yield | kWh | 34 | String 5 Reversed | 0: Normal 1: Faulty
35 | Reduced CO2 emission | kg | 35 | String 6 Reversed | 0: Normal 1: Faulty
36 | Inverter Operating Status | / | 36 | String 7 Reversed | 0: Normal 1: Faulty
37 | Startup time | / | 37 | String 8 Reversed | 0: Normal 1: Faulty
38 | Shutdown time | / | 38 | High DC Input Voltage | 0: Normal 1: Faulty
39 | Monthly energy yield | kWh | 39 | Abnormal DC Circuit | 0: Normal 1: Faulty
40 | Yearly energy yield | kWh | 40 | Abnormal Grid Voltage | 0: Normal 1: Faulty
|  |  | 41 | Abnormal Grid Frequency | 0: Normal 1: Faulty
|  |  | 42 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
|  |  | 43 | On-grid
|  |  | 44 | Shutdown
|  |  | 45 | Faulty
|  |  | 46 | Normal grid connection
|  |  | 47 | Grid connection with derating due to power rationing
|  |  | 48 | Grid connection with derating due to inverter internal causes
|  |  | 49 | Normal shutdown
|  |  | 50 | Shutdown due to power rationing
|  |  | 51 | Spot-check

## SUN2000 V200R002C20
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | ZVRT protection | 0: Normal 1: Protected | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | LVRT protection | 0: Normal 1: Protected
5 | PV5 voltage | V | 5 | Islanding protection | 0: Normal 1: Protected
6 | PV6 voltage | V | 6 | Inverter startup/shutdown status | 0: Shutdown 1: Startup
7 | PV7 voltage | V | 7 | Upgrade Failed | 0: Normal 1: Failed
8 | PV8 voltage | V | 8 | Flash Fault | 0: Normal 1: Faulty
9 | PV1 current | A | 9 | Abnormal SPI Communication | 0: Normal 1: Faulty
10 | PV2 current | A | 10 | Low Insulation Resistance | 0: Normal 1: Faulty
11 | PV3 current | A | 11 | AFCI Self-Check Failure | 0: Normal 1: Faulty
12 | PV4 current | A | 12 | DC Arc Fault | 0: Normal 1: Faulty
13 | PV5 current | A | 13 | Abnormal Auxiliary Power | 0: Normal 1: Faulty
14 | PV6 current | A | 14 | Abnormal Grounding | 0: Normal 1: Faulty
15 | PV7 current | A | 15 | Abnormal String 1 | 0: Normal 1: Faulty
16 | PV8 current | A | 16 | Abnormal String 2 | 0: Normal 1: Faulty
17 | AB Line voltage | V | 17 | Abnormal String 3 | 0: Normal 1: Faulty
18 | BC Line voltage | V | 18 | Abnormal String 4 | 0: Normal 1: Faulty
19 | CA Line voltage | V | 19 | Abnormal String 5 | 0: Normal 1: Faulty
20 | Phase A voltage | V | 20 | Abnormal String 6 | 0: Normal 1: Faulty
21 | Phase B voltage | V | 21 | Abnormal String 7 | 0: Normal 1: Faulty
22 | Phase C voltage | V | 22 | Abnormal String 8 | 0: Normal 1: Faulty
23 | Phase A current | A | 23 | Software Version Unmatch | 0: Normal 1: Faulty
24 | Phase B current | A | 24 | System Fault | 0: Normal 1: Faulty
25 | Phase C current | A | 25 | Abnormal Inverter Circuit | 0: Normal 1: Faulty
26 | Grid frequency | Hz | 26 | Abnormal Residual Current | 0: Normal 1: Faulty
27 | Active power | kW | 27 | Cabinet Overtemperature | 0: Normal 1: Faulty
28 | Reactive power | kVar | 28 | String 1 Reversed | 0: Normal 1: Faulty
29 | Power factor | / | 29 | String 2 Reversed | 0: Normal 1: Faulty
30 | Total input power | kW | 30 | String 3 Reversed | 0: Normal 1: Faulty
31 | Cabinet temperature | °C | 31 | String 4 Reversed | 0: Normal 1: Faulty
32 | Inverter efficiency | % | 32 | String 5 Reversed | 0: Normal 1: Faulty
33 | Daily energy yield | kWh | 33 | String 6 Reversed | 0: Normal 1: Faulty
34 | Total energy yield | kWh | 34 | String 7 Reversed | 0: Normal 1: Faulty
35 | Reduced CO2 emission | kg | 35 | String 8 Reversed | 0: Normal 1: Faulty
36 | Inverter Operating Status | / | 36 | High DC Input Voltage | 0: Normal 1: Faulty
37 | Startup time | / | 37 | Abnormal DC Circuit | 0: Normal 1: Faulty
38 | Shutdown time | / | 38 | Abnormal Grid Voltage | 0: Normal 1: Faulty
39 | Monthly energy yield | kWh | 39 | Abnormal Grid Frequency | 0: Normal 1: Faulty
40 | Yearly energy yield | kWh | 40 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
|  |  | 41 | On-grid
|  |  | 42 | Shutdown
|  |  | 43 | Faulty
|  |  | 44 | Normal grid connection
|  |  | 45 | Grid connection with derating due to power rationing
|  |  | 46 | Grid connection with derating due to inverter internal causes
|  |  | 47 | Normal shutdown
|  |  | 48 | Shutdown due to power rationing
|  |  | 49 | Spot-check

## SUN2000HA V100R001CXX
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | ZVRT protection | 0: Normal 1: Protected | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | LVRT protection | 0: Normal 1: Protected
5 | PV5 voltage | V | 5 | Islanding protection | 0: Normal 1: Protected
6 | PV6 voltage | V | 6 | Inverter startup/shutdown status | 0: Shutdown 1: Startup
7 | PV7 voltage | V | 7 | Upgrade Failed | 0: Normal 1: Failed
8 | PV8 voltage | V | 8 | Flash Fault | 0: Normal 1: Faulty
9 | PV1 current | A | 9 | Abnormal SPI Communication | 0: Normal 1: Faulty
10 | PV2 current | A | 10 | Low Insulation Resistance | 0: Normal 1: Faulty
11 | PV3 current | A | 11 | AFCI Self-Check Failure | 0: Normal 1: Faulty
12 | PV4 current | A | 12 | DC Arc Fault | 0: Normal 1: Faulty
13 | PV5 current | A | 13 | Abnormal Auxiliary Power | 0: Normal 1: Faulty
14 | PV6 current | A | 14 | Abnormal Grounding | 0: Normal 1: Faulty
15 | PV7 current | A | 15 | Abnormal String 1 | 0: Normal 1: Faulty
16 | PV8 current | A | 16 | Abnormal String 2 | 0: Normal 1: Faulty
17 | AB Line voltage | V | 17 | Abnormal String 3 | 0: Normal 1: Faulty
18 | BC Line voltage | V | 18 | Abnormal String 4 | 0: Normal 1: Faulty
19 | CA Line voltage | V | 19 | Abnormal String 5 | 0: Normal 1: Faulty
20 | Phase A voltage | V | 20 | Abnormal String 6 | 0: Normal 1: Faulty
21 | Phase B voltage | V | 21 | Abnormal String 7 | 0: Normal 1: Faulty
22 | Phase C voltage | V | 22 | Abnormal String 8 | 0: Normal 1: Faulty
23 | Phase A current | A | 23 | Software Version Unmatch | 0: Normal 1: Faulty
24 | Phase B current | A | 24 | System Fault | 0: Normal 1: Faulty
25 | Phase C current | A | 25 | Abnormal Inverter Circuit | 0: Normal 1: Faulty
26 | Grid frequency | Hz | 26 | Abnormal Residual Current | 0: Normal 1: Faulty
27 | Active power | kW | 27 | Cabinet Overtemperature | 0: Normal 1: Faulty
28 | Reactive power | kVar | 28 | String 1 Reversed | 0: Normal 1: Faulty
29 | Power factor | / | 29 | String 2 Reversed | 0: Normal 1: Faulty
30 | Total input power | kW | 30 | String 3 Reversed | 0: Normal 1: Faulty
31 | Cabinet temperature | °C | 31 | String 4 Reversed | 0: Normal 1: Faulty
32 | Inverter efficiency | % | 32 | String 5 Reversed | 0: Normal 1: Faulty
33 | Daily energy yield | kWh | 33 | String 6 Reversed | 0: Normal 1: Faulty
34 | Total energy yield | kWh | 34 | String 7 Reversed | 0: Normal 1: Faulty
35 | Reduced CO2 emission | kg | 35 | String 8 Reversed | 0: Normal 1: Faulty
36 | Inverter Operating Status | / | 36 | High DC Input Voltage | 0: Normal 1: Faulty
37 | Startup time | / | 37 | Abnormal DC Circuit | 0: Normal 1: Faulty
38 | Shutdown time | / | 38 | Abnormal Grid Voltage | 0: Normal 1: Faulty
39 | Total DC input power | kWh | 39 | Abnormal Grid Frequency | 0: Normal 1: Faulty
40 | Monthly energy yield | kWh | 40 | Abnormal PV String Connection | 0: Normal 1: Faulty
41 | Yearly energy yield | kWh | 41 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
|  |  | 42 | On-grid
|  |  | 43 | Shutdown
|  |  | 44 | Faulty
|  |  | 45 | Normal grid connection
|  |  | 46 | Grid connection with derating due to power rationing
|  |  | 47 | Grid connection with derating due to inverter internal causes
|  |  | 48 | Normal shutdown
|  |  | 49 | Shutdown due to power rationing
|  |  | 50 | Spot-check

## SUN2000 PV-12
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | Inverter startup/shutdown status | 0: Shutdown 1: Startup | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | High string input voltage | 0: Normal 1: Faulty
5 | PV5 voltage | V | 5 | DC Arc Fault | 0: Normal 1: Faulty
6 | PV6 voltage | V | 6 | String Reverse Connection | 0: Normal 1: Faulty
7 | PV7 voltage | V | 7 | String current backfeed | 0: Normal 1: Faulty
8 | PV8 voltage | V | 8 | Abnormal String Power | 0: Normal 1: Faulty
9 | PV9 voltage | V | 9 | AFCI Self-Check Failure | 0: Normal 1: Faulty
10 | PV10 voltage | V | 10 | Phase Wire Short-Circuited to PE | 0: Normal 1: Faulty
11 | PV11 voltage | V | 11 | Grid Loss | 0: Normal 1: Faulty
12 | PV12 voltage | V | 12 | Grid Undervoltage | 0: Normal 1: Faulty
13 | PV1 current | A | 13 | Grid Overvoltage | 0: Normal 1: Faulty
14 | PV2 current | A | 14 | Grid Voltage Imbalance | 0: Normal 1: Faulty
15 | PV3 current | A | 15 | Grid Overfrequency | 0: Normal 1: Faulty
16 | PV4 current | A | 16 | Grid Underfrequency | 0: Normal 1: Faulty
17 | PV5 current | A | 17 | Unstable Grid Frequency | 0: Normal 1: Faulty
18 | PV6 current | A | 18 | Output Overcurrent | 0: Normal 1: Faulty
19 | PV7 current | A | 19 | Output DC Component Overhigh | 0: Normal 1: Faulty
20 | PV8 current | A | 20 | Abnormal Residual Current | 0: Normal 1: Faulty
21 | PV9 current | A | 21 | Abnormal Grounding | 0: Normal 1: Faulty
22 | PV10 current | A | 22 | Low Insulation Resistance | 0: Normal 1: Faulty
23 | PV11 current | A | 23 | Cabinet Overtemperature | 0: Normal 1: Faulty
24 | PV12 current | A | 24 | Device Fault | 0: Normal 1: Faulty
25 | AB Line voltage | V | 25 | Upgrade Failed | 0: Normal 1: Faulty
26 | BC Line voltage | V | 26 | License Expired | 0: Normal 1: Faulty
27 | CA Line voltage | V | 27 | Faulty Monitoring Unit | 0: Normal 1: Faulty
28 | Phase A voltage | V | 28 | Faulty Power Collector | 0: Normal 1: Faulty
29 | Phase B voltage | V | 29 | Invalid | /
30 | Phase C voltage | V | 30 | Active Islanding | 0: Normal 1: Faulty
31 | Phase A current | A | 31 | Passive Islanding | 0: Normal 1: Faulty
32 | Phase B current | A | 32 | Transient AC Overvoltage | 0: Normal 1: Faulty
33 | Phase C current | A | 33 | Peripheral port short circuit | 0: Normal 1: Faulty
34 | Grid frequency | Hz | 34 | Off-grid output overload | 0: Normal 1: Faulty
35 | Active power | kW | 35 | Abnormal PV module configuration | 0: Normal 1: Faulty
36 | Reactive power | kVar | 36 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
37 | Power factor | / | 37 | On-grid
38 | Total input power | kW | 38 | Normal grid connection
39 | Cabinet temperature | ℃ | 39 | Grid connection with derating due to power rationing
40 | Inverter efficiency | % | 40 | Grid connection with derating due to inverter internal causes
41 | Daily energy yield | kWh | 41 | Normal shutdown
42 | Total energy yield | kWh | 42 | Faulty
43 | Reduced CO2 emission | kg | 43 | Shutdown due to power rationing
44 | Inverter Operating Status | / | 44 | Shutdown
45 | Startup time | / | 45 | Spot-check
46 | Shutdown time | / | 46 | Optimizer fault | 0: Normal 1: Faulty
47 | Monthly energy yield | kWh | 47 | Built-in PID operation abnormal | 0: Normal 1: Faulty
48 | Yearly energy yield | kWh | 48 | High input string voltage to ground | 0: Normal 1: Faulty
49 | Inverter Operating Status (Tianjin, China) | / | 49 | External fan abnormal | 0: Normal 1: Faulty | <-Note: | Inverter running status (Tianjin)
50 | Reserved | / | 50 | Invalid | / |  | 0: Grid-tied
51 | Reserved | / | 51 | Grid-tied/Off-grid controller abnormal | 0: Normal 1: Faulty |  | 1: Standby
52 | Reserved | / | 52 | PV String Loss | 0: Normal 1: Faulty |  | 2: Power limiting
53 | Reserved | / | 53 | Reserved | 0: Normal 1: Faulty |  | 3: Shut down (including shutdown due to faults)
54 | Reserved | / | 54 | Reserved | 0: Normal 1: Faulty
55 | Reserved | / | 55 | Reserved | 0: Normal 1: Faulty
56 | Reserved | / | 56 | Reserved | 0: Normal 1: Faulty
57 | Inverter running status (Hubei) | / | 57 | Reserved | 0: Normal 1: Faulty
|  |  | 58 | Reserved | 0: Normal 1: Faulty
|  |  | 59 | Reserved | 0: Normal 1: Faulty
|  |  | 60 | Reserved | 0: Normal 1: Faulty
|  |  | 61 | Reserved | 0: Normal 1: Faulty
|  |  | 62 | Reserved | /
|  |  | 63 | Reserved | /
|  |  | 64 | Reserved | /
|  |  | 65 | Reserved | /
|  |  | 66 | Reserved | /
|  |  | 67 | Reserved | /
|  |  | 68 | Reserved | /
|  |  | 69 | Reserved | /
|  |  | 70 | Reserved | /
|  |  | 71 | Reserved | /
|  |  | 72 | Reserved | /
|  |  | 73 | Reserved | /
|  |  | 74 | Reserved | /
|  |  | 75 | Reserved | /
|  |  | 76 | Reserved | /
|  |  | 77 | Reserved | /
|  |  | 78 | Reserved | /
|  |  | 79 | Reserved | /
|  |  | 80 | Reserved | /
|  |  | 81 | Reserved | /
|  |  | 82 | Reserved | /
|  |  | 83 | Reserved | /
|  |  | 84 | Indicates the enabling status of the high voltage ride through function. | 0: disabled; 1: enabled
|  |  | 85 | Indicates the enabling status of the bottom pressure traversal function. | 0: disabled; 1: enabled

## SUN2000 PV-14
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 input voltage | V | 1 | Communication failure | 0: No error 1: Error | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 input voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 input voltage | V | 3 | Inverter startup/shutdown status | 0: Shutdown 1: Startup | 3 | Startup/Shutdown control | 0: Shutdown 1: Startup
4 | PV4 input voltage | V | 4 | High String Voltage | 0: No error 1: Error
5 | PV5 input voltage | V | 5 | DC Arc Fault | 0: No error 1: Error
6 | PV6 input voltage | V | 6 | String Reverse Polarity | 0: No error 1: Error
7 | PV7 input voltage | V | 7 | String Backfeed | 0: No error 1: Error
8 | PV8 input voltage | V | 8 | Abnormal String Power | 0: No error 1: Error
9 | PV9 input voltage | V | 9 | AFCI Self-Check Failure | 0: No error 1: Error
10 | PV10 input voltage | V | 10 | Grid Phase Wire Short-Circuited to PE | 0: No error 1: Error
11 | PV11 input voltage | V | 11 | Grid Failure | 0: No error 1: Error
12 | PV12 input voltage | V | 12 | Grid Undervoltage | 0: No error 1: Error
13 | PV1 input current | V | 13 | Grid Overvoltage | 0: No error 1: Error
14 | PV2 input current | V | 14 | Grid Voltage Imbalance | 0: No error 1: Error
15 | PV3 input current | V | 15 | Grid Overfrequency | 0: No error 1: Error
16 | PV4 input current | V | 16 | Grid Underfrequency | 0: No error 1: Error
17 | PV5 input current | A | 17 | Unstable Grid Frequency | 0: No error 1: Error
18 | PV6 input current | A | 18 | Output Overcurrent | 0: No error 1: Error
19 | PV7 input current | A | 19 | Output DC Component Overhigh | 0: No error 1: Error
20 | PV8 input current | A | 20 | Abnormal Residual Current | 0: No error 1: Error
21 | PV9 input current | A | 21 | Abnormal Grounding | 0: No error 1: Error
22 | PV10 input current | A | 22 | Low Insulation Resistance | 0: No error 1: Error
23 | PV11 input current | A | 23 | Overtemperature | 0: No error 1: Error
24 | PV12 input current | A | 24 | Device Fault | 0: No error 1: Error
25 | A-B line voltage of grid | A | 25 | Update Failure | 0: No error 1: Error
26 | B-C line voltage of grid | A | 26 | License Expired | 0: No error 1: Error
27 | C-A line voltage of grid | A | 27 | Monitoring Unit Faulty | 0: No error 1: Error
28 | Phase A voltage of grid | A | 28 | Power Sensor Faulty | 0: No error 1: Error
29 | Phase B voltage of grid | V | 29 | Invalid | /
30 | Phase C voltage of grid | V | 30 | Active Islanding | 0: No error 1: Error
31 | Phase A current of grid | V | 31 | Passive Islanding | 0: No error 1: Error
32 | Phase B current of grid | V | 32 | Transient AC Overvoltage | 0: No error 1: Error
33 | Phase C current of grid | V | 33 | Peripheral Port Short Circuit | 0: No error 1: Error
34 | Grid frequency | V | 34 | Off-Grid Output Overload | 0: No error 1: Error
35 | Active power | A | 35 | Abnormal PV Module Configuration | 0: No error 1: Error
36 | Reactive power | A | 36 | Standby | Inverter running status 0: Other states 1: Current inverter status | <- Note: | On-grid states include On-grid at normal power, On-grid at derated power due to curtailment, and On-grid at self-derated power. Shutdown states include Shut down normally and Shut down due to curtailment.
37 | Power factor | A | 37 | Grid connection
38 | Total DC input power | Hz | 38 | On-grid at normal power
39 | Device internal temperature | kW | 39 | On-grid at derated power due to curtailment
40 | Inverter efficiency | kVar | 40 | On-grid at self-derated power
41 | Yield today | / | 41 | Shut down normally
42 | Total yield | kW | 42 | Faulty
43 | CO2 reduced | °C | 43 | Shut down due to curtailment
44 | Inverter running status | % | 44 | Shutdown
45 | Inverter startup time | kWh | 45 | Terminal test
46 | Inverter shutdown time | kWh | 46 | Optimizer Fault | 0: No error 1: Error
47 | Monthly energy yield | kg | 47 | Built-in PID Module Malfunction | 0: No error 1: Error
48 | Yearly energy yield | / | 48 | High Input String Voltage to Ground | 0: No error 1: Error
49 | Inverter running status (Tianjin) | / | 49 | Abnormal External Fan | 0: No error 1: Error
50 | Reserved | / | 50 | Invalid | /
51 | Reserved | / | 51 | Backup Box Communication Failure | 0: No error 1: Error
52 | Reserved | / | 52 | String Loss | 0: No error 1: Error
53 | Reserved | / | 53 | Reserved | 0: No error 1: Error
54 | Reserved | / | 54 | Reserved | 0: No error 1: Error
55 | Reserved | / | 55 | Reserved | 0: No error 1: Error
56 | Reserved | / | 56 | Reserved | 0: No error 1: Error
57 | Inverter running status (Hubei) | / | 57 | Reserved | 0: No error 1: Error | <- Note: | Inverter running status (Tianjin)
|  |  | 58 | Reserved | 0: No error 1: Error |  | 0: On-grid operation
|  |  | 59 | Reserved | 0: No error 1: Error |  | 1: Standby
|  |  | 60 | Reserved | 0: No error 1: Error |  | 2: Power limiting
|  |  | 61 | Reserved | 0: No error 1: Error |  | 3: Shut down (including shutdown due to faults)
|  |  | 62 | Reserved | /
|  |  | 63 | Reserved | /
|  |  | 64 | Reserved | /
|  |  | 65 | Reserved | /
|  |  | 66 | Reserved | /
|  |  | 67 | Reserved | /
|  |  | 68 | Reserved | /
|  |  | 69 | Reserved | /
|  |  | 70 | Reserved | /
|  |  | 71 | Reserved | /
|  |  | 72 | Reserved | /
|  |  | 73 | Reserved | /
|  |  | 74 | Reserved | /
|  |  | 75 | Reserved | /
|  |  | 76 | Reserved | /
|  |  | 77 | Reserved | /
|  |  | 78 | Reserved | /
|  |  | 79 | Reserved | /
|  |  | 80 | Reserved | /
|  |  | 81 | Reserved | /
|  |  | 82 | Reserved | /
|  |  | 83 | Reserved | /
|  |  | 84 | Indicates the enabling status of the high voltage ride through function. | 0: disabled; 1: enabled
|  |  | 85 | Indicates the enabling status of the bottom pressure traversal function. | 0: disabled; 1: enabled

## SUN2000 PV-18
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | Inverter startup/shutdown status | 0: Shutdown 1: Startup | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | High string input voltage | 0: Normal 1: Faulty
5 | PV5 voltage | V | 5 | DC Arc Fault | 0: Normal 1: Faulty
6 | PV6 voltage | V | 6 | String Reverse Connection | 0: Normal 1: Faulty
7 | PV7 voltage | V | 7 | String current backfeed | 0: Normal 1: Faulty
8 | PV8 voltage | V | 8 | Abnormal String Power | 0: Normal 1: Faulty
9 | PV9 voltage | V | 9 | AFCI Self-Check Failure | 0: Normal 1: Faulty
10 | PV10 voltage | V | 10 | Phase Wire Short-Circuited to PE | 0: Normal 1: Faulty
11 | PV11 voltage | V | 11 | Grid Loss | 0: Normal 1: Faulty
12 | PV12 voltage | V | 12 | Grid Undervoltage | 0: Normal 1: Faulty
13 | PV13 voltage | V | 13 | Grid Overvoltage | 0: Normal 1: Faulty
14 | PV14 voltage | V | 14 | Grid Voltage Imbalance | 0: Normal 1: Faulty
15 | PV15 voltage | V | 15 | Grid Overfrequency | 0: Normal 1: Faulty
16 | PV16 voltage | V | 16 | Grid Underfrequency | 0: Normal 1: Faulty
17 | PV17 voltage | V | 17 | Unstable Grid Frequency | 0: Normal 1: Faulty
18 | PV18 voltage | V | 18 | Output Overcurrent | 0: Normal 1: Faulty
19 | PV1 current | A | 19 | Output DC Component Overhigh | 0: Normal 1: Faulty
20 | PV2 current | A | 20 | Abnormal Residual Current | 0: Normal 1: Faulty
21 | PV3 current | A | 21 | Abnormal Grounding | 0: Normal 1: Faulty
22 | PV4 current | A | 22 | Low Insulation Resistance | 0: Normal 1: Faulty
23 | PV5 current | A | 23 | Cabinet Overtemperature | 0: Normal 1: Faulty
24 | PV6 current | A | 24 | Device Fault | 0: Normal 1: Faulty
25 | PV7 current | A | 25 | Upgrade Failed | 0: Normal 1: Faulty
26 | PV8 current | A | 26 | License Expired | 0: Normal 1: Faulty
27 | PV9 current | A | 27 | Faulty Monitoring Unit | 0: Normal 1: Faulty
28 | PV10 current | A | 28 | Faulty Power Collector | 0: Normal 1: Faulty
29 | PV11 current | A | 29 | Invalid | /
30 | PV12 current | A | 30 | Active Islanding | 0: Normal 1: Faulty
31 | PV13 current | A | 31 | Passive Islanding | 0: Normal 1: Faulty
32 | PV14 current | A | 32 | Transient AC Overvoltage | 0: Normal 1: Faulty
33 | PV15 current | A | 33 | Peripheral port short circuit | 0: Normal 1: Faulty
34 | PV16 current | A | 34 | Off-grid output overload | 0: Normal 1: Faulty
35 | PV17 current | A | 35 | Abnormal PV module configuration | 0: Normal 1: Faulty
36 | PV18 current | A | 36 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
37 | AB Line voltage | V | 37 | On-grid
38 | BC Line voltage | V | 38 | Normal grid connection
39 | CA Line voltage | V | 39 | Grid connection with derating due to power rationing
40 | Phase A voltage | V | 40 | Grid connection with derating due to inverter internal causes
41 | Phase B voltage | V | 41 | Normal shutdown
42 | Phase C voltage | V | 42 | Faulty
43 | Phase A current | A | 43 | Shutdown due to power rationing
44 | Phase B current | A | 44 | Shutdown
45 | Phase C current | A | 45 | Spot-check
46 | Grid frequency | Hz | 46 | Optimizer fault | 0: Normal 1: Faulty
47 | Active power | kW | 47 | Built-in PID operation abnormal | 0: Normal 1: Faulty
48 | Reactive power | kVar | 48 | High input string voltage to ground | 0: Normal 1: Faulty
49 | Power factor | / | 49 | External fan abnormal | 0: Normal 1: Faulty
50 | Total input power | kW | 50 | Invalid | /
51 | Cabinet temperature | ℃ | 51 | Grid-tied/Off-grid controller abnormal | 0: Normal 1: Faulty
52 | Inverter efficiency | % | 52 | PV String Loss | 0: Normal 1: Faulty
53 | Daily energy yield | kWh | 53 | Reserved | 0: Normal 1: Faulty
54 | Total energy yield | kWh | 54 | Reserved | 0: Normal 1: Faulty
55 | Reduced CO2 emission | kg | 55 | Reserved | 0: Normal 1: Faulty
56 | Inverter Operating Status | / | 56 | Reserved | 0: Normal 1: Faulty
57 | Startup time | / | 57 | Reserved | 0: Normal 1: Faulty
58 | Shutdown time | / | 58 | Reserved | 0: Normal 1: Faulty
59 | Monthly energy yield | kWh | 59 | Reserved | 0: Normal 1: Faulty
60 | Yearly energy yield | kWh | 60 | Reserved | 0: Normal 1: Faulty
61 | Inverter Operating Status (Tianjin, China) | / | 61 | Reserved | 0: Normal 1: Faulty | <-Note: | Inverter running status (Tianjin)
62 | Reserved | / | 62 | Reserved | / |  | 0: Grid-tied
63 | Reserved | / | 63 | Reserved | / |  | 1: Standby
64 | Reserved | / | 64 | Reserved | / |  | 2: Power limiting
65 | Reserved | / | 65 | Reserved | / |  | 3: Shut down (including shutdown due to faults)
66 | Reserved | / | 66 | Reserved | /
67 | Reserved | / | 67 | Reserved | /
68 | Reserved | / | 68 | Reserved | /
69 | Inverter running status (Hubei) | / | 69 | Reserved | /
|  |  | 70 | Reserved | /
|  |  | 71 | Reserved | /
|  |  | 72 | Reserved | /
|  |  | 73 | Reserved | /
|  |  | 74 | Reserved | /
|  |  | 75 | Reserved | /
|  |  | 76 | Reserved | /
|  |  | 77 | Reserved | /
|  |  | 78 | Reserved | /
|  |  | 79 | Reserved | /
|  |  | 80 | Reserved | /
|  |  | 81 | Reserved | /
|  |  | 82 | Reserved | /
|  |  | 83 | Reserved | /
|  |  | 84 | Indicates the enabling status of the high voltage ride through function. | 0: disabled; 1: enabled
|  |  | 85 | Indicates the enabling status of the bottom pressure traversal function. | 0: disabled; 1: enabled

## SUN2000 PV-20
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | Inverter startup/shutdown status | 0: Shutdown 1: Startup | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | High string input voltage | 0: Normal 1: Faulty
5 | PV5 voltage | V | 5 | DC Arc Fault | 0: Normal 1: Faulty
6 | PV6 voltage | V | 6 | String Reverse Connection | 0: Normal 1: Faulty
7 | PV7 voltage | V | 7 | String current backfeed | 0: Normal 1: Faulty
8 | PV8 voltage | V | 8 | Abnormal String Power | 0: Normal 1: Faulty
9 | PV9 voltage | V | 9 | AFCI Self-Check Failure | 0: Normal 1: Faulty
10 | PV10 voltage | V | 10 | Phase Wire Short-Circuited to PE | 0: Normal 1: Faulty
11 | PV11 voltage | V | 11 | Grid Loss | 0: Normal 1: Faulty
12 | PV12 voltage | V | 12 | Grid Undervoltage | 0: Normal 1: Faulty
13 | PV13 voltage | V | 13 | Grid Overvoltage | 0: Normal 1: Faulty
14 | PV14 voltage | V | 14 | Grid Voltage Imbalance | 0: Normal 1: Faulty
15 | PV15 voltage | V | 15 | Grid Overfrequency | 0: Normal 1: Faulty
16 | PV16 voltage | V | 16 | Grid Underfrequency | 0: Normal 1: Faulty
17 | PV17 voltage | V | 17 | Unstable Grid Frequency | 0: Normal 1: Faulty
18 | PV18 voltage | V | 18 | Output Overcurrent | 0: Normal 1: Faulty
19 | PV19 voltage | V | 19 | Output DC Component Overhigh | 0: Normal 1: Faulty
20 | PV20 voltage | V | 20 | Abnormal Residual Current | 0: Normal 1: Faulty
21 | PV1 current | A | 21 | Abnormal Grounding | 0: Normal 1: Faulty
22 | PV2 current | A | 22 | Low Insulation Resistance | 0: Normal 1: Faulty
23 | PV3 current | A | 23 | Cabinet Overtemperature | 0: Normal 1: Faulty
24 | PV4 current | A | 24 | Device Fault | 0: Normal 1: Faulty
25 | PV5 current | A | 25 | Upgrade Failed | 0: Normal 1: Faulty
26 | PV6 current | A | 26 | License Expired | 0: Normal 1: Faulty
27 | PV7 current | A | 27 | Faulty Monitoring Unit | 0: Normal 1: Faulty
28 | PV8 current | A | 28 | Faulty Power Collector | 0: Normal 1: Faulty
29 | PV9 current | A | 29 | Invalid | /
30 | PV10 current | A | 30 | Active Islanding | 0: Normal 1: Faulty
31 | PV11 current | A | 31 | Passive Islanding | 0: Normal 1: Faulty
32 | PV12 current | A | 32 | Transient AC Overvoltage | 0: Normal 1: Faulty
33 | PV13 current | A | 33 | Peripheral port short circuit | 0: Normal 1: Faulty
34 | PV14 current | A | 34 | Off-grid output overload | 0: Normal 1: Faulty
35 | PV15 current | A | 35 | Abnormal PV module configuration | 0: Normal 1: Faulty
36 | PV16 current | A | 36 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
37 | PV17 current | A | 37 | On-grid
38 | PV18 current | A | 38 | Normal grid connection
39 | PV19 current | A | 39 | Grid connection with derating due to power rationing
40 | PV20 current | A | 40 | Grid connection with derating due to inverter internal causes
41 | AB Line voltage | V | 41 | Normal shutdown
42 | BC Line voltage | V | 42 | Faulty
43 | CA Line voltage | V | 43 | Shutdown due to power rationing
44 | Phase A voltage | V | 44 | Shutdown
45 | Phase B voltage | V | 45 | Spot-check
46 | Phase C voltage | V | 46 | Optimizer fault | 0: Normal 1: Faulty
47 | Phase A current | A | 47 | Built-in PID operation abnormal | 0: Normal 1: Faulty
48 | Phase B current | A | 48 | High input string voltage to ground | 0: Normal 1: Faulty
49 | Phase C current | A | 49 | External fan abnormal | 0: Normal 1: Faulty
50 | Grid frequency | Hz | 50 | Invalid | /
51 | Active power | kW | 51 | Grid-tied/Off-grid controller abnormal | 0: Normal 1: Faulty
52 | Reactive power | kVar | 52 | PV String Loss | 0: Normal 1: Faulty
53 | Power factor | / | 53 | Reserved | 0: Normal 1: Faulty
54 | Total input power | kW | 54 | Reserved | 0: Normal 1: Faulty
55 | Cabinet temperature | ℃ | 55 | Reserved | 0: Normal 1: Faulty
56 | Inverter efficiency | % | 56 | Reserved | 0: Normal 1: Faulty
57 | Daily energy yield | kWh | 57 | Reserved | 0: Normal 1: Faulty
58 | Total energy yield | kWh | 58 | Reserved | 0: Normal 1: Faulty
59 | Reduced CO2 emission | kg | 59 | Reserved | 0: Normal 1: Faulty
60 | Inverter Operating Status | / | 60 | Reserved | 0: Normal 1: Faulty
61 | Startup time | / | 61 | Reserved | 0: Normal 1: Faulty
62 | Shutdown time | / | 62 | Reserved | /
63 | Monthly energy yield | kWh | 63 | Reserved | /
64 | Yearly energy yield | kWh | 64 | Reserved | /
65 | Inverter Operating Status (Tianjin, China) | / | 65 | Reserved | / | <-Note: | Inverter running status (Tianjin)
66 | Reserved | / | 66 | Reserved | / |  | 0: Grid-tied
67 | Reserved | / | 67 | Reserved | / |  | 1: Standby
68 | Reserved | / | 68 | Reserved | / |  | 2: Power limiting
69 | Reserved | / | 69 | Reserved | / |  | 3: Shut down (including shutdown due to faults)
70 | Reserved | / | 70 | Reserved | /
71 | Reserved | / | 71 | Reserved | /
72 | Reserved | / | 72 | Reserved | /
73 | Inverter running status (Hubei) | / | 73 | Reserved | /
|  |  | 74 | Reserved | /
|  |  | 75 | Reserved | /
|  |  | 76 | Reserved | /
|  |  | 77 | Reserved | /
|  |  | 78 | Reserved | /
|  |  | 79 | Reserved | /
|  |  | 80 | Reserved | /
|  |  | 81 | Reserved | /
|  |  | 82 | Reserved | /
|  |  | 83 | Reserved | /
|  |  | 84 | Indicates the enabling status of the high voltage ride through function. | 0: disabled; 1: enabled
|  |  | 85 | Indicates the enabling status of the bottom pressure traversal function. | 0: disabled; 1: enabled

## SUN2000 PV-21
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 3 | Inverter startup/shutdown status | 0: Shutdown 1: Startup | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 4 | High string input voltage | 0: Normal 1: Faulty
5 | PV5 voltage | V | 5 | DC Arc Fault | 0: Normal 1: Faulty
6 | PV6 voltage | V | 6 | String Reverse Connection | 0: Normal 1: Faulty
7 | PV7 voltage | V | 7 | String current backfeed | 0: Normal 1: Faulty
8 | PV8 voltage | V | 8 | Abnormal String Power | 0: Normal 1: Faulty
9 | PV9 voltage | V | 9 | AFCI Self-Check Failure | 0: Normal 1: Faulty
10 | PV10 voltage | V | 10 | Phase Wire Short-Circuited to PE | 0: Normal 1: Faulty
11 | PV11 voltage | V | 11 | Grid Loss | 0: Normal 1: Faulty
12 | PV12 voltage | V | 12 | Grid Undervoltage | 0: Normal 1: Faulty
13 | PV13 voltage | V | 13 | Grid Overvoltage | 0: Normal 1: Faulty
14 | PV14 voltage | V | 14 | Grid Voltage Imbalance | 0: Normal 1: Faulty
15 | PV15 voltage | V | 15 | Grid Overfrequency | 0: Normal 1: Faulty
16 | PV16 voltage | V | 16 | Grid Underfrequency | 0: Normal 1: Faulty
17 | PV17 voltage | V | 17 | Unstable Grid Frequency | 0: Normal 1: Faulty
18 | PV18 voltage | V | 18 | Output Overcurrent | 0: Normal 1: Faulty
19 | PV19 voltage | V | 19 | Output DC Component Overhigh | 0: Normal 1: Faulty
20 | PV20 voltage | V | 20 | Abnormal Residual Current | 0: Normal 1: Faulty
21 | PV21 voltage | V | 21 | Abnormal Grounding | 0: Normal 1: Faulty
22 | PV1 current | A | 22 | Low Insulation Resistance | 0: Normal 1: Faulty
23 | PV2 current | A | 23 | Cabinet Overtemperature | 0: Normal 1: Faulty
24 | PV3 current | A | 24 | Device Fault | 0: Normal 1: Faulty
25 | PV4 current | A | 25 | Upgrade Failed | 0: Normal 1: Faulty
26 | PV5 current | A | 26 | License Expired | 0: Normal 1: Faulty
27 | PV6 current | A | 27 | Faulty Monitoring Unit | 0: Normal 1: Faulty
28 | PV7 current | A | 28 | Faulty Power Collector | 0: Normal 1: Faulty
29 | PV8 current | A | 29 | Invalid | /
30 | PV9 current | A | 30 | Active Islanding | 0: Normal 1: Faulty
31 | PV10 current | A | 31 | Passive Islanding | 0: Normal 1: Faulty
32 | PV11 current | A | 32 | Transient AC Overvoltage | 0: Normal 1: Faulty
33 | PV12 current | A | 33 | Peripheral port short circuit | 0: Normal 1: Faulty
34 | PV13 current | A | 34 | Off-grid output overload | 0: Normal 1: Faulty
35 | PV14 current | A | 35 | Abnormal PV module configuration | 0: Normal 1: Faulty
36 | PV15 current | A | 36 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
37 | PV16 current | A | 37 | On-grid
38 | PV17 current | A | 38 | Normal grid connection
39 | PV18 current | A | 39 | Grid connection with derating due to power rationing
40 | PV19 current | A | 40 | Grid connection with derating due to inverter internal causes
41 | PV20 current | A | 41 | Normal shutdown
42 | PV21 current | A | 42 | Faulty
43 | AB Line voltage | V | 43 | Shutdown due to power rationing
44 | BC Line voltage | V | 44 | Shutdown
45 | CA Line voltage | V | 45 | Spot-check
46 | Phase A voltage | V | 46 | Optimizer fault | 0: Normal 1: Faulty
47 | Phase B voltage | V | 47 | Built-in PID operation abnormal | 0: Normal 1: Faulty
48 | Phase C voltage | V | 48 | High input string voltage to ground | 0: Normal 1: Faulty
49 | Phase A current | A | 49 | External fan abnormal | 0: Normal 1: Faulty
50 | Phase B current | A | 50 | Invalid | /
51 | Phase C current | A | 51 | Grid-tied/Off-grid controller abnormal | 0: Normal 1: Faulty
52 | 电网频率 | kVar | 52 | PV String Loss | 0: Normal 1: Faulty
53 | 有功功率 | / | 53 | Reserved | 0: Normal 1: Faulty
54 | 无功功率 | kW | 54 | Reserved | 0: Normal 1: Faulty
55 | 功率因数 | ℃ | 55 | Reserved | 0: Normal 1: Faulty
56 | DC输入总功率 | % | 56 | Reserved | 0: Normal 1: Faulty
57 | 机内温度 | kWh | 57 | Reserved | 0: Normal 1: Faulty
58 | 逆变器效率 | kWh | 58 | Reserved | 0: Normal 1: Faulty
59 | 当天发电量 | kg | 59 | Reserved | 0: Normal 1: Faulty
60 | 总发电量 | / | 60 | Reserved | 0: Normal 1: Faulty
61 | 二氧化碳减排 | / | 61 | Reserved | 0: Normal 1: Faulty
62 | 逆变器运行状态 | / | 62 | Reserved | /
63 | 逆变器开机时间 | kWh | 63 | Reserved | /
64 | 逆变器关机时间 | kWh | 64 | Reserved | /
65 | 月发电量 | / | 65 | Reserved | / | <-Note: | Inverter running status (Tianjin)
66 | 年发电量 | / | 66 | Reserved | / |  | 0: Grid-tied
67 | 逆变器运行状态（天津） | / | 67 | Reserved | / |  | 1: Standby
68 | 保留 | / | 68 | Reserved | / |  | 2: Power limiting
69 | 保留 | / | 69 | Reserved | / |  | 3: Shut down (including shutdown due to faults)
70 | 保留 | / | 70 | Reserved | /
71 | 保留 | / | 71 | Reserved | /
72 | 保留 | / | 72 | Reserved | /
73 | 保留 | / | 73 | Reserved | /
74 | 保留 |  | 74 | Reserved | /
75 | 逆变器运行状态（湖北） |  | 75 | Reserved | /
|  |  | 76 | Reserved | /
|  |  | 77 | Reserved | /
|  |  | 78 | Reserved | /
|  |  | 79 | Reserved | /
|  |  | 80 | Reserved | /
|  |  | 81 | Reserved | /
|  |  | 82 | Reserved | /
|  |  | 83 | Reserved | /
|  |  | 84 | Indicates the enabling status of the high voltage ride through function. | 0: disabled; 1: enabled
|  |  | 85 | Indicates the enabling status of the bottom pressure traversal function. | 0: disabled; 1: enabled

## SUN2000 PV-28
Telemetry |  |  |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | Precision | Range | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 0.1 | [-3276,3276] | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | V | 0.1 | [-3276,3276] | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV3 voltage | V | 0.1 | [-3276,3276] | 3 | Inverter startup/shutdown status | 0: Shutdown 1: Startup | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV4 voltage | V | 0.1 | [-3276,3276] | 4 | High string input voltage | 0: Normal 1: Faulty
5 | PV5 voltage | V | 0.1 | [-3276,3276] | 5 | DC Arc Fault | 0: Normal 1: Faulty
6 | PV6 voltage | V | 0.1 | [-3276,3276] | 6 | String Reverse Connection | 0: Normal 1: Faulty
7 | PV7 voltage | V | 0.1 | [-3276,3276] | 7 | String current backfeed | 0: Normal 1: Faulty
8 | PV8 voltage | V | 0.1 | [-3276,3276] | 8 | Abnormal String Power | 0: Normal 1: Faulty
9 | PV9 voltage | V | 0.1 | [-3276,3276] | 9 | AFCI Self-Check Failure | 0: Normal 1: Faulty
10 | PV10 voltage | V | 0.1 | [-3276,3276] | 10 | Phase Wire Short-Circuited to PE | 0: Normal 1: Faulty
11 | PV11 voltage | V | 0.1 | [-3276,3276] | 11 | Grid Loss | 0: Normal 1: Faulty
12 | PV12 voltage | V | 0.1 | [-3276,3276] | 12 | Grid Undervoltage | 0: Normal 1: Faulty
13 | PV13 voltage | V | 0.1 | [-3276,3276] | 13 | Grid Overvoltage | 0: Normal 1: Faulty
14 | PV14 voltage | V | 0.1 | [-3276,3276] | 14 | Grid Voltage Imbalance | 0: Normal 1: Faulty
15 | PV15 voltage | V | 0.1 | [-3276,3276] | 15 | Grid Overfrequency | 0: Normal 1: Faulty
16 | PV16 voltage | V | 0.1 | [-3276,3276] | 16 | Grid Underfrequency | 0: Normal 1: Faulty
17 | PV17 voltage | V | 0.1 | [-3276,3276] | 17 | Unstable Grid Frequency | 0: Normal 1: Faulty
18 | PV18 voltage | V | 0.1 | [-3276,3276] | 18 | Output Overcurrent | 0: Normal 1: Faulty
19 | PV19 voltage | V | 0.1 | [-3276,3276] | 19 | Output DC Component Overhigh | 0: Normal 1: Faulty
20 | PV20 voltage | V | 0.1 | [-3276,3276] | 20 | Abnormal Residual Current | 0: Normal 1: Faulty
21 | PV21 voltage | V | 0.1 | [-3276,3276] | 21 | Abnormal Grounding | 0: Normal 1: Faulty
22 | PV22 voltage | V | 0.1 | [-3276,3276] | 22 | Low Insulation Resistance | 0: Normal 1: Faulty
23 | PV23 voltage | V | 0.1 | [-3276,3276] | 23 | Cabinet Overtemperature | 0: Normal 1: Faulty
24 | PV24 voltage | V | 0.1 | [-3276,3276] | 24 | Device Fault | 0: Normal 1: Faulty
25 | PV25 voltage | V | 0.1 | [-3276,3276] | 25 | Upgrade Failed | 0: Normal 1: Faulty
26 | PV26 voltage | V | 0.1 | [-3276,3276] | 26 | License Expired | 0: Normal 1: Faulty
27 | PV27 voltage | V | 0.1 | [-3276,3276] | 27 | Faulty Monitoring Unit | 0: Normal 1: Faulty
28 | PV28 voltage | V | 0.1 | [-3276,3276] | 28 | Faulty Power Collector | 0: Normal 1: Faulty
29 | PV1 current | A | 0.01 | [-327,327] | 29 | Invalid | /
30 | PV2 current | A | 0.01 | [-327,327] | 30 | Active Islanding | 0: Normal 1: Faulty
31 | PV3 current | A | 0.01 | [-327,327] | 31 | Passive Islanding | 0: Normal 1: Faulty
32 | PV4 current | A | 0.01 | [-327,327] | 32 | Transient AC Overvoltage | 0: Normal 1: Faulty
33 | PV5 current | A | 0.01 | [-327,327] | 33 | Peripheral port short circuit | 0: Normal 1: Faulty
34 | PV6 current | A | 0.01 | [-327,327] | 34 | Off-grid output overload | 0: Normal 1: Faulty
35 | PV7 current | A | 0.01 | [-327,327] | 35 | Abnormal PV module configuration | 0: Normal 1: Faulty
36 | PV8 current | A | 0.01 | [-327,327] | 36 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status | <-Note: | Grid connection conditions are classified into normal connection, grid connection with derating due to power rationing, and grid connection with derating due to inverter internal causes Shutdown conditions are classified into normal shutdown and shutdown due to power rationing.
37 | PV9 current | A | 0.01 | [-327,327] | 37 | On-grid
38 | PV10 current | A | 0.01 | [-327,327] | 38 | Normal grid connection
39 | PV11 current | A | 0.01 | [-327,327] | 39 | Grid connection with derating due to power rationing
40 | PV12 current | A | 0.01 | [-327,327] | 40 | Grid connection with derating due to inverter internal causes
41 | PV13 current | A | 0.01 | [-327,327] | 41 | Normal shutdown
42 | PV14 current | A | 0.01 | [-327,327] | 42 | Faulty
43 | PV15 current | A | 0.01 | [-327,327] | 43 | Shutdown due to power rationing
44 | PV16 current | A | 0.01 | [-327,327] | 44 | Shutdown
45 | PV17 current | A | 0.01 | [-327,327] | 45 | Spot-check
46 | PV18 current | A | 0.01 | [-327,327] | 46 | Optimizer fault | 0: Normal 1: Faulty
47 | PV19 current | A | 0.01 | [-327,327] | 47 | Built-in PID operation abnormal | 0: Normal 1: Faulty
48 | PV20 current | A | 0.01 | [-327,327] | 48 | High input string voltage to ground | 0: Normal 1: Faulty
49 | PV21 current | A | 0.01 | [-327,327] | 49 | External fan abnormal | 0: Normal 1: Faulty
50 | PV22 current | A | 0.01 | [-327,327] | 50 | Battery reverse connection | 0: Normal 1: Faulty
51 | PV23 current | A | 0.01 | [-327,327] | 51 | Invalid | /
52 | PV24 current | A | 0.01 | [-327,327] | 52 | PV String Loss | 0: Normal 1: Faulty
53 | PV25 current | A | 0.01 | [-327,327] | 53 | Reserved | 0: Normal 1: Faulty
54 | PV26 current | A | 0.01 | [-327,327] | 54 | Reserved | 0: Normal 1: Faulty
55 | PV27 current | A | 0.01 | [-327,327] | 55 | Reserved | 0: Normal 1: Faulty
56 | PV28 current | A | 0.01 | [-327,327] | 56 | Reserved | 0: Normal 1: Faulty
57 | AB Line voltage | V | 0.1 | [0,6553] | 57 | Reserved | 0: Normal 1: Faulty
58 | BC Line voltage | V | 0.1 | [0,6553] | 58 | Reserved | 0: Normal 1: Faulty
59 | CA Line voltage | V | 0.1 | [0,6553] | 59 | Reserved | 0: Normal 1: Faulty
60 | Phase A voltage | V | 0.1 | [0,6553] | 60 | Reserved | 0: Normal 1: Faulty
61 | Phase B voltage | V | 0.1 | [0,6553] | 61 | Reserved | 0: Normal 1: Faulty
62 | Phase C voltage | V | 0.1 | [0,6553] | 62 | Retained | /
63 | Phase A current | A | 0.001 | [-2147483,2147483] | 63 | Retained | /
64 | Phase B current | A | 0.001 | [-2147483,2147483] | 64 | Retained | /
65 | Phase C current | A | 0.001 | [-2147483,2147483] | 65 | Retained | / | <-Note: | Inverter running status (Tianjin)
66 | Grid frequency | Hz | 0.01 | [0,655] | 66 | Retained | / |  | 0: Grid-tied
67 | Active power | kW | 0.001 | [-2147483,2147483] | 67 | Retained | / |  | 1: Standby
68 | Reactive power | kVar | 0.001 | [-2147483,2147483] | 68 | Retained | / |  | 2: Power limiting
69 | Power factor | / | 0.001 | (-1,1] | 69 | Retained | / |  | 3: Shut down (including shutdown due to faults)
70 | Total input power | kW | 0.001 | [0,4294967] | 70 | Retained | /
71 | Cabinet temperature | ℃ | 0.1 | [-3276,3276] | 71 | Retained | /
72 | Inverter efficiency | % | 0.01 | [0,100] | 72 | Retained | /
73 | Daily energy yield | kWh | 0.01 | [0,42949672] | 73 | Retained | /
74 | Total energy yield | kWh | 0.01 | [0,42949672] | 74 | Retained | /
75 | Reduced CO2 emission | kg |  |  | 75 | Retained | /
76 | Inverter Operating Status | / | / |  | 76 | Retained | /
77 | Startup time | / | / | / | 77 | Retained | /
78 | Shutdown time | / | / | / | 78 | Retained | /
79 | Monthly energy yield | kWh | 0.01 | [0,42949672] | 79 | Retained | /
80 | Yearly energy yield | kWh | 0.01 | [0,42949672] | 80 | Retained | /
81 | Inverter Operating Status (Tianjin, China) | / | / | 0: On-grid operation; 1: Standby; 2: Power limiting; 3: Shut down (including shutdown due to faults) | 81 | Retained | /
82 | Retained | / | / | / | 82 | Retained | /
83 | Retained | / | / | / | 83 | Retained | /
84 | Retained | / | / | / | 84 | Enable status of the high-voltage ride-through function | 0: disabled; 1: enabled
85 | Retained | / | / | / | 85 | Enable status of the bottom pressure ride-through function. | 0: disabled; 1: enabled
86 | Retained | / | / | /
87 | Retained | / | / | /
88 | Retained | / | / | /
89 | Inverter running status (Hubei) | / | / | 1: normal grid-tied operation; 2: The output is under control. 3: standby state; 4: out-of-service state

## SUN2000HB series
Telemetry |  |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | Range | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | AB Line voltage | V | [0,6553] | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | BC Line voltage | V | [0,6553] | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | CA Line voltage | V | [0,6553] | 3 | Inverter startup/shutdown status | 0: Shutdown 1: Startup | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | Phase A voltage | V | [0,6553] | 4 | Reserved | 0: Normal 1: Faulty
5 | Phase B voltage | V | [0,6553] | 5 | Reserved | 0: Normal 1: Faulty
6 | Phase C voltage | V | [0,6553] | 6 | Reserved | 0: Normal 1: Faulty
7 | Phase A current | A | [-327,327] | 7 | Reserved | 0: Normal 1: Faulty
8 | Phase B current | A | [-327,327] | 8 | Reserved | 0: Normal 1: Faulty
9 | Phase C current | A | [-327,327] | 9 | Reserved | 0: Normal 1: Faulty
10 | Grid frequency | Hz | [0, 655] | 10 | Phase Wire Short-Circuited to PE | 0: Normal 1: Faulty
11 | Active power | kW | [-3.4E+38, 3.4E+38] | 11 | Grid Loss | 0: Normal 1: Faulty
12 | Reactive power | kVar | [-3.4E+38, 3.4E+38] | 12 | Grid Undervoltage | 0: Normal 1: Faulty
13 | Power factor | / | (-1, 1] | 13 | Grid Overvoltage | 0: Normal 1: Faulty
14 | Total input power | kW | [-3.4E+38, 3.4E+38] | 14 | Grid Voltage Imbalance | 0: Normal 1: Faulty
15 | Cabinet temperature | ℃ | [-3276,3276] | 15 | Grid Overfrequency | 0: Normal 1: Faulty
16 | Inverter efficiency | % | [0, 100] | 16 | Grid Underfrequency | 0: Normal 1: Faulty
17 | Daily energy yield | kWh | [0, 3.4E+38] | 17 | Unstable Grid Frequency | 0: Normal 1: Faulty
18 | Total energy yield | kWh | [0, 3.4E+38] | 18 | Output Overcurrent | 0: Normal 1: Faulty
19 | Reserved | / | / | 19 | Output DC Component Overhigh | 0: Normal 1: Faulty
20 | Inverter Operating Status | / | 0x0000: standby: initializing 0x0001: standby: insulation resistance testing 0x0002: standby: irradiance detection 0x0003: standby: grid detection 0x0100: starting 0x0200: grid-connecting 0x0201: grid-connected at limited power 0x0202: grid-connected at self-derated power 0x0203: off-grid 0x0300: shut down: unexpectedly shut down 0x0301: shut down: shut down on command 0x0302: shut down: shut down via OVGR 0x0303 shut down: communication interrupted 0x0304: shut down: power limited 0x0305: shut down: manual startup required 0x0306: shut down: DC switches disconnected 0x0307: shut down: rapid shutdown 0x0308 shut down: input underpower 0x0309: shut down: NS protection 0x030A: shut down: rapid shutdown on command 0x0401: grid scheduling: cosφ-P curve 0x0402: grid scheduling: Q-U curve 0x0403: grid scheduling: PF-U curve 0x0404: grid scheduling: dry contact 0x0405: grid scheduling: Q-P curve 0x0500: ready for terminal test 0x0501: terminal testing 0x0600: inspection in progress 0X0700: AFCI testing 0X0800: I-V curve scanning 0X0900: DC input detection 0xA000: standby: no irradiation 0xA001: standby: no DC input 0xB000: communication interrupted 0xC000: loading | 20 | Abnormal Residual Current | 0: Normal 1: Faulty
21 | Startup time | / | [0, 3.4E+38] | 21 | Abnormal Grounding | 0: Normal 1: Faulty
22 | Shutdown time | / | [0, 3.4E+38] | 22 | Low Insulation Resistance | 0: Normal 1: Faulty
23 | Monthly energy yield | kWh | [0, 3.4E+38] | 23 | Cabinet Overtemperature | 0: Normal 1: Faulty
24 | Yearly energy yield | kWh | [0, 3.4E+38] | 24 | Device Fault | 0: Normal 1: Faulty
25 | Reserved | / | / | 25 | Upgrade Failed | 0: Normal 1: Faulty
26 | DC voltage | V | [0,6553] | 26 | License Expired | 0: Normal 1: Faulty
27 | DC current | A | [-327,327] | 27 | Faulty Monitoring Unit | 0: Normal 1: Faulty
28 | Invalid | / | / | 28 | Reserved | 0: Normal 1: Faulty
29 | Invalid | / | / | 29 | Reserved | 0: Normal 1: Faulty
30 | Invalid | / | / | 30 | Active Islanding | 0: Normal 1: Faulty
31 | Invalid | / | / | 31 | Passive Islanding | 0: Normal 1: Faulty
|  |  |  | 32 | Reserved | 0: Normal 1: Faulty
|  |  |  | 33 | Reserved | 0: Normal 1: Faulty
|  |  |  | 34 | Reserved | 0: Normal 1: Faulty
|  |  |  | 35 | Reserved | 0: Normal 1: Faulty
|  |  |  | 36 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status
|  |  |  | 37 | On-grid
|  |  |  | 38 | Normal grid connection
|  |  |  | 39 | Grid connection with derating due to power rationing
|  |  |  | 40 | Grid connection with derating due to inverter internal causes
|  |  |  | 41 | Normal shutdown
|  |  |  | 42 | Faulty
|  |  |  | 43 | Shutdown due to power rationing
|  |  |  | 44 | Shutdown
|  |  |  | 45 | Spot-check
|  |  |  | 46 | Reserved | 0: Normal 1: Faulty
|  |  |  | 47 | Reserved | 0: Normal 1: Faulty
|  |  |  | 48 | High input string voltage to ground | 0: Normal 1: Faulty
|  |  |  | 49 | External fan abnormal | 0: Normal 1: Faulty
|  |  |  | 50 | Reserved | 0: Normal 1: Faulty
|  |  |  | 51 | Reserved | 0: Normal 1: Faulty
|  |  |  | 52 | Reserved | 0: Normal 1: Faulty
|  |  |  | 53 | Internal Fan Abnormal | 0: Normal 1: Faulty
|  |  |  | 54 | Reserved | 0: Normal 1: Faulty
|  |  |  | 55 | Reserved | 0: Normal 1: Faulty
|  |  |  | 56 | Reserved | 0: Normal 1: Faulty
|  |  |  | 57 | Reserved | 0: Normal 1: Faulty
|  |  |  | 58 | Reserved | 0: Normal 1: Faulty
|  |  |  | 59 | Reserved | 0: Normal 1: Faulty
|  |  |  | 60 | Reserved | 0: Normal 1: Faulty
|  |  |  | 61 | Reserved | 0: Normal 1: Faulty
|  |  |  | 62 | DC Input Overvoltage | 0: Normal 1: Faulty
|  |  |  | 63 | DC Input in Reverse Polarity | 0: Normal 1: Faulty
|  |  |  | 64 | Input Short-Circuited or in Reverse Polarity | 0: Normal 1: Faulty
|  |  |  | 65 | Input Connected in Series | 0: Normal 1: Faulty
|  |  |  | 66 | DC Not Securely Connected | 0: Normal 1: Faulty
|  |  |  | 67 | Invalid Certificate | 0: Normal 1: Faulty
|  |  |  | 68 | Certificate About to Expire | 0: Normal 1: Faulty
|  |  |  | 69 | Certificate Expired | 0: Normal 1: Faulty
|  |  |  | 70 | Off-grid operation | Inverter running status 0: Other states 1: Current inverter status

## SUN8000 V100R001C00
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | PV1 voltage | V | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | PV2 voltage | A | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | PV1 current | V | 3 | ZVRT protection | 0: Normal 1: Protected | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | PV2 current | A | 4 | LVRT protection | 0: Normal 1: Protected
5 | AB Line voltage | V | 5 | Islanding protection | 0: Normal 1: Protected
6 | BC Line voltage | V | 6 | Inverter startup/shutdown status | 0: Shutdown 1: Startup
7 | CA Line voltage | V | 7 | Module Address Conflict | 0: Normal 1: Faulty
8 | Phase A current | A | 8 | Islanding Protection | 0: Normal 1: Faulty
9 | Phase B current | A | 9 | Single Inverter Running | 0: Normal 1: Faulty
10 | Phase C current | A | 10 | Low Ambient Temperature | 0: Normal 1: Faulty
11 | Active power | kW | 11 | High Ambient Humidity | 0: Normal 1: Faulty
12 | Reactive power | kVar | 12 | Heater Fault | 0: Normal 1: Faulty
13 | Power factor | / | 13 | General AC Circuit Breaker Off | 0: Normal 1: Faulty
14 | Grid frequency | Hz | 14 | Internal communication Fault | 0: Normal 1: Faulty
15 | Total input power | kW | 15 | Software Version Unmatch | 0: Normal 1: Faulty
16 | Cabinet temperature | °C | 16 | System Fault | 0: Normal 1: Faulty
17 | Inverter efficiency | % | 17 | Fan Fault | 0: Normal 1: Faulty
18 | Daily energy yield | kWh | 18 | Cabinet Overtemperature | 0: Normal 1: Faulty
19 | Total energy yield | kWh | 19 | Abnormal SPI Communication | 0: Normal 1: Faulty
20 | Reduced CO2 emission | kg | 20 | Low Insulation Resistance | 0: Normal 1: Faulty
21 | Startup time | / | 21 | SPD Faulty | 0: Normal 1: Faulty
22 | Shutdown time | / | 22 | Abnormal DC Circuit | 0: Normal 1: Faulty
23 | Inverter Operating Status | / | 23 | PV Reversed | 0: Normal 1: Faulty
|  |  | 24 | High DC Input Voltage | 0: Normal 1: Faulty
|  |  | 25 | PS Faulty Permanently | 0: Normal 1: Faulty
|  |  | 26 | Abnormal Inverter Circuit | 0: Normal 1: Faulty
|  |  | 27 | Abnormal Grid Frequency | 0: Normal 1: Faulty
|  |  | 28 | Abnormal Grid Voltage | 0: Normal 1: Faulty
|  |  | 29 | Abnormal Grounding | 0: Normal 1: Faulty
|  |  | 30 | Drive Check Failed | 0: Normal 1: Faulty
|  |  | 31 | Input Breaker Abnormal | 0: Normal 1: Faulty
|  |  | 32 | DC Circuit Breaker Off | 0: Normal 1: Faulty
|  |  | 33 | Abnormal Auxiliary Power | 0: Normal 1: Faulty
|  |  | 34 | Emergency Power-Off | 0: Normal 1: Faulty
|  |  | 35 | Cabinet Door Open | 0: Normal 1: Faulty
|  |  | 36 | Standby | Inverter Operating Status 0: Not in this status 1: Inverter present status
|  |  | 37 | On-grid
|  |  | 38 | Shutdown
|  |  | 39 | Faulty

## Modbus Power Meter
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | Phase A voltage | V | 1 | Communication failure | 0: Normal 1: Failed
2 | Phase B voltage | V
3 | Phase C voltage | V
4 | AB Line voltage | V
5 | BC Line voltage | V
6 | CA Line voltage | V
7 | Phase A current | A
8 | Phase B current | A
9 | Phase C current | A
10 | Active power | kW
11 | Reactive power | kVar
12 | Power factor | /
13 | Active electricity | kWh
14 | Reactive electricity | kVarh
15 | Apparent power | kVA
16 | Custom 1 | / | <-Note: | The names and units of these signals can be modified on the SmartLogger WebUI. The actual names and units are used by the monitoring system.
17 | Custom 2 | /
18 | Custom 3 | /
19 | Custom 4 | /
20 | Custom 5 | /
21 | Custom 6 | /
22 | Custom 7 | /
23 | Custom 8 | /
24 | Custom 9 | /
25 | Custom 10 | /
26 | Phase A active power | kW
27 | Phase B active power | kW
28 | Phase C active power | kW
29 | Total active energy | kWh
30 | Total reactive energy | kVArh
31 | Total positive active energy | kWh
32 | Total positive reactive energy | kVArh
33 | Total negative active energy | kWh
34 | Total negative reactive energy | kVArh

## DLT645 Power Meter
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | Phase A voltage | V | 1 | Communication failure | 0: Normal 1: Failed
2 | Phase B voltage | V
3 | Phase C voltage | V
4 | AB Line voltage | V
5 | BC Line voltage | V
6 | CA Line voltage | V
7 | Phase A current | A
8 | Phase B current | A
9 | Phase C current | A
10 | Active power | kW
11 | Reactive power | kVar
12 | Power factor | /
13 | Negative active electric energy | kWh
14 | Negative reactive electric energy | kVarh
15 | Positive active electric energy | kWh
16 | Positive reactive electric energy | kVarh
17 | Apparent power | kVA
18 | Electricity in positive active electricity price segment 1 | kWh
19 | Electricity in positive active electricity price segment 2 | kWh
20 | Electricity in positive active electricity price segment 3 | kWh
21 | Electricity in positive active electricity price segment 4 | kWh
22 | Electricity in negative active electricity price segment 1 | kWh
23 | Electricity in negative active electricity price segment 2 | kWh
24 | Electricity in negative active electricity price segment 3 | kWh
25 | Electricity in negative active electricity price segment 4 | kWh
26 | Total active energy | kWh
27 | Phase A active power | kW
28 | Phase B active power | kW
29 | Phase C active power | kW

## EMI
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | Wind speed | m/s | 1 | Communication failure | 0: Normal 1: Failed
2 | Wind direction | °
3 | PV module temperature | °C
4 | Ambient temperature | °C
5 | Current radiation 1 | W/m2 | <-Note: | The names and units of these signals can be modified on the WebUI of the SmartLogger, the management system is subject to the actual name and unit. (No. 7 to No. 10 are only supported by the SmartLogger2000)
6 | Daily radiation 1 | MJ/m2
7 | Current radiation 2 | W/m2
8 | Daily Radiation 2 | MJ/m2
9 | Custom 1 | /
10 | Custom 2 | /

## PID
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | Running status | / | 1 | Communication failure | 0: Normal 1: Failed
2 | Output voltage | V | 2 | PV1 reverse | 0: Normal 1: Faulty
3 | Output current | mA | 3 | Module Overtemperature | 0: Normal 1: Faulty
4 | Temperature | °C | 4 | Output Overcurrent | 0: Normal 1: Faulty
5 | PV1 input voltage | V | 5 | Grid Voltage Imbalance | 0: Normal 1: Faulty | <-Note: | PID1.0: Supported PID2.0: Not supported
6 | PV2 input voltage | V | 6 | Grid Overvoltage | 0: Normal 1: Faulty
7 | AB Line voltage | V | 7 | Grid Undervoltage | 0: Normal 1: Faulty
8 | BC Line voltage | V | 8 | Incorrect PV Mode | 0: Normal 1: Faulty
9 | CA Line voltage | V | 9 | Incorrect Wiring | 0: Normal 1: Faulty
10 | Grid frequency | Hz | 10 | Grid Loss | 0: Normal 1: Faulty
|  |  | 11 | Grid Overfrequency | 0: Normal 1: Faulty
|  |  | 12 | Grid Underfrequency | 0: Normal 1: Faulty
|  |  | 13 | Incorrect PV module type | 0: Normal 1: Faulty
|  |  | 14 | PID inductor fault | 0: Normal 1: Faulty
|  |  | 15 | PV2 Reverse | 0: Normal 1: Faulty
|  |  | 16 | Device Fault | 0: Normal 1: Faulty
|  |  | 17 | System-to-ground resistance alarm | 0: Normal 1: Faulty | <-Note: | PID1.0: Not supported PID2.0: Supported
|  |  | 18 | Invalid | /
|  |  | 19 | System-to-ground resistance warning | 0: No error 1: Error
|  |  | 20 | License Expired | 0: Not expired 1: Expired
Operating Status
[7 empty] | 0x0000 | Standby
[7 empty] | 0x0001 | Starting
[7 empty] | 0x0002 | Running
[7 empty] | 0x0003 | Shutdown
[7 empty] | 0x0004 | Idle: PV/PE standby
[7 empty] | 0x0005 | Idle: N/PE standby
[7 empty] | 0x0006 | Idle: mode switching
[7 empty] | 0x0007 | Shutdown: Command
[7 empty] | 0x0008 | Shutdown: Fault
[7 empty] | 0x0009 | Idle: inverter disconnected
[7 empty] | 0x000A | Commission: shutdown
[7 empty] | 0x000B | Commission: running

## STS-2500K
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | LV cabinet A current Ia | A | 1 | Communication failure | 0: Normal 1: Failed | 1 | LV cabinet A ACB ON | 0: ON 1: Invalid
2 | LV cabinet A current Ib | A | 2 | Transformer heavy gas | 0: Normal 1: Failed | 2 | LV cabinet A ACB OFF | 0: OFF 1: Invalid
3 | LV cabinet A current Ic | A | 3 | Transformer light gas | 0: Normal 1: Failed | 3 | Invalid
4 | LV cabinet A current Io | A | 4 | Transformer pressure valve action | 0: Normal 1: Failed | 4 | Invalid
5 | LV cabinet A voltage Ua | V | 5 | Transformer low oil level | 0: Normal 1: Failed | 5 | MV circuit breaker remote ON | 0: ON 1: Invalid
6 | LV cabinet A voltage Ub | V | 6 | Transformer high oil level | 0: Normal 1: Failed | 6 | MV circuit breaker remote OFF | 0: OFF 1: Invalid
7 | LV cabinet A voltage Uc | V | 7 | Transformer high oil temperature | 0: Normal 1: Failed | 7 | Reserved 1 | 0: ON 1: Invalid
8 | LV cabinet A voltage Uab | V | 8 | Transformer ultra-high oil temperature | 0: Normal 1: Failed | 8 | Reserved 2 | 0: OFF 1: Invalid
9 | LV cabinet A voltage Ubc | V | 9 | Reserved 1 | 0: Normal 1: Failed
10 | LV cabinet A voltage Uca | V | 10 | LV cabinet A ACB ON | 0: Off 1: On
11 | LV cabinet A active power P | kW | 11 | LV cabinet A ACB OFF | 0: On 1: Off
12 | LV cabinet A reactive power Q | kVar | 12 | LV cabinet A ACB fault tripping | 0: Normal 1: Failed
13 | LV cabinet A power factor cosφ | / | 13 | LV cabinet A ACB remote operation | 0: Local 1: Remote
14 | LV cabinet A positive active energy (kWh) | kWh | 14 | Invalid | / |  | Note: The name and unit of the standby signal can be changed on the WebUI of the SmartLogger, the management system is subject to the actual name and unit.
15 | LV cabinet A reverse active energy (kWh) | kWh | 15 | Invalid | /
16 | LV cabinet A positive reactive energy (kVArh) | kVarh | 16 | Invalid | /
17 | LV cabinet A reverse reactive energy (kVArh) | kVarh | 17 | Invalid | /
18 | Invalid |  | 18 | LV room door open | 0: Normal 1: Failed
19 | Invalid |  | 19 | HVAC of LV cabinet A faulty | 0: Normal 1: Failed
20 | Invalid |  | 20 | Invalid
21 | Invalid |  | 21 | LV room smoke alarm | 0: Normal 1: Failed
22 | Invalid |  | 22 | Transformer cabinet G2 circuit breaker ON | 0: Off 1: On
23 | Invalid |  | 23 | Transformer cabinet G2 circuit breaker OFF | 0: On 1: Off
24 | Invalid |  | 24 | Transformer cabinet G2 isolation switch ON | 0: Off 1: On
25 | Invalid |  | 25 | Transformer cabinet G2 isolation switch OFF | 0: On 1: Off
26 | Invalid |  | 26 | Transformer cabinet G2 ground switch ON | 0: Off 1: On
27 | Invalid |  | 27 | Transformer cabinet G2 ground switch OFF | 0: On 1: Off
28 | Invalid |  | 28 | Transformer cabinet G2 circuit breaker no energy storage | 0: Normal 1: Failed
29 | Invalid |  | 29 | Transformer cabinet G2 circuit breaker remote operation | 0: Local 1: Remote
30 | Invalid |  | 30 | Transformer cabinet G2 circuit breaker OFF no action | 0: Normal 1: Failed
31 | Invalid |  | 31 | Ring network cable entry cabinet G1 load switch ON | 0: Off 1: On
32 | Invalid |  | 32 | Ring network cable entry cabinet G1 load switch OFF | 0: On 1: Off
33 | Invalid |  | 33 | Ring network cable entry cabinet G1 ground switch ON | 0: Off 1: On
34 | Invalid |  | 34 | Ring network cable entry cabinet G1 ground switch OFF | 0: On 1: Off
35 | Frequency | Hz | 35 | Ring network cable outlet cabinet G3 load switch ON | 0: Off 1: On
36 | Transformer oil temperature | ℃ | 36 | Ring network cable outlet cabinet G3 load switch OFF | 0: On 1: Off
37 | Reserved 1 | / | 37 | Ring network cable outlet cabinet G3 ground switch ON | 0: Off 1: On
38 | Transformer MV side current Ia | A | 38 | Ring network cable outlet cabinet G3 ground switch OFF | 0: On 1: Off
39 | Transformer MV side current Ib | A | 39 | MV cabinet SF6 low pressure | 0: Normal 1: Failed
40 | Transformer MV side current Ic | A | 40 | MV room door open | 0: Normal 1: Failed
41 | MV room temperature | ℃ | 41 | HVAC of MV room faulty | 0: Normal 1: Failed
42 | MV room humidity | % | 42 | MV room smoke alarm | 0: Normal 1: Failed
43 | LV room temperature | ℃ | 43 | Reserved 2 | 0: Normal 1: Failed
44 | LV room humidity | % | 44 | Reserved 3 | 0: Normal 1: Failed
45 | Reserved 2 | / | 45 | Reserved 4 | 0: Normal 1: Failed
46 | Reserved 3 | / | 46 | Reserved 5 | 0: Normal 1: Failed
47 | Reserved 4 | / | 47 | Reserved 6 | 0: Normal 1: Failed
48 | Reserved 5 | / | 48 | Reserved 7 | 0: Normal 1: Failed
49 | Reserved 6 | / | 49 | Reserved 8 | 0: Normal 1: Failed
50 | Reserved 7 | / | 50 | Transformer fast disconnection protection | 0: Not actuated 1: Actuated
51 | Reserved 8 | / | 51 | Transformer overcurrent protection | 0: Not actuated 1: Actuated
52 | Reserved 9 | / | 52 | Transformer 0-sequence overcurrent protection | 0: Not actuated 1: Actuated
53 | Invalid |  | 53 | Transformer non-electrical overcurrent protection | 0: Not actuated 1: Actuated
54 | Invalid |  | 54 | MV room ultra-high temperature alarm 1 | 0: Normal 1: Failed
55 | Invalid |  | 55 | LV room ultra-high temperature alarm | 0: Normal 1: Failed
56 | Invalid |  | 56 | Reserved 9 | 0: Normal 1: Failed
57 | Invalid |  | 57 | Reserved 10 | 0: Normal 1: Failed
58 | Invalid |  | 58 | Reserved 11 | 0: Normal 1: Failed
59 | Invalid |  | 59 | Reserved 12 | 0: Normal 1: Failed
|  |  | 60 | Reserved 13 | 0: Normal 1: Failed
|  |  | 61 | Reserved 14 | 0: Normal 1: Failed
|  |  | 62 | Reserved 15 | 0: Normal 1: Failed
|  |  | 63 | Reserved 16 | 0: Normal 1: Failed
|  |  | 64 | Reserved 17 | 0: Normal 1: Failed
|  |  | 65 | Reserved 18 | 0: Normal 1: Failed

## STS-6000K
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | LV cabinet A current Ia | A | 1 | Communication failure | 0: Normal 1: Failed | 1 | LV cabinet A ACB ON | 0: ON 1: Invalid
2 | LV cabinet A current Ib | A | 2 | Transformer heavy gas | 0: Normal 1: Failed | 2 | LV cabinet A ACB OFF | 0: OFF 1: Invalid
3 | LV cabinet A current Ic | A | 3 | Transformer light gas | 0: Normal 1: Failed | 3 | LV cabinet B ACB ON | 0: ON 1: Invalid
4 | LV cabinet A current Io | A | 4 | Transformer pressure valve action | 0: Normal 1: Failed | 4 | LV cabinet B ACB OFF | 0: OFF 1: Invalid
5 | LV cabinet A voltage Ua | V | 5 | Transformer low oil level | 0: Normal 1: Failed | 5 | MV circuit breaker remote ON | 0: ON 1: Invalid
6 | LV cabinet A voltage Ub | V | 6 | Transformer high oil level | 0: Normal 1: Failed | 6 | MV circuit breaker remote OFF | 0: OFF 1: Invalid
7 | LV cabinet A voltage Uc | V | 7 | Transformer high oil temperature | 0: Normal 1: Failed | 7 | Reserved 1 | 0: ON 1: Invalid
8 | LV cabinet A voltage Uab | V | 8 | Transformer ultra-high oil temperature | 0: Normal 1: Failed | 8 | Reserved 2 | 0: OFF 1: Invalid
9 | LV cabinet A voltage Ubc | V | 9 | Reserved 1 | 0: Normal 1: Failed
10 | LV cabinet A voltage Uca | V | 10 | LV cabinet A ACB ON | 0: Off 1: On
11 | LV cabinet A active power P | kW | 11 | LV cabinet A ACB OFF | 0: On 1: Off
12 | LV cabinet A reactive power Q | kVar | 12 | LV cabinet A ACB fault tripping | 0: Normal 1: Failed
13 | LV cabinet A power factor cosφ | / | 13 | LV cabinet A ACB remote operation | 0: Local 1: Remote
14 | LV cabinet A positive active energy (kWh) | kWh | 14 | LV cabinet B ACB ON | 0: Off 1: On |  | Note: The name and unit of the standby signal can be changed on the WebUI of the SmartLogger, the management system is subject to the actual name and unit.
15 | LV cabinet A reverse active energy (kWh) | kWh | 15 | LV cabinet B ACB OFF | 0: On 1: Off
16 | LV cabinet A positive reactive energy (kVArh) | kVarh | 16 | LV cabinet B ACB fault tripping | 0: Normal 1: Failed
17 | LV cabinet A reverse reactive energy (kVArh) | kVarh | 17 | LV cabinet B ACB remote operation | 0: Local 1: Remote
18 | LV cabinet B current Ia | A | 18 | LV room door open | 0: Normal 1: Failed
19 | LV cabinet B current Ib | A | 19 | HVAC of LV cabinet A faulty | 0: Normal 1: Failed
20 | LV cabinet B current Ic | A | 20 | HVAC of LV cabinet B faulty | 0: Normal 1: Failed
21 | LV cabinet B current Io | A | 21 | LV room smoke alarm | 0: Normal 1: Failed
22 | LV cabinet B voltage Ua | V | 22 | Transformer cabinet G2 circuit breaker ON | 0: Off 1: On
23 | LV cabinet B voltage Ub | V | 23 | Transformer cabinet G2 circuit breaker OFF | 0: On 1: Off
24 | LV cabinet B voltage Uc | V | 24 | Transformer cabinet G2 isolation switch ON | 0: Off 1: On
25 | LV cabinet B voltage Uab | V | 25 | Transformer cabinet G2 isolation switch OFF | 0: On 1: Off
26 | LV cabinet B voltage Ubc | V | 26 | Transformer cabinet G2 ground switch ON | 0: Off 1: On
27 | LV cabinet B voltage Uca | V | 27 | Transformer cabinet G2 ground switch OFF | 0: On 1: Off
28 | LV cabinet B active power P | kW | 28 | Transformer cabinet G2 circuit breaker no energy storage | 0: Normal 1: Failed
29 | LV cabinet B reactive power Q | kVar | 29 | Transformer cabinet G2 circuit breaker remote operation | 0: Local 1: Remote
30 | LV cabinet B power factor cosφ | / | 30 | Transformer cabinet G2 circuit breaker OFF no action | 0: Normal 1: Failed
31 | LV cabinet B positive active energy (kWh) | kWh | 31 | Ring network cable entry cabinet G1 load switch ON | 0: Off 1: On
32 | LV cabinet B reverse active energy (kWh) | kWh | 32 | Ring network cable entry cabinet G1 load switch OFF | 0: On 1: Off
33 | LV cabinet B positive reactive energy (kVArh) | kVarh | 33 | Ring network cable entry cabinet G1 ground switch ON | 0: Off 1: On
34 | LV cabinet B reverse reactive energy (kVArh) | kVarh | 34 | Ring network cable entry cabinet G1 ground switch OFF | 0: On 1: Off
35 | Frequency | Hz | 35 | Ring network cable outlet cabinet G3 load switch ON | 0: Off 1: On
36 | Transformer oil temperature | ℃ | 36 | Ring network cable outlet cabinet G3 load switch OFF | 0: On 1: Off
37 | Reserved 1 | / | 37 | Ring network cable outlet cabinet G3 ground switch ON | 0: Off 1: On
38 | Transformer MV side current Ia | A | 38 | Ring network cable outlet cabinet G3 ground switch OFF | 0: On 1: Off
39 | Transformer MV side current Ib | A | 39 | MV cabinet SF6 low pressure | 0: Normal 1: Failed
40 | Transformer MV side current Ic | A | 40 | MV room door open | 0: Normal 1: Failed
41 | MV room temperature | ℃ | 41 | HVAC of MV room faulty | 0: Normal 1: Failed
42 | MV room humidity | % | 42 | MV room smoke alarm | 0: Normal 1: Failed
43 | LV room temperature | ℃ | 43 | Reserved 2 | 0: Normal 1: Failed
44 | LV room humidity | % | 44 | Reserved 3 | 0: Normal 1: Failed
45 | Reserved 2 | / | 45 | Reserved 4 | 0: Normal 1: Failed
46 | Reserved 3 | / | 46 | Reserved 5 | 0: Normal 1: Failed
47 | Reserved 4 | / | 47 | Reserved 6 | 0: Normal 1: Failed
48 | Reserved 5 | / | 48 | Reserved 7 | 0: Normal 1: Failed
49 | Reserved 6 | / | 49 | Reserved 8 | 0: Normal 1: Failed
50 | Reserved 7 | / | 50 | Transformer fast disconnection protection | 0: Not actuated 1: Actuated
51 | Reserved 8 | / | 51 | Transformer overcurrent protection | 0: Not actuated 1: Actuated
52 | Reserved 9 | / | 52 | Transformer 0-sequence overcurrent protection | 0: Not actuated 1: Actuated
53 | Invalid |  | 53 | Transformer non-electrical overcurrent protection | 0: Not actuated 1: Actuated
54 | Invalid |  | 54 | MV room ultra-high temperature alarm 1 | 0: Normal 1: Failed
55 | Invalid |  | 55 | LV room ultra-high temperature alarm | 0: Normal 1: Failed
56 | Invalid |  | 56 | Reserved 9 | 0: Normal 1: Failed
57 | Invalid |  | 57 | Reserved 10 | 0: Normal 1: Failed
58 | Invalid |  | 58 | Reserved 11 | 0: Normal 1: Failed
59 | Invalid |  | 59 | Reserved 12 | 0: Normal 1: Failed
|  |  | 60 | Reserved 13 | 0: Normal 1: Failed
|  |  | 61 | Reserved 14 | 0: Normal 1: Failed
|  |  | 62 | Reserved 15 | 0: Normal 1: Failed
|  |  | 63 | Reserved 16 | 0: Normal 1: Failed
|  |  | 64 | Reserved 17 | 0: Normal 1: Failed
|  |  | 65 | Reserved 18 | 0: Normal 1: Failed

## STS-3000K-H1
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | LV cabinet A current Ia | A | 1 | Communication failure | 0: Normal 1: Failed | 1 | LV cabinet A ACB ON | 0: ON 1: Invalid
2 | LV cabinet A current Ib | A | 2 | Transformer heavy gas | 0: Normal 1: Failed | 2 | LV cabinet A ACB OFF | 0: OFF 1: Invalid
3 | LV cabinet A current Ic | A | 3 | Transformer light gas | 0: Normal 1: Failed | 3 | Invalid | /
4 | LV cabinet A current Io | A | 4 | Transformer pressure valve action | 0: Normal 1: Failed | 4 | Invalid | /
5 | LV cabinet A voltage Ua | V | 5 | Transformer low oil level | 0: Normal 1: Failed | 5 | MV circuit breaker remote ON | 0: ON 1: Invalid
6 | LV cabinet A voltage Ub | V | 6 | Transformer high oil level | 0: Normal 1: Failed | 6 | MV circuit breaker remote OFF | 0: OFF 1: Invalid
7 | LV cabinet A voltage Uc | V | 7 | Transformer high oil temperature | 0: Normal 1: Failed | 7 | Reserved 1 | 0: ON 1: Invalid
8 | LV cabinet A voltage Uab | V | 8 | Transformer ultra-high oil temperature | 0: Normal 1: Failed | 8 | Reserved 2 | 0: OFF 1: Invalid
9 | LV cabinet A voltage Ubc | V | 9 | Transformer winding temperature high | 0: Normal 1: Failed
10 | LV cabinet A voltage Uca | V | 10 | LV cabinet A ACB ON | 0: Off 1: On
11 | LV cabinet A active power P | kW | 11 | LV cabinet A ACB OFF | 0: On 1: Off
12 | LV cabinet A reactive power Q | kVar | 12 | LV cabinet A ACB fault tripping | 0: Normal 1: Failed
13 | LV cabinet A power factor cosφ | / | 13 | LV cabinet A ACB remote operation | 0: Local 1: Remote
14 | LV cabinet A positive active energy (kWh) | kWh | 14 | Invalid | / |  | Note: The name and unit of the standby signal can be changed on the WebUI of the SmartLogger, the management system is subject to the actual name and unit. The gray part is optional, not the default signal
15 | LV cabinet A reverse active energy (kWh) | kWh | 15 | Invalid | /
16 | LV cabinet A positive reactive energy (kVArh) | kVarh | 16 | Invalid | /
17 | LV cabinet A reverse reactive energy (kVArh) | kVarh | 17 | Invalid | /
18 | Invalid | / | 18 | Invalid | /
19 | Invalid | / | 19 | HVAC of LV cabinet A faulty | 0: Normal 1: Failed
20 | Invalid | / | 20 | Invalid | /
21 | Invalid | / | 21 | LV room smoke alarm | 0: Normal 1: Failed
22 | Invalid | / | 22 | RMU cabinet G2 circuit breaker ON | 0: Off 1: On
23 | Invalid | / | 23 | RMU cabinet G2 circuit breaker OFF | 0: On 1: Off
24 | Invalid | / | 24 | RMU cabinet G2 disconnector ON | 0: Off 1: On
25 | Invalid | / | 25 | RMU cabinet G2 disconnector OFF | 0: On 1: Off
26 | Invalid | / | 26 | RMU cabinet G2 earthing switch ON | 0: Off 1: On
27 | Invalid | / | 27 | RMU cabinet G2 earthing switch OFF | 0: On 1: Off
28 | Invalid | / | 28 | RMU cabinet G2 circuit breaker no energy storage | 0: Normal 1: Failed
29 | Invalid | / | 29 | RMU cabinet G2 circuit breaker remote operation | 0: Local 1: Remote
30 | Invalid | / | 30 | RMU cabinet G2 circuit breaker OFF no action | 0: Normal 1: Failed
31 | Invalid | / | 31 | RMU cabinet G1 load switch ON | 0: Off 1: On
32 | Invalid | / | 32 | RMU cabinet G1 load switch OFF | 0: On 1: Off
33 | Invalid | / | 33 | RMU cabinet G1 earthing switch ON | 0: Off 1: On
34 | Invalid | / | 34 | RMU cabinet G1 earthing switch OFF | 0: On 1: Off
35 | Frequency | Hz | 35 | RMU cabinet G3 load switch ON | 0: Off 1: On
36 | Transformer oil temperature | ℃ | 36 | RMU cabinet G3 load switch OFF | 0: On 1: Off
37 | Transformer winding temperature | / | 37 | RMU cabinet G3 earthing switch ON | 0: Off 1: On
38 | Transformer MV side current Ia | A | 38 | RMU cabinet G3 earthing switch OFF | 0: On 1: Off
39 | Transformer MV side current Ib | A | 39 | RMU SF6 low pressure | 0: Normal 1: Failed
40 | Transformer MV side current Ic | A | 40 | Invalid | /
41 | MV room temperature 1 | ℃ | 41 | HVAC of MV room faulty | 0: Normal 1: Failed
42 | MV room humidity 1 | % | 42 | MV room smoke alarm | 0: Normal 1: Failed
43 | Invalid | / | 43 | Transformer ultra-high winding temperature | 0: Normal 1: Failed
44 | Invalid | / | 44 | LV cabinet A IMD warning | 0: Normal 1: Failed
45 | Outdoor ambient temperature | ℃ | 45 | LV cabinet A IMD alarm | 0: Normal 1: Failed
46 | Transformer voltage Ua (MV side) | kV | 46 | Invalid | /
47 | Transformer voltage Ub (MV side) | kV | 47 | Invalid | /
48 | Transformer voltage Uc (MV side) | kV | 48 | Smoke alarm in transformer room | 0: Normal 1: Failed
49 | Transformer active power (MV side) | kW | 49 | LV SPD fault | 0: Normal 1: Failed
50 | Transformer reactive power (MV side) | kVar | 50 | Transformer instantaneous overcurrent protection | 0: Normal 1: Failed
51 | Transformer power factor (MV side) | / | 51 | Transformer overcurrent protection | 0: Normal 1: Failed
52 | Reserved 8 | / | 52 | Transformer zero-sequence overcurrent protection | 0: Normal 1: Failed
53 | Transformer oil level | / | 53 | Transformer non-electrical protection | 0: Normal 1: Failed
54 | MV room temperature 2 | ℃ | 54 | MV room ultra-high temperature alarm 1 | 0: Normal 1: Failed
55 | MV room humidity 2 | % | 55 | Invalid | /
56 | LV cabinet A temperature | ℃ | 56 | MV room ultra-high temperature alarm 2 | 0: Normal 1: Failed
57 | LV cabinet A humidity | % | 57 | LV cabinet A ultra-high temperature alarm | 0: Normal 1: Failed
58 | Invalid | / | 58 | Invalid | /
59 | Invalid | / | 59 | Open doors of LV/MV room | 0: Normal 1: Failed
60 | Maintenance-free dehydrator breather humidity | % | 60 | EPO Operation | 0: Normal 1: Failed
61 | Transformer phase A current THD (MV side) | % | 61 | Maintenance-free dehydration breather fault | 0: Normal 1: Failed
62 | Transformer phase B current THD (MV side) | % | 62 | Maintenance-free dehydration breather heat | 0: Normal 1: Failed
63 | Transformer phase C current THD (MV side) | % | 63 | MV circuit breaker in automatic mode | 0: Normal 1: Failed
64 | Transformer frequency (MV side) | Hz | 64 | Reserved | 0: Normal 1: Failed
65 | Aux. transformer voltage Ua | V | 65 | MV room/LV room over temperature tripping | 0: Normal 1: Failed
66 | Aux. transformer voltage Ub | V | 66 | DC LV panel door open | 0: Normal 1: Failed
67 | Aux. transformer voltage Uc | V | 67 | Reserved | 0: Normal 1: Failed
68 | Aux. transformer active power | kW | 68 | Reserved | 0: Normal 1: Failed
69 | Aux. transformer reactive power | kVar | 69 | Reserved | 0: Normal 1: Failed
70 | Aux. transformer power factor | / | 70 | ESS distribution transformer 1 MCCB ON | 0: Off 1: On
71 | Aux. transformer forward active energy | kWh | 71 | ESS distribution transformer 1 heat exchange fault | 0: Normal 1: Failed
72 | Transformer phase A voltage THD (MV side) | % | 72 | ESS distribution transformer door open | 0: Normal 1: Failed
73 | Transformer phase B voltage THD (MV side) | % | 73 | ESS distribution transformer 2 MCCB ON | 0: Off 1: On
74 | Transformer phase C voltage THD (MV side) | % | 74 | ESS distribution transformer 2 heat exchange fault | 0: Normal 1: Failed
|  |  | 75 | High-configuration relay protection power loss alarm | 0: Normal 1: Failed
|  |  | 76 | Invalid | /
|  |  | 77 | Invalid | /
|  |  | 78 | Invalid | /
|  |  | 79 | Invalid | /
|  |  | 80 | Invalid | /
|  |  | 81 | Invalid | /
|  |  | 82 | Transformer action on overvoltage | 0: Normal 1: Failed
|  |  | 83 | Transformer action on undervoltage | 0: Normal 1: Failed
|  |  | 84 | Delayed automatic switch-on of transformer MV switch | 0: Normal 1: Failed
|  |  | 85 | Transformer MV switch control loop disconnection | 0: Normal 1: Failed
|  |  | 86 | Protection-caused tripping | 0: Normal 1: Failed
|  |  | 87 | Transformer zero-sequence overvoltage protection | 0: Normal 1: Failed
|  |  | 88 | MV side underfrequency protection | 0: Normal 1: Failed
|  |  | 89 | MV side overfrequency protection | 0: Normal 1: Failed
|  |  | 90 | Transformer differential protection | 0: Normal 1: Failed
|  |  | 91 | Circuit breaker fail-safe protection | 0: Normal 1: Failed
|  |  | 92 | Reserved | /
|  |  | 93 | Reserved | /
|  |  | 94 | Reserved | /
|  |  | 95 | Reserved | /
|  |  | 96 | Reserved | /
|  |  | 97 | Reserved | /

## STS-6000K-H1
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | LV cabinet A current Ia | A | 1 | Communication failure | 0: Normal 1: Failed | 1 | LV cabinet A ACB ON | 0: ON 1: Invalid
2 | LV cabinet A current Ib | A | 2 | Transformer heavy gas | 0: Normal 1: Failed | 2 | LV cabinet A ACB OFF | 0: OFF 1: Invalid
3 | LV cabinet A current Ic | A | 3 | Transformer light gas | 0: Normal 1: Failed | 3 | LV cabinet B ACB ON | 0: ON 1: Invalid
4 | LV cabinet A current Io | A | 4 | Transformer pressure valve action | 0: Normal 1: Failed | 4 | LV cabinet B ACB OFF | 0: OFF 1: Invalid
5 | LV cabinet A voltage Ua | V | 5 | Transformer low oil level | 0: Normal 1: Failed | 5 | MV circuit breaker remote ON | 0: ON 1: Invalid
6 | LV cabinet A voltage Ub | V | 6 | Transformer high oil level | 0: Normal 1: Failed | 6 | MV circuit breaker remote OFF | 0: OFF 1: Invalid
7 | LV cabinet A voltage Uc | V | 7 | Transformer high oil temperature | 0: Normal 1: Failed | 7 | Reserved 1 | 0: ON 1: Invalid
8 | LV cabinet A voltage Uab | V | 8 | Transformer ultra-high oil temperature | 0: Normal 1: Failed | 8 | Reserved 2 | 0: OFF 1: Invalid
9 | LV cabinet A voltage Ubc | V | 9 | Transformer winding temperature high | 0: Normal 1: Failed
10 | LV cabinet A voltage Uca | V | 10 | LV cabinet A ACB ON | 0: Off 1: On
11 | LV cabinet A active power P | kW | 11 | LV cabinet A ACB OFF | 0: On 1: Off
12 | LV cabinet A reactive power Q | kVar | 12 | LV cabinet A ACB fault tripping | 0: Normal 1: Failed
13 | LV cabinet A power factor cosφ | / | 13 | LV cabinet A ACB remote operation | 0: Local 1: Remote
14 | LV cabinet A positive active energy (kWh) | kWh | 14 | LV cabinet B ACB ON | 0: Normal 1: Failed |  | Note: The name and unit of the standby signal can be changed on the WebUI of the SmartLogger, the management system is subject to the actual name and unit. The gray part is optional, not the default signal
15 | LV cabinet A reverse active energy (kWh) | kWh | 15 | LV cabinet B ACB OFF | 0: Normal 1: Failed
16 | LV cabinet A positive reactive energy (kVArh) | kVarh | 16 | LV cabinet B ACB fault tripping | 0: Normal 1: Failed
17 | LV cabinet A reverse reactive energy (kVArh) | kVarh | 17 | LV cabinet B ACB remote operation | 0: Local 1: Remote
18 | LV cabinet B current Ia | A | 18 | Invalid | /
19 | LV cabinet B current Ib | A | 19 | HVAC of LV cabinet A faulty | 0: Normal 1: Failed
20 | LV cabinet B current Ic | A | 20 | HVAC of LV cabinet B faulty | 0: Normal 1: Failed
21 | LV cabinet B current Io | A | 21 | LV room smoke alarm | 0: Normal 1: Failed
22 | LV cabinet B voltage Ua | V | 22 | RMU cabinet G2 circuit breaker ON | 0: Off 1: On
23 | LV cabinet B voltage Ub | V | 23 | RMU cabinet G2 circuit breaker OFF | 0: On 1: Off
24 | LV cabinet B voltage Uc | V | 24 | RMU cabinet G2 disconnector ON | 0: Off 1: On
25 | LV cabinet B voltage Uab | V | 25 | RMU cabinet G2 disconnector OFF | 0: On 1: Off
26 | LV cabinet B voltage Ubc | V | 26 | RMU cabinet G2 earthing switch ON | 0: Off 1: On
27 | LV cabinet B voltage Uca | V | 27 | RMU cabinet G2 earthing switch OFF | 0: On 1: Off
28 | LV cabinet B active power P | kW | 28 | RMU cabinet G2 circuit breaker no energy storage | 0: Normal 1: Failed
29 | LV cabinet B reactive power Q | kVar | 29 | RMU cabinet G2 circuit breaker remote operation | 0: Local 1: Remote
30 | LV cabinet B power factor cosφ | / | 30 | RMU cabinet G2 circuit breaker OFF no action | 0: Normal 1: Failed
31 | LV cabinet B positive active energy (kWh) | kWh | 31 | RMU cabinet G1 load switch ON | 0: Off 1: On
32 | LV cabinet B reverse active energy (kWh) | kWh | 32 | RMU cabinet G1 load switch OFF | 0: On 1: Off
33 | LV cabinet B positive reactive energy (kVArh) | kVarh | 33 | RMU cabinet G1 earthing switch ON | 0: Off 1: On
34 | LV cabinet B reverse reactive energy (kVArh) | kVarh | 34 | RMU cabinet G1 earthing switch OFF | 0: On 1: Off
35 | Frequency | Hz | 35 | RMU cabinet G3 load switch ON | 0: Off 1: On
36 | Transformer oil temperature | ℃ | 36 | RMU cabinet G3 load switch OFF | 0: On 1: Off
37 | Transformer winding temperature | / | 37 | RMU cabinet G3 earthing switch ON | 0: Off 1: On
38 | Transformer MV side current Ia | A | 38 | RMU cabinet G3 earthing switch OFF | 0: On 1: Off
39 | Transformer MV side current Ib | A | 39 | RMU SF6 low pressure | 0: Normal 1: Failed
40 | Transformer MV side current Ic | A | 40 | Invalid | /
41 | MV room temperature 1 | ℃ | 41 | HVAC of MV room faulty | 0: Normal 1: Failed
42 | MV room humidity 1 | % | 42 | MV room smoke alarm | 0: Normal 1: Failed
43 | Invalid | / | 43 | Transformer ultra-high winding temperature | 0: Normal 1: Failed
44 | Invalid | / | 44 | LV cabinet A IMD warning | 0: Normal 1: Failed
45 | Outdoor ambient temperature | ℃ | 45 | LV cabinet A IMD alarm | 0: Normal 1: Failed
46 | Transformer voltage Ua(MV side) | kV | 46 | LV cabinet B IMD warning | 0: Normal 1: Failed
47 | Transformer voltage Ub(MV side) | kV | 47 | LV cabinet B IMD alarm | 0: Normal 1: Failed
48 | Transformer voltage Uc(MV side) | kV | 48 | Transformer room smoke alarm | 0: Normal 1: Failed
49 | Transformer active power(MV side) | kW | 49 | LV SPD fault | 0: Normal 1: Failed
50 | Transformer reactive power(MV side) | kVar | 50 | Transformer instantaneous overcurrent protection | 0: Normal 1: Failed
51 | Transformer power factor(MV side) | / | 51 | Transformer overcurrent protection | 0: Normal 1: Failed
52 | Reserved 8 | / | 52 | Transformer zero-sequence overcurrent protection | 0: Normal 1: Failed
53 | Transformer oil level | / | 53 | Transformer non-electrical protection | 0: Normal 1: Failed
54 | MV room temperature 2 | ℃ | 54 | MV room ultra-high temperature alarm 1 | 0: Normal 1: Failed
55 | MV room humidity 2 | % | 55 | Invalid | /
56 | LV cabinet A temperature | ℃ | 56 | MV room ultra-high temperature alarm 2 | 0: Normal 1: Failed
57 | LV cabinet A humidity | % | 57 | LV cabinet A ultra-high temperature alarm | 0: Normal 1: Failed
58 | LV cabinet B temperature | ℃ | 58 | LV cabinet B ultra-high temperature alarm | 0: Normal 1: Failed
59 | LV cabinet B humidity | % | 59 | Open doors of LV/MV room | 0: Normal 1: Failed
60 | Maintenance-free dehydrator breather humidity | % | 60 | EPO Operation | 0: Not actuated 1: Actuated
61 | Transformer phase A current THD(MV side) | % | 61 | Maintenance-free dehydration breather fault | 0: Normal 1: Failed
62 | Transformer phase B current THD(MV side) | % | 62 | Maintenance-free dehydration breather heat | 0: Normal 1: Failed
63 | Transformer phase C current THD(MV side) | % | 63 | MV circuit breaker in automatic mode | 0: Normal 1: Failed
64 | Transformer frequency(MV side) | Hz | 64 | Reserved 2 | 0: Normal 1: Failed
65 | Aux. transformer voltage Ua | V | 65 | MV room/LV room over temperature tripping | 0: Normal 1: Failed
66 | Aux. transformer voltage Ub | V | 66 | DC LV panel door open | 0: Normal 1: Failed
67 | Aux. transformer voltage Uc | V | 67 | Reserved 3 | 0: Normal 1: Failed
68 | Aux. transformer active power | kW | 68 | Reserved 4 | 0: Normal 1: Failed
69 | Aux. transformer reactive power | kVar | 69 | Reserved 5 | 0: Normal 1: Failed
70 | Aux. transformer power factor | / | 70 | ESS distribution transformer 1 MCCB ON | 0: Normal 1: Failed
71 | Aux. transformer forward active energy | kWh | 71 | ESS distribution transformer 1 heat exchange fault | 0: Off 1: On
72 | Transformer phase A voltage THD(MV side) | % | 72 | ESS distribution transformer door open | 0: Normal 1: Failed
73 | Transformer phase B voltage THD(MV side) | % | 73 | ESS distribution transformer 2 MCCB ON | 0: Normal 1: Failed
74 | Transformer phase C voltage THD(MV side) | % | 74 | ESS distribution transformer 2 heat exchange fault | 0: Off 1: On
|  |  | 75 | High-configuration relay protection power loss alarm | 0: Normal 1: Failed
|  |  | 76 | Invalid | /
|  |  | 77 | Invalid | /
|  |  | 78 | Invalid | /
|  |  | 79 | Invalid | /
|  |  | 80 | Invalid | /
|  |  | 81 | Invalid | /
|  |  | 82 | Transformer action on overvoltage | 0: Normal 1: Failed
|  |  | 83 | Transformer action on undervoltage | 0: Normal 1: Failed
|  |  | 84 | Delayed automatic switch-on of transformer MV switch | 0: Normal 1: Failed
|  |  | 85 | Transformer MV switch control loop disconnection | 0: Normal 1: Failed
|  |  | 86 | Protection-caused tripping | 0: Normal 1: Failed
|  |  | 87 | Transformer zero-sequence overvoltage protection | 0: Normal 1: Failed
|  |  | 88 | MV side underfrequency protection | 0: Normal 1: Failed
|  |  | 89 | MV side overfrequency protection | 0: Normal 1: Failed
|  |  | 90 | Transformer differential protection | 0: Normal 1: Failed
|  |  | 91 | Circuit breaker fail-safe protection | 0: Normal 1: Failed
|  |  | 92 | Reserved | 0: Normal 1: Failed
|  |  | 93 | Reserved | 0: Normal 1: Failed
|  |  | 94 | Reserved | 0: Normal 1: Failed
|  |  | 95 | Reserved | 0: Normal 1: Failed
|  |  | 96 | Reserved | 0: Normal 1: Failed
|  |  | 97 | Reserved | 0: Normal 1: Failed

## JUPITER-9000K-H0
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | LV cabinet A current Ia | A | 1 | Communication failure | 0: Normal 1: Failed | 1 | LV cabinet A ACB ON | 0: ON 1: Invalid
2 | LV cabinet A current Ib | A | 2 | Transformer heavy gas | 0: Normal 1: Failed | 2 | LV cabinet A ACB OFF | 0: OFF 1: Invalid
3 | LV cabinet A current Ic | A | 3 | Transformer light gas | 0: Normal 1: Failed | 3 | LV cabinet B ACB ON | 0: ON 1: Invalid
4 | Invalid | / | 4 | Transformer pressure valve action | 0: Normal 1: Failed | 4 | LV cabinet B ACB OFF | 0: OFF 1: Invalid
5 | Invalid | / | 5 | Transformer low oil level | 0: Normal 1: Failed | 5 | MV circuit breaker remote ON | 0: ON 1: Invalid
6 | Invalid | / | 6 | Transformer high oil level | 0: Normal 1: Failed | 6 | MV circuit breaker remote OFF | 0: OFF 1: Invalid
7 | Invalid | / | 7 | Transformer high oil temperature | 0: Normal 1: Failed | 7 | Reserved 1 | 0: ON 1: Invalid
8 | LV cabinet A voltage Uab | V | 8 | Transformer ultra-high oil temperature | 0: Normal 1: Failed | 8 | Reserved 2 | 0: OFF 1: Invalid
9 | LV cabinet A voltage Ubc | V | 9 | Transformer high winding temperature | 0: Normal 1: Failed
10 | LV cabinet A voltage Uca | V | 10 | LV cabinet A ACB ON | 0: Off 1: On
11 | LV cabinet A active power P | kW | 11 | LV cabinet A ACB OFF | 0: On 1: Off
12 | LV cabinet A reactive power Q | kVar | 12 | LV cabinet A ACB fault tripping | 0: Normal 1: Failed
13 | LV cabinet A power factor cosφ | / | 13 | LV cabinet A ACB remote operation | 0: Local 1: Remote
14 | LV cabinet A positive active energy (kWh) | kWh | 14 | LV cabinet B ACB ON | 0: Off 1: On
15 | LV cabinet A reverse active energy (kWh) | kWh | 15 | LV cabinet B ACB OFF | 0: On 1: Off
16 | LV cabinet A positive reactive energy (kVArh) | kVarh | 16 | LV cabinet B ACB fault tripping | 0: Normal 1: Failed
17 | LV cabinet A reverse reactive energy (kVArh) | kVarh | 17 | LV cabinet B ACB remote operation | 0: Local 1: Remote
18 | LV cabinet B current Ia | A | 18 | Open doors of LV room | 0: Normal 1: Failed |  | Note: The name and unit of the standby signal can be changed on the WebUI of the SmartLogger, the management system is subject to the actual name and unit. The gray part is optional, not the default signal.
19 | LV cabinet B current Ib | A | 19 | HVAC of LV cabinet A faulty | 0: Normal 1: Failed
20 | LV cabinet B current Ic | A | 20 | HVAC of LV cabinet B faulty | 0: Normal 1: Failed
21 | Invalid | / | 21 | Invalid | /
22 | Invalid | / | 22 | RMU cabinet G2 circuit breaker ON | 0: Off 1: On
23 | Invalid | / | 23 | RMU cabinet G2 circuit breaker OFF | 0: On 1: Off
24 | Invalid | / | 24 | RMU cabinet G2 disconnector ON | 0: Off 1: On
25 | LV cabinet B voltage Uab | V | 25 | RMU cabinet G2 disconnector OFF | 0: On 1: Off
26 | LV cabinet B voltage Ubc | V | 26 | RMU cabinet G2 earthing switch ON | 0: Off 1: On
27 | LV cabinet B voltage Uca | V | 27 | RMU cabinet G2 earthing switch OFF | 0: On 1: Off
28 | LV cabinet B active power P | kW | 28 | RMU cabinet G2 circuit breaker no energy storage | 0: Normal 1: Failed
29 | LV cabinet B reactive power Q | kVar | 29 | RMU cabinet G2 circuit breaker remote operation | 0: Local 1: Remote
30 | LV cabinet B power factor cosφ | / | 30 | RMU cabinet G2 circuit breaker OFF no action | 0: Normal 1: Failed
31 | LV cabinet B positive active energy (kWh) | kWh | 31 | RMU cabinet G1 load switch ON | 0: Off 1: On
32 | LV cabinet B reverse active energy (kWh) | kWh | 32 | RMU cabinet G1 load switch OFF | 0: On 1: Off
33 | LV cabinet B positive reactive energy (kVArh) | kVarh | 33 | RMU cabinet G1 earthing switch ON | 0: Off 1: On
34 | LV cabinet B reverse reactive energy (kVArh) | kVarh | 34 | RMU cabinet G1 earthing switch OFF | 0: On 1: Off
35 | Frequency | Hz | 35 | RMU cabinet G3 load switch ON | 0: Off 1: On
36 | Transformer oil temperature | ℃ | 36 | RMU cabinet G3 load switch OFF | 0: On 1: Off
37 | Transformer winding temperature | ℃ | 37 | RMU cabinet G3 earthing switch ON | 0: Off 1: On
38 | Transformer MV side current Ia | A | 38 | RMU cabinet G3 earthing switch OFF | 0: On 1: Off
39 | Transformer MV side current Ib | A | 39 | RMU SF6 low pressure | 0: Normal 1: Failed
40 | Transformer MV side current Ic | A | 40 | Open doors of MV room | 0: Normal 1: Failed
41 | MV room temperature | ℃ | 41 | HVAC of MV room faulty | 0: Normal 1: Failed
42 | MV room humidity | % | 42 | Invalid | /
43 | Invalid | / | 43 | Transformer ultra-high winding temperature | 0: Normal 1: Failed
44 | Invalid | / | 44 | Invalid
45 | Invalid | / | 45 | LV cabinet A IMD alarm | 0: Normal 1: Failed
46 | Invalid | / | 46 | Invalid
47 | Invalid | / | 47 | LV cabinet B IMD alarm | 0: Normal 1: Failed
48 | Invalid | / | 48 | Invalid | /
49 | Invalid | / | 49 | Invalid | /
50 | Invalid | / | 50 | Transformer instantaneous overcurrent protection | 0: Normal 1: Failed
51 | Invalid | / | 51 | Transformer overcurrent protection | 0: Normal 1: Failed
52 | Invalid | / | 52 | Transformer zero-sequence overcurrent protection | 0: Normal 1: Failed
53 | Invalid | / | 53 | Transformer non-electrical protection | 0: Normal 1: Failed
54 | Invalid | / | 54 | High temperature alarm of MV room | 0: Normal 1: Failed
55 | Invalid | / | 55 | Invalid | /
56 | LV cabinet A temperature | ℃ | 56 | Invalid | /
57 | LV cabinet A humidity | % | 57 | LV cabinet A high temperature alarm | 0: Normal 1: Failed
58 | LV cabinet B temperature | ℃ | 58 | LV cabinet B high temperature alarm | 0: Normal 1: Failed
59 | LV cabinet B humidity | % | 59 | Invalid | /
60 | Maintenance-free dehydrator breather humidity | % | 60 | EPO Operation | 0: Not actuated 1: Actuated
61 | Transformer MV side THD of Ia | % | 61 | Maintenance-free hygroscopic fault | 0: Normal 1: Failed
62 | Transformer MV side THD of Ib | % | 62 | Maintenance-free hygroscopic start heating | 0: Normal 1: Failed
63 | Transformer MV side THD of Ic | % | 63 | Circuit Breaker auto-mode of cabinet G2 | 0: Normal 1: Failed
64 | Transformer frequency(MV side) | Hz | 64 | Invalid | /
65 | Aux. Transformer voltage Ua/Aux. Transformer voltage U | V | 65 | Invalid | /
66 | Aux. Transformer voltage Ub | V | 66 | DC LV panel door open | 0: Normal 1: Failed
67 | Aux. Transformer voltage Uc | V | 67 | Invalid | /
68 | Aux. Transformer active power P | kW | 68 | Invalid | /
69 | Aux. Transformer reactive power Q | kVar | 69 | Invalid | /
70 | Aux. Transformer power factor cosφ | / | 70 | ESS distribution transformer 1 MCCB ON | 0: Off 1: On
71 | Aux. Transformer positive active energy (kWh) | kWh | 71 | ESS distribution transformer 1 heat exchange fault | 0: Normal 1: Failed
72 | Transformer MV side THD of Ua | % | 72 | ESS distribution transformer door open | 0: Normal 1: Failed
73 | Transformer MV side THD of Ub | % | 73 | ESS distribution transformer 2 MCCB ON | 0: Off 1: On
74 | Transformer MV side THD of Uc | % | 74 | ESS distribution transformer 2 heat exchange fault | 0: Normal 1: Failed
75 | Invalid | / | 75 | Invalid | /
76 | Invalid | / | 76 | LV room smoke alarm 1 | 0: Normal 1: Failed
77 | Invalid | / | 77 | LV room smoke alarm 2 | 0: Normal 1: Failed
78 | Invalid | / | 78 | LV cabinet A SPD fault | 0: Normal 1: Failed
79 | Transformer MV side active power P | kW | 79 | LV cabinet B SPD fault | 0: Normal 1: Failed
80 | Transformer MV side reactive power Q | kVar | 80 | MV room smoke alarm 1 | 0: Normal 1: Failed
81 | Transformer MV side power factor cosφ | / | 81 | MV room smoke alarm 2 | 0: Normal 1: Failed
82 | Aux. Transformer reverse active energy (kWh) | kWh | 82 | Transformer overvoltage action | 0: Normal 1: Failed
83 | Aux. Transformer positive reactive energy (kVArh) | kVarh | 83 | Transformer action on undervoltage | 0: Normal 1: Failed
84 | Aux. Transformer reverse reactive energy (kVArh) | kVarh | 84 | Delayed automatic switch-on of transformer MV switch | 0: Normal 1: Failed
85 | Aux. Transformer Frequency | Hz | 85 | Transformer MV switch control loop disconnection | 0: Normal 1: Failed
86 | Aux. Transformer current Ia/Aux. Transformer current I | A | 86 | Protection-caused tripping | 0: Normal 1: Failed
87 | Aux. Transformer current Ib | A | 87 | Transformer zero-sequence overvoltage protection | 0: Normal 1: Failed
88 | Aux. Transformer current Ic | A | 88 | MV side under-frequency action | 0: Normal 1: Failed
89 | Transformer MV side voltage Uab | kV | 89 | MV side over-frequency action | 0: Normal 1: Failed
90 | Transformer MV side voltage Ubc | kV | 90 | Transformer differential protection | 0: Normal 1: Failed
91 | Transformer MV side voltage Uca | kV | 91 | Circuit Breaker failure protection | 0: Normal 1: Failed
|  |  | 92 | Invalid | /
|  |  | 93 | Invalid | /
|  |  | 94 | Invalid | /
|  |  | 95 | Invalid | /
|  |  | 96 | Invalid | /
|  |  | 97 | Invalid | /
|  |  | 98 | Aux. circuit SPD fault | 0: Normal 1: Failed
|  |  | 99 | UPS AC power failure | 0: Normal 1: Failed
|  |  | 100 | UPS-associated alarm | 0: Normal 1: Failed
|  |  | 101 | LV room smoke sensor fault | 0: Normal 1: Failed
|  |  | 102 | High-configuration relay protection power loss alarm | 0: Normal 1: Failed
|  |  | 103 | ESS distribution transformer 3 MCCB ON | 0: Off 1: On
|  |  | 104 | ESS distribution transformer 3 heat exchange fault | 0: Normal 1: Failed
|  |  | 105 | ESS distribution transformer 4 MCCB ON | 0: Off 1: On
|  |  | 106 | ESS distribution transformer 4 heat exchange fault | 0: Normal 1: Failed
|  |  | 107 | Reserved 1 | 0: Normal 1: Failed
|  |  | 108 | Reserved 2 | 0: Normal 1: Failed
|  |  | 109 | Reserved 3 | 0: Normal 1: Failed
|  |  | 110 | Reserved 4 | 0: Normal 1: Failed
|  |  | 111 | Reserved 5 | 0: Normal 1: Failed
|  |  | 112 | Reserved 6 | 0: Normal 1: Failed
|  |  | 113 | Reserved 7 | 0: Normal 1: Failed
|  |  | 114 | Reserved 8 | 0: Normal 1: Failed
|  |  | 115 | Reserved 9 | 0: Normal 1: Failed
|  |  | 116 | Reserved 10 | 0: Normal 1: Failed
|  |  | 117 | Reserved 11 | 0: Normal 1: Failed
|  |  | 118 | Reserved 12 | 0: Normal 1: Failed
|  |  | 119 | LV cabinet A tripping due to high temperature | 0: Normal 1: Failed
|  |  | 120 | LV cabinet B tripping due to high temperature | 0: Normal 1: Failed
|  |  | 121 | MV room overtemperature tripping | 0: Normal 1: Failed
|  |  | 122 | LV room double smoke sensor tripping | 0: Normal 1: Failed
|  |  | 123 | MV room double smoke sensor tripping | 0: Normal 1: Failed
|  |  | 124 | Invalid | /
|  |  | 125 | Invalid | /
|  |  | 126 | Invalid | /
|  |  | 127 | Invalid | /
|  |  | 128 | Invalid | /
|  |  | 129 | Invalid | /
|  |  | 130 | MV room smoke sensor fault | 0: Normal 1: Failed
|  |  | 131 | G1 cabinet short-circuit indicator alarm | 0: Normal 1: Failed
|  |  | 132 | G3 cabinet short-circuit indicator alarm | 0: Normal 1: Failed
|  |  | 133 | Remote mode of load switch of cabinet G1 | 0: Normal 1: Failed
|  |  | 134 | Remote mode of load switch of cabinet G3 | 0: Normal 1: Failed
|  |  | 135 | LV room side-door open | 0: Normal 1: Failed
|  |  | 136 | Reserved 13
|  |  | 137 | Reserved 14
|  |  | 138 | Reserved 15 | 0: Normal 1: Failed
|  |  | 139 | Reserved 16 | 0: Normal 1: Failed

## JUPITER-3000K-H1
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | LV cabinet A current Ia | A | 1 | Communication failure | 0: Normal 1: Failed | 1 | LV cabinet A ACB ON | 0: ON 1: Invalid
2 | LV cabinet A current Ib | A | 2 | Transformer heavy gas | 0: Normal 1: Failed | 2 | LV cabinet A ACB OFF | 0: OFF 1: Invalid
3 | LV cabinet A current Ic | A | 3 | Transformer light gas | 0: Normal 1: Failed | 3 | Invalid | /
4 | Invalid | / | 4 | Transformer pressure valve action | 0: Normal 1: Failed | 4 | Invalid | /
5 | Invalid | / | 5 | Transformer low oil level | 0: Normal 1: Failed | 5 | MV circuit breaker remote ON | 0: ON 1: Invalid
6 | Invalid | / | 6 | Transformer high oil level | 0: Normal 1: Failed | 6 | MV circuit breaker remote OFF | 0: OFF 1: Invalid
7 | Invalid | / | 7 | Transformer high oil temperature | 0: Normal 1: Failed | 7 | Reserved 1 | 0: ON 1: Invalid
8 | LV cabinet A voltage Uab | V | 8 | Transformer ultra-high oil temperature | 0: Normal 1: Failed | 8 | Reserved 2 | 0: OFF 1: Invalid
9 | LV cabinet A voltage Ubc | V | 9 | Transformer high winding temperature | 0: Normal 1: Failed
10 | LV cabinet A voltage Uca | V | 10 | LV cabinet A ACB ON | 0: Off 1: On
11 | LV cabinet A active power P | kW | 11 | LV cabinet A ACB OFF | 0: On 1: Off
12 | LV cabinet A reactive power Q | kVar | 12 | LV cabinet A ACB fault tripping | 0: Normal 1: Failed
13 | LV cabinet A power factor cosφ | / | 13 | LV cabinet A ACB remote operation | 0: Local 1: Remote
14 | LV cabinet A positive active energy (kWh) | kWh | 14 | Invalid | /
15 | LV cabinet A reverse active energy (kWh) | kWh | 15 | Invalid | /
16 | LV cabinet A positive reactive energy (kVArh) | kVarh | 16 | Invalid | /
17 | LV cabinet A reverse reactive energy (kVArh) | kVarh | 17 | Invalid | /
18 | Invalid | / | 18 | Open doors of LV room | 0: Normal 1: Failed |  | Note: The name and unit of the standby signal can be changed on the WebUI of the SmartLogger, the management system is subject to the actual name and unit. The gray part is optional, not the default signal.
19 | Invalid | / | 19 | HVAC of LV cabinet A faulty | 0: Normal 1: Failed
20 | Invalid | / | 20 | Invalid | /
21 | Invalid | / | 21 | Invalid | /
22 | Invalid | / | 22 | RMU cabinet G2 circuit breaker ON | 0: Off 1: On
23 | Invalid | / | 23 | RMU cabinet G2 circuit breaker OFF | 0: On 1: Off
24 | Invalid | / | 24 | RMU cabinet G2 disconnector ON | 0: Off 1: On
25 | Invalid | / | 25 | RMU cabinet G2 disconnector OFF | 0: On 1: Off
26 | Invalid | / | 26 | RMU cabinet G2 earthing switch ON | 0: Off 1: On
27 | Invalid | / | 27 | RMU cabinet G2 earthing switch OFF | 0: On 1: Off
28 | Invalid | / | 28 | RMU cabinet G2 circuit breaker no energy storage | 0: Normal 1: Failed
29 | Invalid | / | 29 | RMU cabinet G2 circuit breaker remote operation | 0: Local 1: Remote
30 | Invalid | / | 30 | RMU cabinet G2 circuit breaker OFF no action | 0: Normal 1: Failed
31 | Invalid | / | 31 | RMU cabinet G1 load switch ON | 0: Off 1: On
32 | Invalid | / | 32 | RMU cabinet G1 load switch OFF | 0: On 1: Off
33 | Invalid | / | 33 | RMU cabinet G1 earthing switch ON | 0: Off 1: On
34 | Invalid | / | 34 | RMU cabinet G1 earthing switch OFF | 0: On 1: Off
35 | Frequency | Hz | 35 | RMU cabinet G3 load switch ON | 0: Off 1: On
36 | Transformer oil temperature | ℃ | 36 | RMU cabinet G3 load switch OFF | 0: On 1: Off
37 | Transformer winding temperature | ℃ | 37 | RMU cabinet G3 earthing switch ON | 0: Off 1: On
38 | Transformer MV side current Ia | A | 38 | RMU cabinet G3 earthing switch OFF | 0: On 1: Off
39 | Transformer MV side current Ib | A | 39 | RMU SF6 low pressure | 0: Normal 1: Failed
40 | Transformer MV side current Ic | A | 40 | Open doors of MV room | 0: Normal 1: Failed
41 | MV room temperature | ℃ | 41 | HVAC of MV room faulty | 0: Normal 1: Failed
42 | MV room humidity | % | 42 | Invalid | /
43 | Invalid | / | 43 | Transformer ultra-high winding temperature | 0: Normal 1: Failed
44 | Invalid | / | 44 | LV cabinet A IMD warning | 0: Normal 1: Failed
45 | Invalid | / | 45 | LV cabinet A IMD alarm | 0: Normal 1: Failed
46 | Invalid | / | 46 | Invalid | /
47 | Invalid | / | 47 | Invalid | /
48 | Invalid | / | 48 | Invalid | /
49 | Invalid | / | 49 | Invalid | /
50 | Invalid | / | 50 | Transformer instantaneous overcurrent protection | 0: Normal 1: Failed
51 | Invalid | / | 51 | Transformer overcurrent protection | 0: Normal 1: Failed
52 | Invalid | / | 52 | Transformer zero-sequence overcurrent protection | 0: Normal 1: Failed
53 | Invalid | / | 53 | Transformer non-electrical protection | 0: Normal 1: Failed
54 | Invalid | / | 54 | High temperature alarm of MV room | 0: Normal 1: Failed
55 | Invalid | / | 55 | Invalid | /
56 | LV cabinet A temperature | ℃ | 56 | Invalid | /
57 | LV cabinet A humidity | % | 57 | LV cabinet A high temperature alarm | 0: Normal 1: Failed
58 | Invalid | / | 58 | Invalid | /
59 | Invalid | / | 59 | Invalid | /
60 | Maintenance-free dehydrator breather humidity | % | 60 | EPO Operation | 0: Not actuated 1: Actuated
61 | Transformer MV side THD of Ia | % | 61 | Maintenance-free hygroscopic fault | 0: Normal 1: Failed
62 | Transformer MV side THD of Ib | % | 62 | Maintenance-free hygroscopic start heating | 0: Normal 1: Failed
63 | Transformer MV side THD of Ic | % | 63 | Circuit Breaker auto-mode of cabinet G2 | 0: Normal 1: Failed
64 | Transformer frequency(MV side) | Hz | 64 | Invalid | /
65 | Aux. Transformer voltage Ua/Aux. Transformer voltage U | V | 65 | Invalid | /
66 | Aux. Transformer voltage Ub | V | 66 | Invalid | /
67 | Aux. Transformer voltage Uc | V | 67 | Invalid | /
68 | Aux. Transformer active power P | kW | 68 | Invalid | /
69 | Aux. Transformer reactive power Q | kVar | 69 | Invalid | /
70 | Aux. Transformer power factor cosφ | / | 70 | Invalid | /
71 | Aux. Transformer positive active energy (kWh) | kWh | 71 | Invalid | /
72 | Transformer MV side THD of Ua | % | 72 | Invalid | /
73 | Transformer MV side THD of Ub | % | 73 | Invalid | /
74 | Transformer MV side THD of Uc | % | 74 | Invalid | /
75 | Invalid | / | 75 | Invalid | /
76 | Invalid | / | 76 | LV room smoke alarm 1 | 0: Normal 1: Failed
77 | Invalid | / | 77 | LV room smoke alarm 2 | 0: Normal 1: Failed
78 | Invalid | / | 78 | LV cabinet A SPD fault | 0: Normal 1: Failed
79 | Transformer MV side active power P | kW | 79 | Invalid | /
80 | Transformer MV side reactive power Q | kVar | 80 | MV room smoke alarm 1 | 0: Normal 1: Failed
81 | Transformer MV side power factor cosφ | / | 81 | MV room smoke alarm 2 | 0: Normal 1: Failed
82 | Aux. Transformer reverse active energy (kWh) | kWh | 82 | Transformer overvoltage action | 0: Normal 1: Failed
83 | Aux. Transformer positive reactive energy (kVArh) | kVarh | 83 | Transformer action on undervoltage | 0: Normal 1: Failed
84 | Aux. Transformer reverse reactive energy (kVArh) | kVarh | 84 | Delayed automatic switch-on of transformer MV switch | 0: Normal 1: Failed
85 | Aux. Transformer Frequency | Hz | 85 | Transformer MV switch control loop disconnection | 0: Normal 1: Failed
86 | Aux. Transformer current Ia/Aux. Transformer current I | A | 86 | Protection-caused tripping | 0: Normal 1: Failed
87 | Aux. Transformer current Ib | A | 87 | Transformer zero-sequence overvoltage protection | 0: Normal 1: Failed
88 | Aux. Transformer current Ic | A | 88 | MV side under-frequency action | 0: Normal 1: Failed
89 | Transformer MV side voltage Uab | kV | 89 | MV side over-frequency action | 0: Normal 1: Failed
90 | Transformer MV side voltage Ubc | kV | 90 | Transformer differential protection | 0: Normal 1: Failed
91 | Transformer MV side voltage Uca | kV | 91 | Circuit Breaker failure protection | 0: Normal 1: Failed
|  |  | 92 | Invalid | /
|  |  | 93 | Invalid | /
|  |  | 94 | Invalid | /
|  |  | 95 | Invalid | /
|  |  | 96 | Invalid | /
|  |  | 97 | Invalid | /
|  |  | 98 | Aux. circuit SPD fault | 0: Normal 1: Failed
|  |  | 99 | UPS AC power failure | 0: Normal 1: Failed
|  |  | 100 | UPS-associated alarm | 0: Normal 1: Failed
|  |  | 101 | LV room smoke sensor fault | 0: Normal 1: Failed
|  |  | 102 | High-configuration relay protection power loss alarm | 0: Normal 1: Failed
|  |  | 103 | Invalid | /
|  |  | 104 | Invalid | /
|  |  | 105 | Invalid | /
|  |  | 106 | Invalid | /
|  |  | 107 | Reserved 1 | 0: Normal 1: Failed
|  |  | 108 | Reserved 2 | 0: Normal 1: Failed
|  |  | 109 | Reserved 3 | 0: Normal 1: Failed
|  |  | 110 | Reserved 4 | 0: Normal 1: Failed
|  |  | 111 | Reserved 5 | 0: Normal 1: Failed
|  |  | 112 | Reserved 6 | 0: Normal 1: Failed
|  |  | 113 | Reserved 7 | 0: Normal 1: Failed
|  |  | 114 | Reserved 8 | 0: Normal 1: Failed
|  |  | 115 | Reserved 9 | 0: Normal 1: Failed
|  |  | 116 | Reserved 10 | 0: Normal 1: Failed
|  |  | 117 | Reserved 11 | 0: Normal 1: Failed
|  |  | 118 | Reserved 12 | 0: Normal 1: Failed
|  |  | 119 | LV cabinet A tripping due to high temperature | 0: Normal 1: Failed
|  |  | 120 | Invalid | /
|  |  | 121 | MV room overtemperature tripping | 0: Normal 1: Failed
|  |  | 122 | LV room double smoke sensor tripping | 0: Normal 1: Failed
|  |  | 123 | MV room double smoke sensor tripping | 0: Normal 1: Failed
|  |  | 124 | Invalid | /
|  |  | 125 | Invalid | /
|  |  | 126 | Invalid | /
|  |  | 127 | Invalid | /
|  |  | 128 | Invalid | /
|  |  | 129 | Invalid | /
|  |  | 130 | MV room smoke sensor fault | 0: Normal 1: Failed
|  |  | 131 | G1 cabinet short-circuit indicator alarm | 0: Normal 1: Failed
|  |  | 132 | G3 cabinet short-circuit indicator alarm | 0: Normal 1: Failed
|  |  | 133 | Remote mode of load switch of cabinet G1 | 0: Normal 1: Failed
|  |  | 134 | Remote mode of load switch of cabinet G3 | 0: Normal 1: Failed
|  |  | 135 | LV room side-door open | 0: Normal 1: Failed
|  |  | 136 | Reserved 13 | 0: Normal 1: Failed
|  |  | 137 | Reserved 14 | 0: Normal 1: Failed
|  |  | 138 | Reserved 15 | 0: Normal 1: Failed
|  |  | 139 | Reserved 16 | 0: Normal 1: Failed

## JUPITER-3000K-H1-AC(GF)
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | Current Ia of low-voltage cabinet A | A | 1 | Communication failure | 0: normal1: faulty | 1 | Low-voltage cabinet A ACB remote closing | 0: On1: Invalid
2 | Current Ib of low-voltage cabinet A | A | 2 | transformer heavy gas | 0: normal1: faulty | 2 | Low-voltage cabinet A ACB remote opening | 0: Switch off; 1: Invalid
3 | Low-voltage cabinet A current Ic | A | 3 | transformer light gas | 0: normal1: faulty | 3 | Inactive | /
4 | Inactive | / | 4 | Transformer pressure relief valve action | 0: normal1: faulty | 4 | Inactive | /
5 | Inactive | / | 5 | Low transformer oil level | 0: normal1: faulty | 5 | Remote closing of medium-voltage circuit breaker | 0: On1: Invalid
6 | Inactive | / | 6 | High transformer oil level | 0: normal1: faulty | 6 | Remote opening of medium-voltage circuit breaker | 0: Switch off; 1: Invalid
7 | Inactive | / | 7 | High transformer oil temperature | 0: normal1: faulty | 7 | Spare 1 | 0: On1: Invalid
8 | Voltage Uab of low-voltage cabinet A | V | 8 | Transformer oil temperature is too high | 0: normal1: faulty | 8 | Spare 2 | 0: Switch off; 1: Invalid
9 | Voltage of low-voltage cabinet A Ubc | V | 9 | High transformer winding temperature | 0: normal1: faulty
10 | Voltage of low-voltage cabinet A Uca | V | 10 | ACB in low-voltage cabinet A | 0: split; 1: combined
11 | Active power P of low-voltage cabinet A | kW | 11 | ACB division in low-voltage cabinet A | 0: combined; 1: split
12 | Reactive power Q of low-voltage cabinet A | kVar | 12 | Low-voltage cabinet A ACB tripping due to fault | 0: normal1: faulty
13 | Low-voltage cabinet A power factor cosφ | N/A | 13 | Low-voltage cabinet A ACB remote operation | 0: local 1: remote
14 | Low-voltage cabinet A positive active electricity | kWh | 14 | Invalidation | /
15 | Reverse active electric degree of low-voltage cabinet A | kWh | 15 | Invalidation | /
16 | Positive reactive electricity of low-voltage cabinet A | kVarh | 16 | Invalidation | / |  | Description: The SmartLogger WebUI allows you to modify the name and unit of the standby signal. The actual name and unit prevail.
17 | Reverse reactive electric degree of low-voltage cabinet A | kVarh | 17 | Invalidation | /
18 | Inactive | / | 18 | The end door of the low-voltage chamber is open. | 0: normal1: faulty
19 | Inactive | / | 19 | The temperature control system of low-voltage cabinet A is faulty. | 0: normal1: faulty
20 | Inactive | / | 20 | Invalidation | /
21 | Inactive | / | 21 | Invalidation | /
22 | Inactive | / | 22 | Close the G2 circuit breaker of the transformer cabinet. | 0: split; 1: combined
23 | Inactive | / | 23 | Transformer cabinet G2 circuit breaker division | 0: combined; 1: split
24 | Inactive | / | 24 | Transformer cabinet G2 disconnector closed | 0: split; 1: combined
25 | Inactive | / | 25 | Transformer cabinet G2 disconnector division | 0: combined; 1: split
26 | Inactive | / | 26 | The G2 grounding switch of the transformer cabinet is in position. | 0: split; 1: combined
27 | Inactive | / | 27 | Grounding switch division of transformer cabinet G2 | 0: combined; 1: split
28 | Inactive | / | 28 | Transformer cabinet G2 circuit breaker spring does not store energy | 0: normal1: faulty
29 | Inactive | / | 29 | Transformer Cabinet G2 Circuit Breaker Remote Operation | 0: local 1: remote
30 | Inactive | / | 30 | Circuit breaker G2 of transformer cabinet is not switched off. | 0: normal1: faulty
31 | Inactive | / | 31 | The load switch G1 of the ring network incoming cabinet is in position. | 0: split; 1: combined
32 | Inactive | / | 32 | G1 load switch division of ring network incoming cabinet | 0: combined; 1: split
33 | Inactive | / | 33 | The G1 grounding switch of the ring network incoming cabinet is in position. | 0: split; 1: combined
34 | Inactive | / | 34 | Grounding switch division of G1 in the ring network incoming cabinet | 0: combined; 1: split
35 | Freq | Hz | 35 | Switch on the G3 load switch of the ring network outlet cabinet | 0: split; 1: combined
36 | Transformer oil surface temperature | ℃ | 36 | Distribution of G3 load switch in ring network outlet cabinet | 0: combined; 1: split
37 | Transformer winding temperature | ℃ | 37 | The G3 grounding switch of the ring network outlet cabinet is in position. | 0: split; 1: combined
38 | Current at medium-voltage side of transformer Ia | A | 38 | Location of G3 grounding switch in ring network outlet cabinet | 0: combined; 1: split
39 | Transformer MV side current Ib | A | 39 | Ring main unit insulation gas pressure low | 0: normal1: faulty
40 | Transformer MV side current Ic | A | 40 | Medium pressure chamber door open | 0: normal1: faulty
41 | Medium-voltage room temperature | ℃ | 41 | Medium-voltage room temperature control system failure | 0: normal1: faulty
42 | Humidity of medium-voltage room | % | 42 | Invalidation | /
43 | Inactive | / | 43 | Transformer winding temperature is too high | 0: normal1: faulty
44 | Inactive | / | 44 | Invalidation | /
45 | Inactive | / | 45 | Low-voltage cabinet A IMD alarm | 0: normal1: faulty
46 | Inactive | / | 46 | Invalidation | /
47 | Inactive | / | 47 | Invalidation | /
48 | Inactive | / | 48 | Invalidation | /
49 | Inactive | / | 49 | Invalidation | /
50 | Inactive | / | 50 | Transformer quick break protection action | 0: normal1: faulty
51 | Inactive | / | 51 | Transformer overcurrent protection action | 0: normal1: faulty
52 | Inactive | / | 52 | Transformer zero-sequence overcurrent protection action | 0: normal1: faulty
53 | Inactive | / | 53 | Transformer non-electric protection action | 0: normal1: faulty
54 | Inactive | / | 54 | Medium-voltage room high temperature alarm | 0: normal1: faulty
55 | Inactive | / | 55 | Invalidation | /
56 | Low-voltage cabinet A temperature | ℃ | 56 | Invalidation | /
57 | Low-voltage cabinet A humidity | % | 57 | Low-voltage cabinet A high temperature alarm | 0: normal1: faulty
58 | Inactive | / | 58 | Invalidation | /
59 | Inactive | / | 59 | Invalidation | /
60 | Maintenance-free dehydrating breather humidity | % | 60 | Operation of the EPO emergency stop button | 0: normal1: action
61 | Total harmonic component of medium-voltage side phase A current | % | 61 | Maintenance-free dehydrator fault | 0: normal1: faulty
62 | Total harmonic component of medium-voltage side Phase B current | % | 62 | Maintenance-free hygroscopic absorber heating | 0: normal1: faulty
63 | Total harmonic component of medium-voltage side Phase C current | % | 63 | Transformer Cabinet G2 Circuit Breaker Automatic Mode | 0: normal1: faulty
64 | Transformer MV side frequency | Hz | 64 | Invalidation | /
65 | Auxiliary transformer voltage Ua/Auxiliary transformer voltage U1 | V | 65 | Invalidation | /
66 | Auxiliary transformer voltage Ub/Auxiliary transformer voltage U2 | V | 66 | Opening the door of the DC PDC | 0: normal1: faulty
67 | Auxiliary transformer voltage Uc | V | 67 | Invalidation | /
68 | Active power of auxiliary transformer P | kW | 68 | Invalidation | /
69 | Auxiliary transformer reactive power Q | kVar | 69 | Invalidation | /
70 | Auxiliary variable power factor cosφ | N/A | 70 | Battery distribution transformer 1 MCCB in position | 0: split; 1: combined
71 | Positive active electric degree of auxiliary transformer | kWh | 71 | Energy storage and distribution transformer 1 heat exchange fault | 0: normal1: faulty
72 | Total harmonic component of medium voltage side phase A voltage | % | 72 | Opening the cabinet door of the energy storage and distribution transformer | 0: normal1: faulty
73 | Total harmonic component of phase B voltage at medium voltage side | % | 73 | Invalidation | /
74 | Total harmonic component of phase C voltage at medium voltage side | % | 74 | Invalidation | /
75 | Inactive | / | 75 | Invalidation | /
76 | Inactive | / | 76 | Low-voltage room smoke alarm 1 | 0: normal1: faulty
77 | Inactive | / | 77 | Low-voltage room smoke alarm 2 | 0: normal1: faulty
78 | Inactive | / | 78 | The SPD of low-voltage cabinet A is faulty. | 0: normal1: faulty
79 | Active power P at medium voltage side of transformer | kW | 79 | Invalidation | /
80 | Reactive power Q at medium-voltage side of transformer | kVar | 80 | Medium-voltage room smoke alarm 1 | 0: normal1: faulty
81 | Power factor cosφ at medium-voltage side of transformer | N/A | 81 | Medium-voltage room smoke alarm 2 | 0: normal1: faulty
82 | Reverse active electric degree of auxiliary transformer | kWh | 82 | Transformer overvoltage action | 0: normal1: faulty
83 | Positive reactive electric degree of auxiliary transformer | kVarh | 83 | Transformer undervoltage action | 0: normal1: faulty
84 | Reverse reactive electric degree of auxiliary transformer | kVarh | 84 | Automatic delay closing of transformer medium voltage switch | 0: normal1: faulty
85 | Auxiliary variable frequency | Hz | 85 | Transformer medium voltage switch control circuit broken | 0: normal1: faulty
86 | Auxiliary variable current Ia/Auxiliary variable current I1 | A | 86 | Protection action locking and closing | 0: normal1: faulty
87 | Auxiliary transformer current Ib/Auxiliary transformer current I2 | A | 87 | Transformer zero-sequence overvoltage action | 0: normal1: faulty
88 | Auxiliary variable current Ic | A | 88 | Underfrequency protection at medium voltage side | 0: normal1: faulty
89 | Voltage at medium-voltage side of transformer Uab | V | 89 | Overfrequency protection at medium voltage side | 0: normal1: faulty
90 | Voltage at medium voltage side of transformer Ubc | V | 90 | Transformer differential protection action | 0: normal1: faulty
91 | Voltage at medium-voltage side of transformer Uca | V | 91 | Circuit breaker failure protection action | 0: normal1: faulty
|  |  | 92 | Invalidation | /
|  |  | 93 | Invalidation | /
|  |  | 94 | Invalidation | /
|  |  | 95 | Invalidation | /
|  |  | 96 | Invalidation | /
|  |  | 97 | Invalidation | /
|  |  | 98 | Auxiliary loop SPD fault | 0: normal1: faulty
|  |  | 99 | UPS AC power failure | 0: normal1: faulty
|  |  | 100 | UPS Associated Alarms | 0: normal1: faulty
|  |  | 101 | The smoke sensor in the low-voltage room is faulty. | 0: normal1: faulty
|  |  | 102 | Relay protection power loss alarm | 0: normal1: faulty
|  |  | 103 | Invalidation | /
|  |  | 104 | Invalidation | /
|  |  | 105 | Invalidation | /
|  |  | 106 | Invalidation | /
|  |  | 107 | Standby 1 | 0: normal1: faulty
|  |  | 108 | Spare 2 | 0: normal1: faulty
|  |  | 109 | Spare 3 | 0: normal1: faulty
|  |  | 110 | Spare 4 | 0: normal1: faulty
|  |  | 111 | Spare 5 | 0: normal1: faulty
|  |  | 112 | Spare 6 | 0: normal1: faulty
|  |  | 113 | Spare 7 | 0: normal1: faulty
|  |  | 114 | Spare 8 | 0: normal1: faulty
|  |  | 115 | Spare 9 | 0: normal1: faulty
|  |  | 116 | Spare 10 | 0: normal1: faulty
|  |  | 117 | Spare 11 | 0: normal1: faulty
|  |  | 118 | Spare 12 | 0: normal1: faulty
|  |  | 119 | Low-voltage cabinet A overtemperature trip | 0: normal1: faulty
|  |  | 120 | Invalidation | /
|  |  | 121 | Overtemperature trip of medium pressure chamber | 0: normal1: faulty
|  |  | 122 | Double smoke sensor tripping in the low-voltage chamber | 0: normal1: faulty
|  |  | 123 | Medium-voltage chamber double smoke sensor trip | 0: normal1: faulty
|  |  | 124 | The PSU in low-voltage cabinet A is shut down. | 0: power-on; 1: power-off
|  |  | 125 | Invalidation | /
|  |  | 126 | Shut down the PSU in the medium-voltage room. | 0: power-on; 1: power-off
|  |  | 127 | Low-voltage side zero-sequence overcurrent | 0: normal1: faulty
|  |  | 128 | Invalidation | /
|  |  | 129 | Invalidation | /
|  |  | 130 | The smoke sensor in the medium-voltage chamber is faulty. | 0: normal1: faulty
|  |  | 131 | Short-circuit fault indicator alarm signal of cabinet G1 | 0: normal1: faulty
|  |  | 132 | Short-circuit fault indicator alarm signal of cabinet G3 | 0: normal1: faulty
|  |  | 133 | Remote control signal of load switch of cabinet G1 | 0: normal1: faulty
|  |  | 134 | Remote control signal of load switch of cabinet G3 | 0: normal1: faulty
|  |  | 135 | The side door of the low-voltage chamber is open. | 0: normal1: faulty
|  |  | 136 | Spare 13 | 0: normal1: faulty
|  |  | 137 | Spare 14 | 0: normal1: faulty
|  |  | 138 | Spare 15 | 0: normal1: faulty
|  |  | 139 | Spare 16 | 0: normal1: faulty

## JUPITER-9000K(6000K)-H1
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | LV cabinet A current Ia | A | 1 | Communication failure | 0: Normal 1: Failed | 1 | LV cabinet A ACB ON | 0: ON 1: Invalid
2 | LV cabinet A current Ib | A | 2 | Transformer heavy gas | 0: Normal 1: Failed | 2 | LV cabinet A ACB OFF | 0: OFF 1: Invalid
3 | LV cabinet A current Ic | A | 3 | Transformer light gas | 0: Normal 1: Failed | 3 | LV cabinet B ACB ON | 0: ON 1: Invalid
4 | Invalid | / | 4 | Transformer pressure valve action | 0: Normal 1: Failed | 4 | LV cabinet B ACB OFF | 0: OFF 1: Invalid
5 | Invalid | / | 5 | Transformer low oil level | 0: Normal 1: Failed | 5 | MV circuit breaker remote ON | 0: ON 1: Invalid
6 | Invalid | / | 6 | Transformer high oil level | 0: Normal 1: Failed | 6 | MV circuit breaker remote OFF | 0: OFF 1: Invalid
7 | Invalid | / | 7 | Transformer high oil temperature | 0: Normal 1: Failed | 7 | Reserved 1 | 0: ON 1: Invalid
8 | LV cabinet A voltage Uab | V | 8 | Transformer ultra-high oil temperature | 0: Normal 1: Failed | 8 | Reserved 2 | 0: OFF 1: Invalid
9 | LV cabinet A voltage Ubc | V | 9 | Transformer high winding temperature | 0: Normal 1: Failed
10 | LV cabinet A voltage Uca | V | 10 | LV cabinet A ACB ON | 0: Off 1: On
11 | LV cabinet A active power P | kW | 11 | LV cabinet A ACB OFF | 0: On 1: Off
12 | LV cabinet A reactive power Q | kVar | 12 | LV cabinet A ACB fault tripping | 0: Normal 1: Failed
13 | LV cabinet A power factor cosφ | / | 13 | LV cabinet A ACB remote operation | 0: Local 1: Remote
14 | LV cabinet A positive active energy (kWh) | kWh | 14 | LV cabinet B ACB ON | 0: Off 1: On
15 | LV cabinet A reverse active energy (kWh) | kWh | 15 | LV cabinet B ACB OFF | 0: On 1: Off
16 | LV cabinet A positive reactive energy (kVArh) | kVarh | 16 | LV cabinet B ACB fault tripping | 0: Normal 1: Failed
17 | LV cabinet A reverse reactive energy (kVArh) | kVarh | 17 | LV cabinet B ACB remote operation | 0: Local 1: Remote
18 | LV cabinet B current Ia | A | 18 | Open doors of LV room | 0: Normal 1: Failed |  | Note: The name and unit of the standby signal can be changed on the WebUI of the SmartLogger, the management system is subject to the actual name and unit. The gray part is optional, not the default signal.
19 | LV cabinet B current Ib | A | 19 | HVAC of LV cabinet A faulty | 0: Normal 1: Failed
20 | LV cabinet B current Ic | A | 20 | HVAC of LV cabinet B faulty | 0: Normal 1: Failed
21 | Invalid | / | 21 | Invalid | /
22 | Invalid | / | 22 | RMU cabinet G2 circuit breaker ON | 0: Off 1: On
23 | Invalid | / | 23 | RMU cabinet G2 circuit breaker OFF | 0: On 1: Off
24 | Invalid | / | 24 | RMU cabinet G2 disconnector ON | 0: Off 1: On
25 | LV cabinet B voltage Uab | V | 25 | RMU cabinet G2 disconnector OFF | 0: On 1: Off
26 | LV cabinet B voltage Ubc | V | 26 | RMU cabinet G2 earthing switch ON | 0: Off 1: On
27 | LV cabinet B voltage Uca | V | 27 | RMU cabinet G2 earthing switch OFF | 0: On 1: Off
28 | LV cabinet B active power P | kW | 28 | RMU cabinet G2 circuit breaker no energy storage | 0: Normal 1: Failed
29 | LV cabinet B reactive power Q | kVar | 29 | RMU cabinet G2 circuit breaker remote operation | 0: Local 1: Remote
30 | LV cabinet B power factor cosφ | / | 30 | RMU cabinet G2 circuit breaker OFF no action | 0: Normal 1: Failed
31 | LV cabinet B positive active energy (kWh) | kWh | 31 | RMU cabinet G1 load switch ON | 0: Off 1: On
32 | LV cabinet B reverse active energy (kWh) | kWh | 32 | RMU cabinet G1 load switch OFF | 0: On 1: Off
33 | LV cabinet B positive reactive energy (kVArh) | kVarh | 33 | RMU cabinet G1 earthing switch ON | 0: Off 1: On
34 | LV cabinet B reverse reactive energy (kVArh) | kVarh | 34 | RMU cabinet G1 earthing switch OFF | 0: On 1: Off
35 | Frequency | Hz | 35 | RMU cabinet G3 load switch ON | 0: Off 1: On
36 | Transformer oil temperature | ℃ | 36 | RMU cabinet G3 load switch OFF | 0: On 1: Off
37 | Transformer winding temperature | ℃ | 37 | RMU cabinet G3 earthing switch ON | 0: Off 1: On
38 | Transformer MV side current Ia | A | 38 | RMU cabinet G3 earthing switch OFF | 0: On 1: Off
39 | Transformer MV side current Ib | A | 39 | RMU SF6 low pressure | 0: Normal 1: Failed
40 | Transformer MV side current Ic | A | 40 | Open doors of MV room | 0: Normal 1: Failed
41 | MV room temperature | ℃ | 41 | HVAC of MV room faulty | 0: Normal 1: Failed
42 | MV room humidity | % | 42 | Invalid | /
43 | Invalid | / | 43 | Transformer ultra-high winding temperature | 0: Normal 1: Failed
44 | Invalid | / | 44 | Invalid
45 | Invalid | / | 45 | LV cabinet A IMD alarm | 0: Normal 1: Failed
46 | Invalid | / | 46 | Invalid
47 | Invalid | / | 47 | LV cabinet B IMD alarm | 0: Normal 1: Failed
48 | Invalid | / | 48 | Invalid | /
49 | Invalid | / | 49 | Invalid | /
50 | Invalid | / | 50 | Transformer instantaneous overcurrent protection | 0: Normal 1: Failed
51 | Invalid | / | 51 | Transformer overcurrent protection | 0: Normal 1: Failed
52 | Invalid | / | 52 | Transformer zero-sequence overcurrent protection | 0: Normal 1: Failed
53 | Invalid | / | 53 | Transformer non-electrical protection | 0: Normal 1: Failed
54 | Invalid | / | 54 | High temperature alarm of MV room | 0: Normal 1: Failed
55 | Invalid | / | 55 | Invalid | /
56 | LV cabinet A temperature | ℃ | 56 | Invalid | /
57 | LV cabinet A humidity | % | 57 | LV cabinet A high temperature alarm | 0: Normal 1: Failed
58 | LV cabinet B temperature | ℃ | 58 | LV cabinet B high temperature alarm | 0: Normal 1: Failed
59 | LV cabinet B humidity | % | 59 | Invalid | /
60 | Maintenance-free dehydrator breather humidity | % | 60 | EPO Operation | 0: Not actuated 1: Actuated
61 | Transformer MV side THD of Ia | % | 61 | Maintenance-free hygroscopic fault | 0: Normal 1: Failed
62 | Transformer MV side THD of Ib | % | 62 | Maintenance-free hygroscopic start heating | 0: Normal 1: Failed
63 | Transformer MV side THD of Ic | % | 63 | Circuit Breaker auto-mode of cabinet G2 | 0: Normal 1: Failed
64 | Transformer frequency(MV side) | Hz | 64 | Invalid | /
65 | Aux. Transformer voltage Ua/Aux. Transformer voltage U | V | 65 | Invalid | /
66 | Aux. Transformer voltage Ub | V | 66 | Invalid | /
67 | Aux. Transformer voltage Uc | V | 67 | Invalid | /
68 | Aux. Transformer active power P | kW | 68 | Invalid | /
69 | Aux. Transformer reactive power Q | kVar | 69 | Invalid | /
70 | Aux. Transformer power factor cosφ | / | 70 | Invalid | /
71 | Aux. Transformer positive active energy (kWh) | kWh | 71 | Invalid | /
72 | Transformer MV side THD of Ua | % | 72 | Invalid | /
73 | Transformer MV side THD of Ub | % | 73 | Invalid | /
74 | Transformer MV side THD of Uc | % | 74 | Invalid | /
75 | Invalid | / | 75 | Invalid | /
76 | Invalid | / | 76 | LV room smoke alarm 1 | 0: Normal 1: Failed
77 | Invalid | / | 77 | LV room smoke alarm 2 | 0: Normal 1: Failed
78 | Invalid | / | 78 | LV cabinet A SPD fault | 0: Normal 1: Failed
79 | Transformer MV side active power P | kW | 79 | LV cabinet B SPD fault | 0: Normal 1: Failed
80 | Transformer MV side reactive power Q | kVar | 80 | MV room smoke alarm 1 | 0: Normal 1: Failed
81 | Transformer MV side power factor cosφ | / | 81 | MV room smoke alarm 2 | 0: Normal 1: Failed
82 | Aux. Transformer reverse active energy (kWh) | kWh | 82 | Transformer overvoltage action | 0: Normal 1: Failed
83 | Aux. Transformer positive reactive energy (kVArh) | kVarh | 83 | Transformer action on undervoltage | 0: Normal 1: Failed
84 | Aux. Transformer reverse reactive energy (kVArh) | kVarh | 84 | Delayed automatic switch-on of transformer MV switch | 0: Normal 1: Failed
85 | Aux. Transformer Frequency | Hz | 85 | Transformer MV switch control loop disconnection | 0: Normal 1: Failed
86 | Aux. Transformer current Ia/Aux. Transformer current I | A | 86 | Protection-caused tripping | 0: Normal 1: Failed
87 | Aux. Transformer current Ib | A | 87 | Transformer zero-sequence overvoltage protection | 0: Normal 1: Failed
88 | Aux. Transformer current Ic | A | 88 | MV side under-frequency action | 0: Normal 1: Failed
89 | Transformer MV side voltage Uab | kV | 89 | MV side over-frequency action | 0: Normal 1: Failed
90 | Transformer MV side voltage Ubc | kV | 90 | Transformer differential protection | 0: Normal 1: Failed
91 | Transformer MV side voltage Uca | kV | 91 | Circuit Breaker failure protection | 0: Normal 1: Failed
|  |  | 92 | Invalid | /
|  |  | 93 | Invalid | /
|  |  | 94 | Invalid | /
|  |  | 95 | Invalid | /
|  |  | 96 | Invalid | /
|  |  | 97 | Invalid | /
|  |  | 98 | Aux. circuit SPD fault | 0: Normal 1: Failed
|  |  | 99 | UPS AC power failure | 0: Normal 1: Failed
|  |  | 100 | UPS-associated alarm | 0: Normal 1: Failed
|  |  | 101 | LV room smoke sensor fault | 0: Normal 1: Failed
|  |  | 102 | High-configuration relay protection power loss alarm | 0: Normal 1: Failed
|  |  | 103 | Invalid | /
|  |  | 104 | Invalid | /
|  |  | 105 | Invalid | /
|  |  | 106 | Invalid | /
|  |  | 107 | Reserved 1 | 0: Normal 1: Failed
|  |  | 108 | Reserved 2 | 0: Normal 1: Failed
|  |  | 109 | Reserved 3 | 0: Normal 1: Failed
|  |  | 110 | Reserved 4 | 0: Normal 1: Failed
|  |  | 111 | Reserved 5 | 0: Normal 1: Failed
|  |  | 112 | Reserved 6 | 0: Normal 1: Failed
|  |  | 113 | Reserved 7 | 0: Normal 1: Failed
|  |  | 114 | Reserved 8 | 0: Normal 1: Failed
|  |  | 115 | Reserved 9 | 0: Normal 1: Failed
|  |  | 116 | Reserved 10 | 0: Normal 1: Failed
|  |  | 117 | Reserved 11 | 0: Normal 1: Failed
|  |  | 118 | Reserved 12 | 0: Normal 1: Failed
|  |  | 119 | LV cabinet A tripping due to high temperature | 0: Normal 1: Failed
|  |  | 120 | LV cabinet B tripping due to high temperature | 0: Normal 1: Failed
|  |  | 121 | MV room overtemperature tripping | 0: Normal 1: Failed
|  |  | 122 | LV room double smoke sensor tripping | 0: Normal 1: Failed
|  |  | 123 | MV room double smoke sensor tripping | 0: Normal 1: Failed
|  |  | 124 | Invalid | /
|  |  | 125 | Invalid | /
|  |  | 126 | Invalid | /
|  |  | 127 | Invalid | /
|  |  | 128 | Invalid | /
|  |  | 129 | Invalid | /
|  |  | 130 | MV room smoke sensor fault | 0: Normal 1: Failed
|  |  | 131 | G1 cabinet short-circuit indicator alarm | 0: Normal 1: Failed
|  |  | 132 | G3 cabinet short-circuit indicator alarm | 0: Normal 1: Failed
|  |  | 133 | Remote mode of load switch of cabinet G1 | 0: Normal 1: Failed
|  |  | 134 | Remote mode of load switch of cabinet G3 | 0: Normal 1: Failed
|  |  | 135 | LV room side-door open | 0: Normal 1: Failed
|  |  | 136 | Reserved 13 | 0: Normal 1: Failed
|  |  | 137 | Reserved 14 | 0: Normal 1: Failed
|  |  | 138 | Reserved 15 | 0: Normal 1: Failed
|  |  | 139 | Reserved 16 | 0: Normal 1: Failed

## JUPITER-9000K(6000K)-H1-AC
Telemetry |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | Current Ia of low-voltage cabinet A | A | 1 | Communication failure | 0: normal 1: faulty | 1 | Low-voltage cabinet A ACB remote closing | 0: On1: Invalid
2 | Current Ib of low-voltage cabinet A | A | 2 | transformer heavy gas | 0: normal 1: faulty | 2 | Low-voltage cabinet A ACB remote opening | 0: Switch off; 1: Invalid
3 | Low-voltage cabinet A current Ic | A | 3 | transformer light gas | 0: normal 1: faulty | 3 | Low-voltage cabinet B ACB remote closing | 0: On1: Invalid
4 | Inactive | / | 4 | Transformer pressure relief valve action | 0: normal 1: faulty | 4 | Low-voltage cabinet B ACB remote opening | 0: Switch off; 1: Invalid
5 | Inactive | / | 5 | Low transformer oil level | 0: normal 1: faulty | 5 | Remote closing of medium-voltage circuit breaker | 0: On1: Invalid
6 | Inactive | / | 6 | High transformer oil level | 0: normal 1: faulty | 6 | Remote opening of medium-voltage circuit breaker | 0: Switch off; 1: Invalid
7 | Inactive | / | 7 | High transformer oil temperature | 0: normal 1: faulty | 7 | Spare 1 | 0: On1: Invalid
8 | Voltage Uab of low-voltage cabinet A | V | 8 | Transformer oil temperature is too high | 0: normal 1: faulty | 8 | Spare 2 | 0: Switch off; 1: Invalid
9 | Voltage of low-voltage cabinet A Ubc | V | 9 | High transformer winding temperature | 0: normal 1: faulty
10 | Voltage of low-voltage cabinet A Uca | V | 10 | ACB in low-voltage cabinet A | 0: split digit1: close digit
11 | Active power P of low-voltage cabinet A | kW | 11 | ACB division of low-voltage cabinet A | 0: close 1: separate
12 | Reactive power Q of low-voltage cabinet A | kVar | 12 | Low-voltage cabinet A ACB tripping due to fault | 0: normal 1: faulty
13 | Low-voltage cabinet A power factor cosφ | N/A | 13 | Low-voltage cabinet A ACB remote operation | 0: Local 1: Remote
14 | Low-voltage cabinet A positive active electric degree | kWh | 14 | ACB in low-voltage cabinet B | 0: split digit1: close digit
15 | Reverse active electric degree of low-voltage cabinet A | kWh | 15 | ACB division of low-voltage cabinet B | 0: close 1: separate
16 | Positive reactive electricity of low-voltage cabinet A | kVarh | 16 | Low-voltage cabinet B ACB tripping due to fault | 0: normal 1: faulty |  | Description: The SmartLogger WebUI allows you to modify the name and unit of the standby signal. The actual name and unit prevail.
17 | Reverse reactive electric degree of low-voltage cabinet A | kVarh | 17 | Low-voltage cabinet B ACB remote operation | 0: Local 1: Remote
18 | Current Ia of low-voltage cabinet B | A | 18 | The end door of the low-voltage chamber is open. | 0: normal 1: faulty
19 | Current Ib of low-voltage cabinet B | A | 19 | The temperature control system of low-voltage cabinet A is faulty. | 0: normal 1: faulty
20 | Low-voltage cabinet B current Ic | A | 20 | The temperature control system of low-voltage cabinet B is faulty. | 0: normal 1: faulty
21 | Inactive | / | 21 | Invalidation | /
22 | Inactive | / | 22 | Close the G2 circuit breaker of the transformer cabinet. | 0: split digit1: close digit
23 | Inactive | / | 23 | Transformer cabinet G2 circuit breaker division | 0: close 1: separate
24 | Inactive | / | 24 | Transformer cabinet G2 disconnector closed | 0: split digit1: close digit
25 | Voltage Uab of low-voltage cabinet B | V | 25 | Transformer cabinet G2 disconnector division | 0: close 1: separate
26 | Voltage of low-voltage cabinet B Ubc | V | 26 | The G2 grounding switch of the transformer cabinet is in position. | 0: split digit1: close digit
27 | Voltage of low-voltage cabinet B Uca | V | 27 | Grounding switch division of transformer cabinet G2 | 0: close 1: separate
28 | Active power P of low-voltage cabinet B | kW | 28 | Transformer cabinet G2 circuit breaker spring does not store energy | 0: normal 1: faulty
29 | Reactive power Q of low-voltage cabinet B | kVar | 29 | Transformer Cabinet G2 Circuit Breaker Remote Operation | 0: Local 1: Remote
30 | Low-voltage cabinet B power factor cosφ | N/A | 30 | Circuit breaker G2 of transformer cabinet is not switched off. | 0: normal 1: faulty
31 | Positive active electric degree of low-voltage cabinet B | kWh | 31 | The load switch G1 of the ring network incoming cabinet is in position. | 0: split digit1: close digit
32 | Reverse active electric degree of low-voltage cabinet B | kWh | 32 | G1 load switch division of ring network incoming cabinet | 0: close 1: separate
33 | Positive reactive electricity of low-voltage cabinet B | kVarh | 33 | The G1 grounding switch of the ring network incoming cabinet is in position. | 0: split digit1: close digit
34 | Reverse reactive electric degree of low-voltage cabinet B | kVarh | 34 | Grounding switch division of G1 in the ring network incoming cabinet | 0: close 1: separate
35 | Freq | Hz | 35 | Switch on the G3 load switch of the ring network outlet cabinet | 0: split digit1: close digit
36 | Transformer oil surface temperature | ℃ | 36 | Distribution of G3 load switch in ring network outlet cabinet | 0: close 1: separate
37 | Transformer winding temperature | ℃ | 37 | The G3 grounding switch of the ring network outlet cabinet is in position. | 0: split digit1: close digit
38 | Current at medium-voltage side of transformer Ia | A | 38 | Location of G3 grounding switch in ring network outlet cabinet | 0: close 1: separate
39 | Transformer MV side current Ib | A | 39 | Ring main unit insulation gas pressure low | 0: normal 1: faulty
40 | Transformer MV side current Ic | A | 40 | Medium pressure chamber door open | 0: normal 1: faulty
41 | Medium-voltage room temperature | ℃ | 41 | Medium-voltage room temperature control system failure | 0: normal 1: faulty
42 | Humidity of medium-voltage room | % | 42 | Invalidation | /
43 | Inactive | / | 43 | Transformer winding temperature is too high | 0: normal 1: faulty
44 | Inactive | / | 44 | Invalidation | /
45 | Inactive | / | 45 | Low-voltage cabinet A IMD alarm | 0: normal 1: faulty
46 | Inactive | / | 46 | Invalidation | /
47 | Inactive | / | 47 | Low-voltage cabinet B IMD alarm | 0: normal 1: faulty
48 | Inactive | / | 48 | Invalidation | /
49 | Inactive | / | 49 | Invalidation | /
50 | Inactive | / | 50 | Transformer quick break protection action | 0: normal 1: faulty
51 | Inactive | / | 51 | Transformer overcurrent protection action | 0: normal 1: faulty
52 | Inactive | / | 52 | Transformer zero-sequence overcurrent protection action | 0: normal 1: faulty
53 | Inactive | / | 53 | Transformer non-electric protection action | 0: normal 1: faulty
54 | Inactive | / | 54 | Medium-voltage room high temperature alarm | 0: normal 1: faulty
55 | Inactive | / | 55 | Invalidation | /
56 | Low-voltage cabinet A temperature | ℃ | 56 | Invalidation | /
57 | Low-voltage cabinet A humidity | % | 57 | Low-voltage cabinet A high temperature alarm | 0: normal 1: faulty
58 | Low-voltage cabinet B temperature | ℃ | 58 | Low-voltage cabinet B high temperature alarm | 0: normal 1: faulty
59 | Low-voltage cabinet B humidity | % | 59 | Invalidation | /
60 | Maintenance-free dehydrating breather humidity | % | 60 | Operation of the EPO emergency stop button | 0: normal; 1: action
61 | Total harmonic component of medium-voltage side phase A current | % | 61 | Maintenance-free dehydrator fault | 0: normal 1: faulty
62 | Total harmonic component of medium-voltage side Phase B current | % | 62 | Maintenance-free moisture absorber heating | 0: normal 1: faulty
63 | Total harmonic component of medium-voltage side Phase C current | % | 63 | Transformer Cabinet G2 Circuit Breaker Automatic Mode | 0: normal 1: faulty
64 | Transformer MV side frequency | Hz | 64 | Invalidation | /
65 | Auxiliary transformer voltage Ua/Auxiliary transformer voltage U1 | V | 65 | Invalidation | /
66 | Auxiliary transformer voltage Ub/Auxiliary transformer voltage U2 | V | 66 | Opening the door of the DC PDC | 0: normal 1: faulty
67 | Auxiliary transformer voltage Uc | V | 67 | Invalidation | /
68 | Active power of auxiliary transformer P | kW | 68 | Invalidation | /
69 | Auxiliary transformer reactive power Q | kVar | 69 | Invalidation | /
70 | Auxiliary variable power factor cosφ | N/A | 70 | Battery distribution transformer 1 MCCB in position | 0: split digit1: close digit
71 | Positive active electric degree of auxiliary transformer | kWh | 71 | Energy storage and distribution transformer 1 heat exchange fault | 0: normal 1: faulty
72 | Total harmonic component of medium voltage side phase A voltage | % | 72 | Opening the cabinet door of the energy storage and distribution transformer | 0: normal 1: faulty
73 | Total harmonic component of phase B voltage at medium voltage side | % | 73 | Invalidation | /
74 | Total harmonic component of phase C voltage at medium voltage side | % | 74 | Invalidation | /
75 | Inactive | / | 75 | Invalidation | /
76 | Inactive | / | 76 | Low-voltage room smoke alarm 1 | 0: normal 1: faulty
77 | Inactive | / | 77 | Low-voltage room smoke alarm 2 | 0: normal 1: faulty
78 | Inactive | / | 78 | The SPD of low-voltage cabinet A is faulty. | 0: normal 1: faulty
79 | Active power P at medium-voltage side of transformer | kW | 79 | The SPD of low-voltage cabinet B is faulty. | 0: normal 1: faulty
80 | Reactive power Q at medium-voltage side of transformer | kVar | 80 | Medium-voltage room smoke alarm 1 | 0: normal 1: faulty
81 | Power factor cosφ at medium-voltage side of transformer | N/A | 81 | Medium-voltage room smoke alarm 2 | 0: normal 1: faulty
82 | Reverse active electric degree of auxiliary transformer | kWh | 82 | Transformer overvoltage action | 0: normal 1: faulty
83 | Positive reactive electric degree of auxiliary transformer | kVarh | 83 | Transformer undervoltage action | 0: normal 1: faulty
84 | Reverse reactive electric degree of auxiliary transformer | kVarh | 84 | Automatic delay closing of transformer medium voltage switch | 0: normal 1: faulty
85 | Auxiliary variable frequency | Hz | 85 | Transformer medium voltage switch control circuit broken | 0: normal 1: faulty
86 | Auxiliary variable current Ia/Auxiliary variable current I1 | A | 86 | Protection action locking and closing | 0: normal 1: faulty
87 | Auxiliary transformer current Ib/Auxiliary transformer current I2 | A | 87 | Transformer zero-sequence overvoltage action | 0: normal 1: faulty
88 | Auxiliary variable current Ic | A | 88 | Underfrequency protection at medium voltage side | 0: normal 1: faulty
89 | Voltage at medium-voltage side of transformer Uab | V | 89 | Overfrequency protection at medium voltage side | 0: normal 1: faulty
90 | Voltage at medium voltage side of transformer Ubc | V | 90 | Transformer differential protection action | 0: normal 1: faulty
91 | Voltage at medium-voltage side of transformer Uca | V | 91 | Circuit breaker failure protection action | 0: normal 1: faulty
|  |  | 92 | Invalidation | /
|  |  | 93 | Invalidation | /
|  |  | 94 | Invalidation | /
|  |  | 95 | Invalidation | /
|  |  | 96 | Invalidation | /
|  |  | 97 | Invalidation | /
|  |  | 98 | Auxiliary loop SPD fault | 0: normal 1: faulty
|  |  | 99 | UPS AC power failure | 0: normal 1: faulty
|  |  | 100 | UPS Associated Alarms | 0: normal 1: faulty
|  |  | 101 | The smoke sensor in the low-voltage room is faulty. | 0: normal 1: faulty
|  |  | 102 | Relay protection power loss alarm | 0: normal 1: faulty
|  |  | 103 | Battery distribution transformer 3 MCCB in position | 0: split digit1: close digit
|  |  | 104 | Energy storage and distribution transformer 3 heat exchange fault | 0: normal 1: faulty
|  |  | 105 | Battery distribution transformer 4 MCCB in position | 0: split digit1: close digit
|  |  | 106 | Heat exchange fault of energy storage and distribution transformer 4 | 0: normal 1: faulty
|  |  | 107 | Standby 1 | 0: normal 1: faulty
|  |  | 108 | Spare 2 | 0: normal 1: faulty
|  |  | 109 | Spare 3 | 0: normal 1: faulty
|  |  | 110 | Spare 4 | 0: normal 1: faulty
|  |  | 111 | Spare 5 | 0: normal 1: faulty
|  |  | 112 | Spare 6 | 0: normal 1: faulty
|  |  | 113 | Spare 7 | 0: normal 1: faulty
|  |  | 114 | Spare 8 | 0: normal 1: faulty
|  |  | 115 | Spare 9 | 0: normal 1: faulty
|  |  | 116 | Spare 10 | 0: normal 1: faulty
|  |  | 117 | Spare 11 | 0: normal 1: faulty
|  |  | 118 | Spare 12 | 0: normal 1: faulty
|  |  | 119 | Overtemperature trip of low-voltage cabinet A | 0: normal 1: faulty
|  |  | 120 | Low-voltage cabinet B overtemperature tripping | 0: normal 1: faulty
|  |  | 121 | Overtemperature trip of medium pressure chamber | 0: normal 1: faulty
|  |  | 122 | Double smoke sensor tripping in the low-voltage room | 0: normal 1: faulty
|  |  | 123 | Medium-voltage chamber double smoke sensor trip | 0: normal 1: faulty
|  |  | 124 | The PSU in low-voltage cabinet A is shut down. | 0: On1: Off
|  |  | 125 | The PSU module in low-voltage cabinet B is shut down. | 0: On1: Off
|  |  | 126 | The PSU in the medium-voltage room is shut down. | 0: On1: Off
|  |  | 127 | Low-voltage side zero-sequence overcurrent | 0: normal 1: faulty
|  |  | 128 | Invalidation | /
|  |  | 129 | Invalidation | /
|  |  | 130 | The smoke sensor in the medium-voltage chamber is faulty. | 0: normal 1: faulty
|  |  | 131 | Short-circuit fault indicator alarm signal of cabinet G1 | 0: normal 1: faulty
|  |  | 132 | Short-circuit fault indicator alarm signal of cabinet G3 | 0: normal 1: faulty
|  |  | 133 | Remote control signal of load switch of cabinet G1 | 0: normal 1: faulty
|  |  | 134 | Remote control signal of load switch of cabinet G3 | 0: normal 1: faulty
|  |  | 135 | The side door of the low-voltage chamber is open. | 0: normal 1: faulty
|  |  | 136 | Spare 13 | 0: normal 1: faulty
|  |  | 137 | Spare 14 | 0: normal 1: faulty
|  |  | 138 | Spare 15 | 0: normal 1: faulty
|  |  | 139 | Spare 16 | 0: normal 1: faulty

## PCS(Utility_C&I)
Telemetry |  |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Unit | Range | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | A-B line voltage | V | [0,6553] | 1 | Communication failure | 0: Normal 1: Failed | 1 | Startup control | 0: Startup 1: Invalid
2 | B-C line voltage | V | [0,6553] | 2 | Locking status | 0: Locked 1: Unlocked | 2 | Shutdown control | 0: Shutdown 1: Invalid
3 | C-A line voltage | V | [0,6553] | 3 | Inverter startup/shutdown status | 0: Shutdown 1: Startup | 3 | Startup/shutdown control | 0: Shutdown 1: Startup
4 | Phase A voltage | V | [0,6553] | 4 | Reserved | 0: Normal 1: Faulty
5 | Phase B voltage | V | [0,6553] | 5 | Reserved | 0: Normal 1: Faulty
6 | Phase C voltage | V | [0,6553] | 6 | Reserved | 0: Normal 1: Faulty
7 | Phase A current | A | [-327,327] | 7 | Reserved | 0: Normal 1: Faulty
8 | Phase B current | A | [-327,327] | 8 | Reserved | 0: Normal 1: Faulty
9 | Phase C current | A | [-327,327] | 9 | Reserved | 0: Normal 1: Faulty
10 | Grid frequency | Hz | [0, 655] | 10 | Phase wire short-circuited to PE | 0: Normal 1: Faulty
11 | Active power | kW | [-3.4E+38, 3.4E+38] | 11 | Grid loss | 0: Normal 1: Faulty
12 | Reactive power | kVar | [-3.4E+38, 3.4E+38] | 12 | Grid undervoltage | 0: Normal 1: Faulty
13 | Power factor | N/A | (-1, 1] | 13 | Grid overvoltage | 0: Normal 1: Faulty
14 | Reserved | / | [-3.4E+38, 3.4E+38] | 14 | Grid voltage imbalance | 0: Normal 1: Faulty
15 | Cabinet temperature | ℃ | [-3276,3276] | 15 | Grid overfrequency | 0: Normal 1: Faulty
16 | Reserved | / | [0, 100] | 16 | Grid underfrequency | 0: Normal 1: Faulty
17 | Energy yield of current day | kWh | [0, 3.4E+38] | 17 | Unstable grid frequency | 0: Normal 1: Faulty
18 | Total energy yield | kWh | [0, 3.4E+38] | 18 | Output overcurrent | 0: Normal 1: Faulty
19 | Invalid | / | [0, 3.4E+38] | 19 | Output DC component overhigh | 0: Normal 1: Faulty
20 | Running state | / | 0x0000: standby: initializing 0x0001: standby: insulation resistance testing 0x0002: standby: irradiance detection 0x0003: standby: grid detection 0x0004: standby: safe mode 0x0005: standby: cable connection detection 0x0006: standby: soft-starting 0x0100: starting 0x0200: grid-connecting 0x0201: grid-connected at limited power 0x0202: grid-connected at self-derated power 0x0203: off-grid 0x0300: shut down: unexpectedly shut down 0x0301: shut down: shut down on command 0x0302: shut down: shut down via OVGR 0x0303 shut down: communication interrupted 0x0304: shut down: power limited 0x0305: shut down: manual startup required 0x0306: shut down: DC switches disconnected 0x0307: shut down: rapid shutdown 0x0308 shut down: input underpower 0x0309: shut down: NS protection 0x030A: shut down: rapid shutdown on command 0x0401: grid scheduling: cosφ-P curve 0x0402: grid scheduling: Q-U curve 0x0403: grid scheduling: PF-U curve 0x0404: grid scheduling: dry contact 0x0405: grid scheduling: Q-P curve 0x0500: ready for terminal test 0x0501: terminal testing 0x0600: inspection in progress 0X0700: AFCI testing 0X0800: I-V curve scanning 0X0900: DC input detection 0xA000: standby: no irradiation 0xA001: standby: no DC input 0xB000: communication interrupted 0xC000: loading | 20 | Abnormal residual current | 0: Normal 1: Faulty | <-Note: | Running State
21 | Startup time | / | [0, 3.4E+38] | 21 | Abnormal grounding | 0: Normal 1: Faulty |  | 0–3, 256, 769–778, 1792, 2304, 2560, 40960, 40961 | Standby
22 | Shutdown time | / | [0, 3.4E+38] | 22 | Low insulation resistance | 0: Normal 1: Faulty |  | 512–515, 1025–1029, 1280, 1281, 1536, 2048 | Running
23 | Yield this month | kWh | [0, 3.4E+38] | 23 | Cabinet overtemperature | 0: Normal 1: Faulty |  | 2816 | Disconnected
24 | Yield this year | kWh | [0, 3.4E+38] | 24 | Device fault | 0: Normal 1: Faulty |  | 768 | Faulty
25 | Invalid | / | / | 25 | Upgrade failed | 0: Normal 1: Faulty |  | 3072 | Loading
26 | DC voltage | V | [0,6553] | 26 | Reserved | 0: Normal 1: Faulty
27 | DC current | A | [-327,327] | 27 | Faulty monitoring unit | 0: Normal 1: Faulty
28 | Today's power supply from grid | kWh | [0, 3.4E+38] | 28 | Reserved | 0: Normal 1: Faulty
29 | Power supply from grid this month | kWh | [0, 3.4E+38] | 29 | Reserved | 0: Normal 1: Faulty
30 | Power supply from grid in this year | kWh | [0, 3.4E+38] | 30 | Reserved | 0: Normal 1: Faulty
31 | Total power supply from grid | kWh | [0, 3.4E+38] | 31 | Reserved | 0: Normal 1: Faulty
32 | Working mode | / | 0: PQ 1: VSG | 32 | Reserved | 0: Normal 1: Faulty
|  |  |  | 33 | Reserved | 0: Normal 1: Faulty
|  |  |  | 34 | Reserved | 0: Normal 1: Faulty
|  |  |  | 35 | Reserved | 0: Normal 1: Faulty
|  |  |  | 36 | Standby | Inverter running status 0: Other states 1: Current inverter status
|  |  |  | 37 | On-grid
|  |  |  | 38 | On-grid at normal power
|  |  |  | 39 | On-grid at derated power due to curtailment
|  |  |  | 40 | On-grid at self-derated power
|  |  |  | 41 | Shut down normally
|  |  |  | 42 | Shut down due to faults
|  |  |  | 43 | Shut down due to curtailment
|  |  |  | 44 | Shut down
|  |  |  | 45 | Terminal test
|  |  |  | 46 | Reserved | 0: Normal 1: Faulty
|  |  |  | 47 | Reserved | 0: Normal 1: Faulty
|  |  |  | 48 | Reserved | 0: Normal 1: Faulty
|  |  |  | 49 | External fan abnormal | 0: Normal 1: Faulty
|  |  |  | 50 | Reserved | 0: Normal 1: Faulty
|  |  |  | 51 | Reserved | 0: Normal 1: Faulty
|  |  |  | 52 | Reserved | 0: Normal 1: Faulty
|  |  |  | 53 | Internal fan abnormal | 0: Normal 1: Faulty
|  |  |  | 54 | Reserved | 0: Normal 1: Faulty
|  |  |  | 55 | Reserved | 0: Normal 1: Faulty
|  |  |  | 56 | Reserved | 0: Normal 1: Faulty
|  |  |  | 57 | Reserved | 0: Normal 1: Faulty
|  |  |  | 58 | Reserved | 0: Normal 1: Faulty
|  |  |  | 59 | Reserved | 0: Normal 1: Faulty
|  |  |  | 60 | Reserved | 0: Normal 1: Faulty
|  |  |  | 61 | Reserved | 0: Normal 1: Faulty
|  |  |  | 62 | DC input overvoltage | 0: Normal 1: Faulty
|  |  |  | 63 | DC input in reverse polarity | 0: Normal 1: Faulty
|  |  |  | 64 | Input short-circuited or in reverse polarity | 0: Normal 1: Faulty
|  |  |  | 65 | Input connected in series | 0: Normal 1: Faulty
|  |  |  | 66 | DC cable not securely connected | 0: Normal 1: Faulty
|  |  |  | 67 | Invalid certificate | 0: Normal 1: Faulty
|  |  |  | 68 | Certificate about to expire | 0: Normal 1: Faulty
|  |  |  | 69 | Certificate expired | 0: Normal 1: Faulty
|  |  |  | 70 | Off-grid running | Inverter running status 0: Other states 1: Off-grid running
|  |  |  | 71 | Parallel System Communication Failure | 0: No error 1: Error
|  |  |  | 72 | Local Access Certificate Invalid | 0: No error 1: Error
|  |  |  | 73 | Local Access Certificate About to Expire | 0: No error 1: Error
|  |  |  | 74 | Local Access Certificate Expired | 0: No error 1: Error
|  |  |  | 75 | Reverse Phase Sequence on AC Side | 0: No error 1: Error
|  |  |  | 76 | String Short-Circuited to Ground | 0: No error 1: Error
|  |  |  | 77 | Protection upon Communication Failure | 0: No error 1: Error
|  |  |  | 78 | AC Terminal Temperature Abnormal | 0: No error 1: Error
|  |  |  | 79 | DC Terminal Temperature Abnormal | 0: No error 1: Error
|  |  |  | 80 | Black Start Failed | 0: No error 1: Error
|  |  |  | 81 | Incorrect Black Start Instruction Sequence | 0: No error 1: Error
|  |  |  | 82 | CAN Bus Cable Between Parallel PCSs Disconnected | 0: No error 1: Error
|  |  |  | 83 | DC Input Abnormal | 0: No error 1: Error
|  |  |  | 84 | Retained | /
|  |  |  | 85 | Standby | /
|  |  |  | 86 | Cold standby operation | "Inverter running status 0: not in this state 1: current status of the inverter

## CMU(Utility Smart String ESS)
Telemetry |  |  |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Precision | Range | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | Rated capacity | 0.001 | [0, 3.4E+38] | kWh | 1 | AC SPD fault | 0: Normal 1: Faulty
2 | Rated power | 0.001 | [0, 3.4E+38] | kW | 2 | UPS alarm | 0: Normal 1: Faulty
3 | Battery cabin temperature 1 | 0.1 | [-3276,3276] | °C | 3 | Fire alarm | 0: Normal 1: Faulty
4 | Battery cabin humidity 1 | 0.1 | [0, 100] | % | 4 | Fire suppression system fault | 0: Normal 1: Faulty
5 | Battery cabin temperature 2 | 0.1 | [-3276,3276] | °C | 5 | Fire suppression gas discharge status | 0: Normal 1: Gas releasing
6 | Battery cabin humidity 2 | 0.1 | [0, 100] | % | 6 | Fire alarm status | 0: Normal 1: Fire alarm
7 | Battery cabin temperature 3 | 0.1 | [-3276,3276] | °C | 7 | Combustible gas alarm | 0: Normal 1: Faulty
8 | Battery cabin humidity 3 | 0.1 | [0, 100] | % | 8 | Battery cabin water alarm | 0: Normal 1: Faulty
9 | Battery cabin temperature 4 | 0.1 | [-3276,3276] | °C | 9 | Control unit cabin water alarm | 0: Normal 1: Faulty
10 | Battery cabin humidity 4 | 0.1 | [0, 100] | % | 10 | Control unit cabin door status alarm | 0: Normal 1: Faulty
11 | Control unit cabin temperature 1 | 0.1 | [-3276,3276] | °C | 11 | Battery cabin door 1 status alarm | 0: Normal 1: Faulty
12 | Control unit cabin humidity 1 | 0.1 | [0, 100] | % | 12 | Battery cabin door 2 status alarm | 0: Normal 1: Faulty
13 | Battery cabin dew point temperature | 0.1 | [-3276,3276] | °C | 13 | Battery cabin door 3 status alarm | 0: Normal 1: Faulty
14 | Control unit cabin dew point temperature | 0.1 | [-3276,3276] | °C | 14 | Battery cabin door 4 status alarm | 0: Normal 1: Faulty
15 | SOC | 1 | [0, 100] | % | 15 | Battery cabin door 5 status alarm | 0: Normal 1: Faulty
16 | Energy charged today | 0.01 | [0, 3.4E+38] | kWh | 16 | Battery cabin door 6 status alarm | 0: Normal 1: Faulty
17 | Energy discharged today | 0.01 | [0, 3.4E+38] | kWh | 17 | Battery cabin temperature high | 0: Normal 1: Faulty
18 | Energy charged this month | 0.01 | [0, 3.4E+38] | kWh | 18 | Control unit cabin temperature high | 0: Normal 1: Faulty
19 | Energy discharged this month | 0.01 | [0, 3.4E+38] | kWh | 19 | Battery cabin condensation risk | 0: Normal 1: Faulty
20 | Energy charged this year | 0.01 | [0, 3.4E+38] | kWh | 20 | Control unit cabin condensation risk | 0: Normal 1: Faulty
21 | Energy discharged this year | 0.01 | [0, 3.4E+38] | kWh | 21 | Battery cabin T/H sensor malfunction | 0: Normal 1: Faulty
22 | Total charged energy | 0.01 | [0, 3.4E+38] | kWh | 22 | Control unit cabin T/H sensor malfunction | 0: Normal 1: Faulty
23 | Total discharged energy | 0.01 | [0, 3.4E+38] | kWh | 23 | Battery cabin T/H control malfunction | 0: Normal 1: Faulty
24 | Charge/Discharge power | 0.001 | [-3.4E+38, 3.4E+38] | kW | 24 | Control unit cabin T/H control malfunction | 0: Normal 1: Faulty
25 | Chargeable capacity | 0.001 | [0, 3.4E+38] | kWh | 25 | Rectifier fault | 0: Normal 1: Faulty
26 | Dischargeable capacity | 0.001 | [0, 3.4E+38] | kWh
27 | Fan speed 1 | 1 | [0, 65535] | RPM
28 | Fan speed 2 | 1 | [0, 65535] | RPM
29 | Gas concentration at CO sensor 1 | 1 | [0, 65535] | ppm
30 | Gas concentration at CO sensor 2 | 1 | [0, 65535] | ppm
31 | Gas concentration at CO sensor 3 | 1 | [0, 65535] | ppm
32 | Gas concentration at CO sensor 4 | 1 | [0, 65535] | ppm
33 | Gas concentration at CO sensor 5 | 1 | [0, 65535] | ppm
34 | Gas concentration at CO sensor 6 | 1 | [0, 65535] | ppm
35 | Total output voltage of rectifiers | 0.1 | [0, 6553] | V
36 | Total output current of rectifiers | 0.1 | [0, 6553] | A
37 | Quantity of rectifiers | 1 | [0, 65535] | NA
38 | Total output power of rectifiers | 0.001 | [0, 3.4E+38] | W
39 | Gas concentration measured by H2 sensor 1 | 1 | [0, 65535] | ppm
40 | Fan speed 3 | 1 | [0, 65535] | RPM
41 | Fan speed 4 | 1 | [0, 65535] | RPM
42 | Fan speed 5 | 1 | [0, 65535] | RPM
43 | Fan speed 6 | 1 | [0, 65535] | RPM
44 | Fan speed 7 | 1 | [0, 65535] | RPM
45 | Fan speed 8 | 1 | [0, 65535] | RPM
46 | Fan speed 9 | 1 | [0, 65535] | RPM
47 | Fan speed 10 | 1 | [0, 65535] | RPM
48 | Fan speed 11 | 1 | [0, 65535] | RPM
49 | Fan speed 12 | 1 | [0, 65535] | RPM
50 | DC bus voltage | 0.1 | [0, 6553] | V
51 | DC bus current | 0.1 | [0, 6553] | A
52 | Phase A voltage of auxiliary meter | 0.1 | [0, 3.4E+38] | V
53 | Phase B voltage of auxiliary meter | 0.1 | [0, 3.4E+38] | V
54 | Phase C voltage of auxiliary meter | 0.1 | [0, 3.4E+38] | V
55 | Phase A active power of auxiliary meter | 0.001 | [-3.4E+38, 3.4E+38] | kW
56 | Phase B active power of auxiliary meter | 0.001 | [-3.4E+38, 3.4E+38] | kW
57 | Phase C active power of auxiliary meter | 0.001 | [-3.4E+38, 3.4E+38] | kW
58 | Active power of auxiliary meter | 0.001 | [-3.4E+38, 3.4E+38] | kW
59 | Reactive power of auxiliary meter | 0.001 | [-3.4E+38, 3.4E+38] | kVar
60 | Power factor of auxiliary meter | 0.001 | (-1, 1] | /
61 | Total active power of auxiliary meter | 0.001 | [0, 3.4E+38] | kWh

## CMU(C&I Smart String ESS)
Telemetry |  |  |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Precision | Range | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | Rated capacity | 0.001 | [0, 3.4E+38] | kWh | 1 | AC SPD fault | 0: Normal 1: Faulty
2 | Rated power | 0.001 | [0, 3.4E+38] | kW | 2 | UPS alarm | 0: Normal 1: Faulty
3 | Battery cabin temperature 1 | 0.1 | [-3276,3276] | °C | 3 | Fire alarm | 0: Normal 1: Faulty
4 | Battery cabin humidity 1 | 0.1 | [0, 100] | % | 4 | Fire suppression system fault | 0: Normal 1: Faulty
5 | Reserved | / | / | / | 5 | Fire suppression gas discharge status | 0: Normal 1: Gas releasing
6 | Reserved | / | / | / | 6 | Fire alarm status | 0: Normal 1: Fire alarm
7 | Reserved | / | / | / | 7 | Combustible gas alarm | 0: Normal 1: Faulty
8 | Reserved | / | / | / | 8 | Battery cabin water alarm | 0: Normal 1: Faulty
9 | Reserved | / | / | / | 9 | Reserved | /
10 | Reserved | / | / | / | 10 | Reserved | /
11 | Reserved | / | / | / | 11 | Battery cabin door 1 status alarm | 0: Normal 1: Faulty
12 | Reserved | / | / | / | 12 | Reserved | /
13 | Battery cabin dew point temperature | 0.1 | [-3276,3276] | °C | 13 | Reserved | /
14 | Reserved | / | / | / | 14 | Reserved | /
15 | SOC | 1 | [0, 100] | % | 15 | Reserved | /
16 | Energy charged of the day | 0.01 | [0, 3.4E+38] | kWh | 16 | Reserved | /
17 | Energy discharged of the day | 0.01 | [0, 3.4E+38] | kWh | 17 | Ambient temperature high in the battery cabin | 0: Normal 1: Faulty
18 | Energy charged of the month | 0.01 | [0, 3.4E+38] | kWh | 18 | Reserved | /
19 | Energy discharged of the month | 0.01 | [0, 3.4E+38] | kWh | 19 | Condensation risk in the battery cabin | 0: Normal 1: Faulty
20 | Energy charged of the year | 0.01 | [0, 3.4E+38] | kWh | 20 | Reserved | /
21 | Energy discharged of the year | 0.01 | [0, 3.4E+38] | kWh | 21 | Battery cabin T/H sensor malfunction | 0: Normal 1: Faulty
22 | Total charged energy | 0.01 | [0, 3.4E+38] | kWh | 22 | Reserved | /
23 | Total discharged energy | 0.01 | [0, 3.4E+38] | kWh | 23 | Battery cabin T/H control malfunction | 0: Normal 1: Faulty
24 | Charge/Discharge power | 0.001 | [-3.4E+38, 3.4E+38] | kW | 24 | Reserved | /
25 | Chargeable capacity | 0.001 | [0, 3.4E+38] | kWh | 25 | Rectifier fault | 0: Normal 1: Faulty
26 | Dischargeable capacity | 0.001 | [0, 3.4E+38] | kWh
27 | Fan speed 1 | 1 | [0, 65535] | RPM
28 | Fan speed 2 | 1 | [0, 65535] | RPM
29 | Gas concentration measured by CO sensor 1 | 1 | [0, 65535] | ppm
30 | Gas concentration measured by CO sensor 2 | 1 | [0, 65535] | ppm
31 | Reserved | / | / | /
32 | Reserved | / | / | /
33 | Reserved | / | / | /
34 | Reserved | / | / | /
35 | Total output voltage of rectifiers | 0.1 | [0, 6553] | V
36 | Total output current of rectifiers | 0.1 | [0, 6553] | A
37 | Quantity of rectifiers | 1 | [0, 65535] | NA
38 | Total output power of rectifiers | 0.001 | [0, 3.4E+38] | W
39 | Gas concentration measured by H2 sensor 1 | 1 | [0, 65535] | ppm
40 | Reserved | / | / | /
41 | Reserved | / | / | /
42 | Reserved | / | / | /
43 | Reserved | / | / | /
44 | Reserved | / | / | /
45 | Reserved | / | / | /
46 | Reserved | / | / | /
47 | Reserved | / | / | /
48 | Reserved | / | / | /
49 | Reserved | / | / | /
50 | DC bus voltage | 0.1 | [0, 6553] | V
51 | DC bus current | 0.1 | [0, 6553] | A
52 | Reserved | / | / | /
53 | Reserved | / | / | /
54 | Reserved | / | / | /
55 | Reserved | / | / | /
56 | Reserved | / | / | /
57 | Reserved | / | / | /
58 | Active power of auxiliary meter | 0.001 | [-3.4E+38, 3.4E+38] | kW
59 | Reactive power of auxiliary meter | 0.001 | [-3.4E+38, 3.4E+38] | kVar
60 | Power factor of auxiliary meter | 0.001 | (-1, 1] | /
61 | Total active power of auxiliary meter | 0.001 | [0, 3.4E+38] | kWh

## ESC(C&I and Utility_1C)
Telemetry |  |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Range | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | DCDC Cabinet temperature | [-3276,3276] | °C | 1 | Invalid | / | 1 | Rack 1-Running | 0: Valid 1: Invalid | 1 | Rack 1 - End-of-charge SOC | % | 1
2 | DCDC Running state | 0-Standby 1-Standby: safe mode 2-Standby: cable connection detection 256-Soft start 512-Running 513-Operating: limited power 514-Operating: self-derating 515-Running: current limiting 768-Unexpected shutdown 769-Shut down on command 770-Emergency power-off 771-Charge/Discharge disabled 772-Battery pack rapid shutdown 45056-Offline 49152-Loading | / | 2 | Invalid | / | 2 | Rack 1-Hibernation | 0: Valid 1: Invalid | 2 | Rack 1 - End-of-discharge SOC | % | 1
3 | DCDC Bus-side voltage | [-3276,3276] | V | 3 | Invalid | / | 3 | Reserved | / | 3 | Reserved | / | /
4 | DCDC Bus-side current | [-3276,3276] | A | 4 | Invalid | / | 4 | Reserved | / | 4 | Reserved | / | /
5 | DCDC Battery-side voltage | [-3276,3276] | V | 5 | Invalid | /
6 | DCDC Battery-side current | [-3276,3276] | A | 6 | Invalid | /
7 | DCDC ISO insulation resistance | [0, 65.535] | MΩ | 7 | Invalid | /
8 | Reserved | / | / | 8 | Invalid | /
9 | Reserved | / | / | 9 | Invalid | /
10 | Reserved | / | / | 10 | Invalid | /
11 | Reserved | / | / | 11 | Invalid | /
12 | Reserved | / | / | 12 | Invalid | /
13 | Reserved | / | / | 13 | Invalid | / |  | <==Note | Rack-Device status
14 | Reserved | / | / | 14 | Controller-pack communication error | 0: Normal 1: Faulty |  |  | 1: Running
15 | Reserved | / | / | 15 | Controller error | 0: Normal 1: Faulty |  |  | 2: Sleep
16 | Reserved | / | / | 16 | Controller battery side overvoltage | 0: Normal 1: Faulty |  |  | 3: Charging
17 | Reserved | / | / | 17 | Controller battery side undervoltage | 0: Normal 1: Faulty |  |  | 4: Discharging
18 | Reserved | / | / | 18 | Controller battery side short-circuit | 0: Normal 1: Faulty |  |  | 5: Power off
19 | Reserved | / | / | 19 | Controller battery side reverse polarity | 0: Normal 1: Faulty |  |  | 6: Faulted
20 | Rack 1-Quantity of working battery packs | [0, 65535] | / | 20 | Controller bus side overvoltage | 0: Normal 1: Faulty |  |  | 7: Off-line
21 | Rack 1-Device status | 1: In operation 2: Hibernating 3: Charging 4: Discharging 5: Shut down 6. Faulty 7: Offline 8: Self-check in progress 49152: Loading | / | 21 | Controller bus side reverse polarity | 0: Normal 1: Faulty |  |  | 8: Self-check in progress
22 | Rack 1-Voltage | [-3276,3276] | V | 22 | Controller insulation resistance abnormal | 0: Normal 1: Faulty |  |  | 49152: Loading
23 | Rack 1-Current | [-3276,3276] | A | 23 | Controller temperature high | 0: Normal 1: Faulty
24 | Rack 1-SOC | [0, 100] | % | 24 | Controller battery terminal temperature high | 0: Normal 1: Faulty
25 | Rack 1-SOH | [0, 100] | % | 25 | Controller bus terminal temperature high | 0: Normal 1: Faulty
26 | Rack 1-SOE | [0, 100] | % | 26 | Controller version mismatch | 0: Normal 1: Faulty
27 | Rack 1-DOD | [0, 100] | % | 27 | Controller internal fan faulty | 0: Normal 1: Faulty
28 | Rack 1-Charge/Discharge power | [-3.4E+38, 3.4E+38] | kW | 28 | Pack monitoring board error | 0: Normal 1: Faulty
29 | Rack 1-Chargeable capacity | [0, 3.4E+38] | kWh | 29 | Pack internal error | 0: Normal 1: Faulty
30 | Rack 1-Dischargeable capacity | [0, 3.4E+38] | kWh | 30 | Pack lockout | 0: Normal 1: Faulty
31 | Rack 1-Highest battery pack temperature | [-327,327] | °C | 31 | Pack fan faulty | 0: Normal 1: Faulty
32 | Rack 1-Position where the highest battery pack temperature was detected | [0, 65535] | / | 32 | Pack temperature imbalance | 0: Normal 1: Faulty
33 | Rack 1-Lowest battery pack temperature | [-327,327] | °C | 33 | Pack overvoltage | 0: Normal 1: Faulty
34 | Rack 1-Position where the lowest battery rack temperature was detected | [0, 65535] | / | 34 | Controller power control unit communication error | 0: Normal 1: Faulty
35 | Rack 1-Lowest battery pack voltage | [0, 6553] | V | 35 | Controller connection detection error | 0: Normal 1: Faulty
36 | Rack 1-Position where the lowest battery pack voltage was detected | [0, 65535] | / | 36 |  | 0: Normal 1: Faulty
37 | Rack 1-Highest battery pack voltage | [0, 6553] | V | 37 | Optimizer error | 0: Normal 1: Faulty
38 | Rack 1-Position where the highest battery pack voltage was detected | [0, 65535] | / | 38 | Optimizer temperature high | 0: Normal 1: Faulty
39 | Rack 1-Energy charged of the day | [0, 3.4E+38] | kWh | 39 | Optimizer terminal temperature high | 0: Normal 1: Faulty
40 | Rack 1-Energy discharged of the day | [0, 3.4E+38] | kWh | 40 | Optimizer version mismatch | 0: Normal 1: Faulty
41 | Rack 1-Energy charged of the month | [0, 3.4E+38] | kWh | 41 | Incorrect controller bus connection | 0: Normal 1: Faulty
42 | Rack 1-Energy discharged of the month | [0, 3.4E+38] | kWh | 42 | Loose pack connection to copper bar | 0: Normal 1: Faulty
43 | Rack 1-Energy charged of the year | [0, 3.4E+38] | kWh | 43 | Controller rapid shutdown connection detection error | 0: Normal 1: Faulty
44 | Rack 1-Energy discharged of the year | [0, 3.4E+38] | kWh | 44 | Pack SOH low | 0: Normal 1: Faulty
45 | Rack 1-Total charged energy | [0, 3.4E+38] | kWh | 45 | Pack overcurrent | 0: Normal 1: Faulty
46 | Rack 1-Total discharged energy | [0, 3.4E+38] | kWh | 46 | Pack temperature high | 0: Normal 1: Faulty
47 | Reserved | / | / | 47 | Pack temperature low | 0: Normal 1: Faulty
48 | Reserved | / | / | 48 | Pack undervoltage | 0: Normal 1: Faulty
49 | Reserved | / | / | 49 | Pack aux. power supply faulty | 0: Normal 1: Faulty
50 | Reserved | / | / | 50 | Invalid | /
51 | Reserved | / | / | 51 | Invalid | /
52 | Reserved | / | / | 52 | Invalid | /
53 | Reserved | / | / | 53 | DC aux. power supply of controller faulty | 0: Normal 1: Faulty
54 | Reserved | / | / | 54 | External Fan of Rack Controller Faulty | 0: Normal 1: Faulty
55 | Reserved | / | / | 55 | Rack Controller Temperature Abnormal | 0: Normal 1: Faulty
56 | Reserved | / | / | 56 | Optimizer temperature low | 0: Normal 1: Faulty
57 | Reserved | / | / | 57 | Emergency Power-Off | 0: Normal 1: Faulty
58 | Reserved | / | / | 58 | Controller-pack version inconsistency | 0: Normal 1: Faulty
59 | Reserved | / | / | 59 | Controller-pack version mismatch | 0: Normal 1: Faulty
60 | Reserved | / | / | 60 | Communication error between controller and PCS | 0: Normal 1: Faulty
61 | Reserved | / | / | 61 | Communication error between BCU and SmartLogger | 0: Normal 1: Faulty
62 | Reserved | / | /
63 | Reserved | / | /
64 | Reserved | / | /
65 | Reserved | / | /
66 | Reserved | / | /
67 | Reserved | / | /
68 | Reserved | / | /
69 | Reserved | / | /
70 | Reserved | / | /
71 | Reserved | / | /
72 | Reserved | / | /
73 | Reserved | / | /
Note 1. The ratio of DCDCs to battery racks is closely related to the discharge rate. For example, in the 1C scenario, each battery rack is configured with a DCDC; in the 0.5C scenario, two battery racks share a DCDC. Among the preceding BCU telemetering signals, "DCDC Running state", "DCDC Bus-side voltage", ..., and "DCDC ISO insulation resistance" signals are used in the 1C scenario, whereas "DCDC Running state 1" and "DCDC Bus-side voltage 1", ..., and "DCDC ISO insulation resistance 2" signals are used in the 0.5C scenario.
2. DCDC running state, DCDC running state 1, and DCDC running state 2 have the same definitions. For details, see the following enumeration definitions.
DCDC Running Status
0-Standby
1-Standby: safe mode
2-Standby: cable connection detection
256-Soft start
512-Running
513-Operating: limited power
514-Operating: self-derating
515-Running: Current limiting
768-Unexpected shutdown
769-Commanded shutdown
770-Emergency power off
771-Charge/Discharge disabled
772-Battery pack rapid shutdown
45056-off-line
49152-Loading

## ESC(Utility_0.5C)
Telemetry |  |  |  | Teleindication | Signal Name | Status | Telecontrol | Signal Name | Command | Teleadjust
No. | Signal Name | Range | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | DCDC Cabinet temperature | [-3276,3276] | °C | 1 | Invalid | / | 1 | Rack 1-Running | 0: Valid 1: Invalid | 1 | Rack 1 - End-of-charge SOC | % | 1
2 | Reserved | / | / | 2 | Invalid | / | 2 | Rack 1-Hibernation | 0: Valid 1: Invalid | 2 | Rack 1 - End-of-discharge SOC | % | 1
3 | Reserved | / | / | 3 | Invalid | / | 3 | Rack 2-Running | 0: Valid 1: Invalid | 3 | Rack 2 - End-of-charge SOC | % | 1
4 | Reserved | / | / | 4 | Invalid | / | 4 | Rack 2-Hibernation | 0: Valid 1: Invalid | 4 | Rack 2 - End-of-discharge SOC | % | 1
5 | Reserved | / | / | 5 | Invalid | /
6 | Reserved | / | / | 6 | Invalid | /
7 | Reserved | / | / | 7 | Invalid | /
8 | DCDC Running state 1 | 0-Standby 1-Standby: safe mode 2-Standby: cable connection detection 256-Soft start 512-Running 513-Operating: limited power 514-Operating: self-derating 515-Running: current limiting 768-Unexpected shutdown 769-Shut down on command 770-Emergency power-off 771-Charge/Discharge disabled 772-Battery pack rapid shutdown 45056-Offline 49152-Loading | / | 8 | Invalid | /
9 | DCDC Bus-side voltage 1 | [-3276,3276] | V | 9 | Invalid | /
10 | DCDC Bus-side current 1 | [-3276,3276] | A | 10 | Invalid | /
11 | DCDC Battery-side voltage 1 | [-3276,3276] | V | 11 | Invalid | /
12 | DCDC Battery-side current 1 | [-3276,3276] | A | 12 | Invalid | /
13 | DCDC ISO insulation resistance 1 | [0, 65.535] | MΩ | 13 | Invalid | /
14 | DCDC Running state 2 | 0-Standby 1-Standby: safe mode 2-Standby: cable connection detection 256-Soft start 512-Running 513-Operating: limited power 514-Operating: self-derating 515-Running: current limiting 768-Unexpected shutdown 769-Shut down on command 770-Emergency power-off 771-Charge/Discharge disabled 772-Battery pack rapid shutdown 45056-Offline 49152-Loading | / | 14 | Controller-pack communication error | 0: Normal 1: Faulty
15 | DCDC Bus-side voltage 2 | [-3276,3276] | V | 15 | Controller error | 0: Normal 1: Faulty
16 | DCDC Bus-side current 2 | [-3276,3276] | A | 16 | Controller battery side overvoltage | 0: Normal 1: Faulty | <==Note | Rack-Device status
17 | DCDC Battery-side voltage 2 | [-3276,3276] | V | 17 | Controller battery side undervoltage | 0: Normal 1: Faulty |  | 1: Running
18 | DCDC Battery-side current 2 | [-3276,3276] | A | 18 | Controller battery side short-circuit | 0: Normal 1: Faulty |  | 2: Sleep
19 | DCDC ISO insulation resistance 2 | [0, 65.535] | MΩ | 19 | Controller battery side reverse polarity | 0: Normal 1: Faulty |  | 3: Charging
20 | Rack 1-Quantity of working packs | [0, 65535] | / | 20 | Controller bus side overvoltage | 0: Normal 1: Faulty |  | 4: Discharging
21 | Rack 1-Device status | 1: In operation 2: Hibernating 3: Charging 4: Discharging 5: Shut down 6. Faulty 7: Offline 8: Self-check in progress 49152: Loading | / | 21 | Controller bus side reverse polarity | 0: Normal 1: Faulty |  | 5: Power off
22 | Rack 1-Voltage | [-3276,3276] | V | 22 | Controller insulation resistance abnormal | 0: Normal 1: Faulty |  | 6: Faulted
23 | Rack 1-Current | [-3276,3276] | A | 23 | Controller temperature high | 0: Normal 1: Faulty |  | 7: Off-line
24 | Rack 1-SOC | [0, 100] | % | 24 | Controller battery terminal temperature high | 0: Normal 1: Faulty |  | 8: Self-check in progress
25 | Rack 1-SOH | [0, 100] | % | 25 | Controller bus terminal temperature high | 0: Normal 1: Faulty |  | 49152: Loading
26 | Rack 1-SOE | [0, 100] | % | 26 | Controller version mismatch | 0: Normal 1: Faulty
27 | Rack 1-DOD | [0, 100] | % | 27 | Controller internal fan faulty | 0: Normal 1: Faulty
28 | Rack 1-Charge/Discharge power | [-3.4E+38, 3.4E+38] | kW | 28 | Pack monitoring board error | 0: Normal 1: Faulty
29 | Rack 1-Chargeable capacity | [0, 3.4E+38] | kWh | 29 | Pack internal error | 0: Normal 1: Faulty
30 | Rack 1-Dischargeable capacity | [0, 3.4E+38] | kWh | 30 | Pack lockout | 0: Normal 1: Faulty
31 | Rack 1-Highest pack temperature | [-327,327] | °C | 31 | Pack fan faulty | 0: Normal 1: Faulty
32 | Rack 1-Pack with highest temperature | [0, 65535] | / | 32 | Pack temperature imbalance | 0: Normal 1: Faulty
33 | Rack 1-Lowest pack temperature | [-327,327] | °C | 33 | Pack overvoltage | 0: Normal 1: Faulty
34 | Rack 1-Pack with lowest temperature | [0, 65535] | / | 34 | Controller power control unit communication error | 0: Normal 1: Faulty
35 | Rack 1-Lowest pack voltage | [0, 6553] | V | 35 | Controller connection detection error | 0: Normal 1: Faulty
36 | Rack 1-Pack with lowest voltage | [0, 65535] | / | 36 |  | 0: Normal 1: Faulty
37 | Rack 1-Highest pack voltage | [0, 6553] | V | 37 | Optimizer error | 0: Normal 1: Faulty
38 | Rack 1-Pack with highest voltage | [0, 65535] | / | 38 | Optimizer temperature high | 0: Normal 1: Faulty
39 | Rack 1-Energy charged of the day | [0, 3.4E+38] | kWh | 39 | Optimizer terminal temperature high | 0: Normal 1: Faulty
40 | Rack 1-Energy discharged of the day | [0, 3.4E+38] | kWh | 40 | Optimizer version mismatch | 0: Normal 1: Faulty
41 | Rack 1-Energy charged of the month | [0, 3.4E+38] | kWh | 41 | Incorrect controller bus connection | 0: Normal 1: Faulty
42 | Rack 1-Energy discharged of the month | [0, 3.4E+38] | kWh | 42 | Loose pack connection to copper bar | 0: Normal 1: Faulty
43 | Rack 1-Energy charged of the year | [0, 3.4E+38] | kWh | 43 | Controller rapid shutdown connection detection error | 0: Normal 1: Faulty
44 | Rack 1-Energy discharged of the year | [0, 3.4E+38] | kWh | 44 | Pack SOH low | 0: Normal 1: Faulty
45 | Rack 1-Total charged energy | [0, 3.4E+38] | kWh | 45 | Pack overcurrent | 0: Normal 1: Faulty
46 | Rack 1-Total discharged energy | [0, 3.4E+38] | kWh | 46 | Pack temperature high | 0: Normal 1: Faulty
47 | Rack 2-Quantity of working packs | 1: In operation 2: Hibernating 3: Charging 4: Discharging 5: Shut down 6. Faulty 7: Offline 8: Self-check in progress 49152: Loading | / | 47 | Pack temperature low | 0: Normal 1: Faulty
48 | Rack 2-Device status | [0, 65535] | / | 48 | Pack undervoltage | 0: Normal 1: Faulty
49 | Rack 2-Voltage | [-3276,3276] | V | 49 | Pack aux. power supply faulty | 0: Normal 1: Faulty
50 | Rack 2-Current | [-3276,3276] | A | 50 | Invalid | /
51 | Rack 2-SOC | [0, 100] | % | 51 | Invalid | /
52 | Rack 2-SOH | [0, 100] | % | 52 | Invalid | /
53 | Rack 2-SOE | [0, 100] | % | 53 | DC aux. power supply of controller faulty | 0: Normal 1: Faulty
54 | Rack 2-DOD | [0, 100] | % | 54 | External Fan of Rack Controller Faulty | 0: Normal 1: Faulty
55 | Rack 2-Charge/Discharge power | [-3.4E+38, 3.4E+38] | kW | 55 | Rack Controller Temperature Abnormal | 0: Normal 1: Faulty
56 | Rack 2-Chargeable capacity | [0, 3.4E+38] | kWh | 56 | Optimizer temperature low | 0: Normal 1: Faulty
57 | Rack 2-Dischargeable capacity | [0, 3.4E+38] | kWh | 57 | Emergency Power-Off | 0: Normal 1: Faulty
58 | Rack 2-Highest pack temperature | [-327,327] | °C | 58 | Controller-pack version inconsistency | 0: Normal 1: Faulty
59 | Rack 2-Pack with highest temperature | [0, 65535] | / | 59 | Controller-pack version mismatch | 0: Normal 1: Faulty
60 | Rack 2-Lowest pack temperature | [-327,327] | °C | 60 | Communication error between controller and PCS | 0: Normal 1: Faulty
61 | Rack 2-Pack with lowest temperature | [0, 65535] | / | 61 | Communication error between BCU and SmartLogger | 0: Normal 1: Faulty
62 | Rack 2-Lowest pack voltage | [0, 6553] | V
63 | Rack 2-Pack with lowest voltage | [0, 65535] | /
64 | Rack 2-Highest pack voltage | [0, 6553] | V
65 | Rack 2-Pack with highest voltage | [0, 65535] | /
66 | Rack 2-Energy charged of the day | [0, 3.4E+38] | kWh
67 | Rack 2-Energy discharged of the day | [0, 3.4E+38] | kWh
68 | Rack 2-Energy charged of the month | [0, 3.4E+38] | kWh
69 | Rack 2-Energy discharged of the month | [0, 3.4E+38] | kWh
70 | Rack 2-Energy charged of the year | [0, 3.4E+38] | kWh
71 | Rack 2-Energy discharged of the year | [0, 3.4E+38] | kWh
72 | Rack 2-Total charged energy | [0, 3.4E+38] | kWh
73 | Rack 2-Total discharged energy | [0, 3.4E+38] | kWh
Note 1. The ratio of DCDCs to battery racks is closely related to the discharge rate. For example, in the 1C scenario, each battery rack is configured with a DCDC; in the 0.5C scenario, two battery racks share a DCDC. Among the preceding BCU telemetering signals, "DCDC Running state", "DCDC Bus-side voltage", ..., and "DCDC ISO insulation resistance" signals are used in the 1C scenario, whereas "DCDC Running state 1" and "DCDC Bus-side voltage 1", ..., and "DCDC ISO insulation resistance 2" signals are used in the 0.5C scenario.
2. DCDC running state, DCDC running state 1, and DCDC running state 2 have the same definitions. For details, see the following enumeration definitions.
DCDC Running Status
0-Standby
1-Standby: safe mode
2-Standby: cable connection detection
256-Soft start
512-Running
513-Operating: limited power
514-Operating: self-derating
515-Running: Current limiting
768-Unexpected shutdown
769-Commanded shutdown
770-Emergency power off
771-Charge/Discharge disabled
772-Battery pack rapid shutdown
45056-off-line
49152-Loading

## ESS (new-generation industrial
Telemetry | [5 empty] | Teleindication |  |  |  | Telecontrol |  |  |  | Teleadjust
No. | Signal Name | Unit | Precision | Range | Remarks | No. | Signal Name | Status | Remarks | No. | Signal Name | Command | Remarks | No. | Signal Name | Unit | Precision | Range
1 | A-B line voltage of the power grid | V | 0.1 | [0,6553] |  | 1 | Communication failure | 0: normal 1: faulty |  | 1 | Power on | 0: effective1: invalid | Select one of the two according to the actual situation and the power-on/off control
2 | B-C line voltage of the power grid | V | 0.1 | [0,6553] |  | 2 | Standby | Running status of the energy storage cabinet 0: not in this state 1: current status of the battery cabinet |  | 2 | Shutdown | 0: effective1: invalid
3 | Power grid C-A line voltage | V | 0.1 | [0,6553] |  | 3 | Running |  | The overall status is running. | 3 | Power-on/off control | 0: power off1: power on
4 | Phase A voltage of the power grid | V | 0.1 | [0,6553] |  | 4 | Shut down |  | The overall status is shutdown.
5 | Phase B voltage of the power grid | V | 0.1 | [0,6553] |  | 5 | Spot check
6 | Phase C voltage of the power grid | V | 0.1 | [0,6553] |  | 6 | Retained |  | Reserved for overall status expansion
7 | Phase A current of the power grid | A | 0.001 | [-327,327] |  | 7 | Normal operation |  | Breakdown Status of Run
8 | Phase B current of the power grid | A | 0.001 | [-327,327] |  | 8 | Power-limited derating operation |  | Breakdown Status of Run
9 | Phase C current of the power grid | A | 0.001 | [-327,327] |  | 9 | Self-derating operation |  | Breakdown Status of Run
10 | Power grid frequency | Hz | 0.01 | [0, 655] |  | 10 | Locked operation |  | Breakdown Status of Run
11 | Active power | kW | 0.001 | [-3.4E+38, 3.4E+38] |  | 11 | Hot backup operation |  | Breakdown Status of Run
12 | Reactive power | kVar | 0.001 | [-3.4E+38, 3.4E+38] |  | 12 | Retained |  | Reserved for run breakdown status
13 | Power Factor | N/A | 0.001 | (-1, 1] |  | 13 | Normal shutdown |  | Shutdown breakdown status
14 | Electricity generated on the current day | kWh | 0.01 | [0, 3.4E+38] |  | 14 | Abnormal shutdown |  | Shutdown breakdown status
15 | Electricity Generated in the Current Month | kWh | 0.01 | [0, 3.4E+38] |  | 15 | Power-limited shutdown |  | Shutdown breakdown status
16 | Electricity generated in the current year | kWh | 0.01 | [0, 3.4E+38] |  | 16 | Retained |  | Reserved for shutdown breakdown status
17 | Accumulated generated electricity | kWh | 0.01 | [0, 3.4E+38] |  | 17 | Power loss alarm | 0: normal1: faulty
18 | Current-day absorbed power | kWh | 0.01 | [0, 3.4E+38] |  | 18 | Abnormal power supply voltage | 0: normal1: faulty
[6 empty] | 19 | The power frequency is abnormal. | 0: normal1: faulty
19 | Electricity absorbed in the current month | kWh | 0.01 | [0, 3.4E+38] |  | 20 | The outdoor temperature sensor is faulty. | 0: normal1: faulty
[6 empty] | 21 | Outdoor low temperature alarm | 0: normal1: faulty
20 | Electricity absorbed in the current year | kWh | 0.01 | [0, 3.4E+38] |  | 22 | Liquid cooling unit communication error | 0: normal1: faulty
[6 empty] | 23 | Liquid cooling unit expiration alarm | 0: normal1: faulty
[6 empty] | 24 | The certificate is about to expire. | 0: normal1: faulty
[6 empty] | 25 | The certificate has expired. | 0: normal1: faulty
21 | Accumulated absorbed electricity | kWh | 0.01 | [0, 3.4E+38] |  | 26 | Compressor discharge high pressure alarm | 0: normal1: faulty
22 | Working status | / | / | 0x0000 Standby 0x0100 Startup 0x0200: PQ running 0x0201 Run: The VSG is running. 0x0202 Run: hot backup 0x0204 Run: limited power 0x0205: The power module is derated. 0x0206: battery current limiting 0x0207: indicates that the ESS is derated. 0x0208 Run: Locked 0x0300: abnormal shutdown 0x0301: shutdown command 0x0302 Power-off: Power-on authorization is not performed. 0x0303 Shutdown 0x0304: The EPO module shuts down. 0x0305: AC power-off 0x0400: ready for spot check 0x0401 Spot check: The spot check is in progress. 0xB000 Offline 0xC000 Loading |  | 27 | Compressor suction low pressure alarm | 0: normal1: faulty
23 | Work mode | / | / | 0：PQ 1：VSG |  | 28 | Compressor low superheat alarm | 0: normal1: faulty
24 | Rated power | kWh | 0.001 | [0, 3.4E+38] |  | 29 | Compressor discharge pressure sensor fault | 0: normal1: faulty
[6 empty] | 30 | Condenser outlet pressure sensor fault | 0: normal1: faulty
[6 empty] | 31 | Condenser outlet temperature sensor fault | 0: normal1: faulty
25 | rated power | kW | 0.001 | [0, 3.4E+38] |  | 32 | Compressor suction pressure sensor fault | 0: normal1: faulty
26 | SOC | % | 1 | [0, 100] |  | 33 | Compressor suction temperature sensor fault | 0: normal1: faulty
[6 empty] | 34 | The dehumidification temperature sensor is faulty. | 0: normal1: faulty
27 | Current-day charging capacity | kWh | 0.01 | [0, 3.4E+38] |  | 35 | Compressor Drive Alarm | 0: normal1: faulty
28 | Current-day discharge capacity | kWh | 0.01 | [0, 3.4E+38] |  | 36 | The compressor drive output is abnormal. | 0: normal1: faulty
29 | Electricity charged in the current month | kWh | 0.01 | [0, 3.4E+38] |  | 37 | Compressor overcurrent alarm | 0: normal1: faulty
30 | Discharged electricity in the current month | kWh | 0.01 | [0, 3.4E+38] |  | 38 | Compressor drive communication error. | 0: normal1: faulty
31 | Electricity charged in the current year | kWh | 0.01 | [0, 3.4E+38] |  | 39 | Exhaust high temperature alarm | 0: normal1: faulty
32 | Discharge power of the year | kWh | 0.01 | [0, 3.4E+38] |  | 40 | Compressor exhaust temperature sensor fault | 0: normal1: faulty
33 | Accumulated charge capacity | kWh | 0.01 | [0, 3.4E+38] |  | 41 | The auxiliary source is abnormal. | 0: normal1: faulty
34 | Accumulated discharge capacity | kWh | 0.01 | [0, 3.4E+38] |  | 42 | The outdoor heat dissipation module is dirty and blocked. | 0: normal1: faulty
[6 empty] | 43 | The temperature sensor of the outdoor heat exchanger is faulty. | 0: normal1: faulty
35 | Charge/discharge power | kW | 0.001 | [-3.4E+38, 3.4E+38] |  | 44 | Outdoor fan fault | 0: normal1: faulty
[6 empty] | 45 | The dehumidifier fan is faulty. | 0: normal1: faulty
36 | Rechargeable battery | kWh | 0.001 | [0, 3.4E+38] |  | 46 | The electric heater is faulty. | 0: normal1: faulty
37 | Dischargeable capacity | kWh | 0.001 | [0, 3.4E+38] |  | 47 | Electric heater overvoltage alarm | 0: normal1: faulty
38 | Energy storage compartment temperature 1 | ℃ | 0.1 | [-3276,3276] |  | 48 | The water supply temperature sensor on the power side is faulty. | 0: normal1: faulty
39 | Energy storage compartment humidity 1 | % | 0.1 | [0, 100] |  | 49 | The return water temperature sensor on the power side is faulty. | 0: normal1: faulty
40 | Energy storage compartment temperature 2 | ℃ | 0.1 | [-3276,3276] |  | 50 | The supply and return water temperature sensor on the power side is abnormal. | 0: normal1: faulty
41 | Energy storage compartment humidity 2 | % | 0.1 | [0, 100] |  | 51 | The water supply temperature sensor on the battery side is faulty. | 0: normal1: faulty
42 | Exhaust fan 1 speed | RPM | 1 | [0, 65535] |  | 52 | The return water temperature sensor on the battery side is faulty. | 0: normal1: faulty
43 | Exhaust fan 2 speed | RPM | 1 | [0, 65535] |  | 53 | The supply and return water temperature sensor on the battery side is abnormal. | 0: normal1: faulty
44 | CO sensor 1 gas concentration | ppm | 1 | [0, 65535] |  | 54 | Battery side water supply high temperature alarm | 0: normal1: faulty
45 | H2 Sensor 1 Gas Concentration | ppm | 1 | [0, 65535] |  | 55 | Battery side water supply low temperature alarm | 0: normal1: faulty
46 | Active power of auxiliary source | kW | 0.001 | [-3.4E+38, 3.4E+38] |  | 56 | Coolant Expiration Alarm | 0: normal1: faulty
47 | Auxiliary source reactive power | kVar | 0.001 | [-3.4E+38, 3.4E+38] |  | 57 | Coolant Expired Shutdown Alarm | 0: normal1: faulty
48 | Auxiliary power factor | / | 0.001 | (-1, 1] |  | 58 | Coolant Change Not Completed | 0: normal1: faulty
49 | Total auxiliary power consumption | kWh | 0.01 | [0, 3.4E+38] |  | 59 | The water pump power supply is abnormal. | 0: normal1: faulty
50 | DCDC busbar side voltage | V | 0.1 | [0,6553] |  | 60 | The water pump is not functioning properly. | 0: normal1: faulty
51 | DCDC bus side current | A | 0.1 | [-3276,3276] |  | 61 | Water pump failure | 0: normal1: faulty
52 | DCDC bus side power | kW | 0.001 | [-3.4E+38, 3.4E+38] |  | 62 | Multi-way valve communication error | 0: normal1: faulty
53 | DCDC Internal Temperature | ℃ | 0.1 | [-3276,3276] |  | 63 | Multi-way valve power supply abnormal | 0: normal1: faulty
54 | DCDC battery side voltage | V | 0.1 | [-3276,3276] |  | 64 | Multi-way valve failure | 0: normal1: faulty
55 | Cluster voltage | V | 0.1 | [-3276,3276] |  | 65 | Water tank low level alarm | 0: normal1: faulty
56 | Cluster current | A | 0.1 | [-3276,3276] |  | 66 | The AC SPD is faulty. | 0: normal1: faulty
57 | SOH | % | 1 | [0, 100] |  | 67 | Door status alarm | 0: normal1: faulty
58 | SOE | % | 1 | [0, 100] |  | 68 | The battery compartment door is open. | 0: normal1: faulty
59 | DOD | % | 1 | [0, 100] |  | 69 | Water Alarm | 0: normal1: faulty
60 | Maximum battery pack temperature | ℃ | 0.01 | [-327,327] |  | 70 | smoke detector alarm | 0: normal1: faulty
61 | Location of the highest battery pack temperature | / | 1 | [0, 65535] |  | 71 | High concentration of combustible gases | 0: normal1: faulty
62 | Minimum battery pack temperature | ℃ | 0.01 | [-327,327] |  | 72 | Combustible gas detector communication failure | 0: normal1: faulty
63 | Location of the lowest battery pack temperature | / | 1 | [0, 65535] |  | 73 | Combustible gas detector failure | 0: normal1: faulty
64 | Minimum battery pack voltage | V | 0.1 | [0, 6553] |  | 74 | Temperature and humidity sensor communication failure | 0: normal1: faulty
65 | Location of the lowest battery pack voltage | / | 1 | [0, 65535] |  | 75 | The temperature and humidity sensor is faulty. | 0: normal1: faulty
66 | Maximum battery pack voltage | V | 0.1 | [0, 6553] |  | 76 | Heat detector alarm | 0: normal1: faulty
67 | Location of highest battery pack voltage | / | 1 | [0, 65535] |  | 77 | The ambient temperature inside the cabin is too high. | 0: normal1: faulty
68 | Running status of the liquid cooling unit | / | / | 0: disabled; 1: self-loop; 2: cooling; 3: heating; |  | 78 | EPO emergency stop alarm | 0: normal1: faulty
69 | Outdoor temperature | ℃ | 0.1 | [-50, 150] |  | 79 | Fire alarm | 0: normal1: faulty
70 | Supply water temperature at the battery side | ℃ | 0.1 | [-50, 150] |  | 80 | The exhaust fan is faulty. | 0: normal1: faulty
71 | Water return temperature at the battery side | ℃ | 0.1 | [-50, 150] |  | 81 | The device access does not match the device configuration. | 0: normal1: faulty
72 | Supply water temperature on the power side | ℃ | 0.1 | [-50, 150] |  | 82 | Thermal runaway suppression device abnormal | 0: normal1: faulty
73 | Power side return water temperature | ℃ | 0.1 | [-50, 150] |  | 83 | Thermal Runaway Suppression Device Zone Control | 0: normal1: faulty
[6 empty] | 84 | The relative humidity in the cabin is too high. | 0: normal1: faulty
[6 empty] | 85 | The offering software package is not backed up. | 0: normal1: faulty
[6 empty] | 86 | Inconsistent component software versions | 0: normal1: faulty
[6 empty] | 87 | The electronic label board data is abnormal. | 0: normal1: faulty
[6 empty] | 88 | The certificate will expire. | 0: normal1: faulty
[6 empty] | 89 | The certificate has expired. | 0: normal1: faulty
[6 empty] | 90 | The communication between the upper-layer controller is abnormal. | 0: normal1: faulty
[6 empty] | 91 | Thermal Runaway Suppression Device Communication Abnormal | 0: normal1: faulty
[6 empty] | 92 | Auxiliary power meter communication exception | 0: normal1: faulty
[6 empty] | 93 | Display module communication is abnormal. | 0: normal1: faulty
[6 empty] | 94 | Power-on authorization is not enabled. | 0: normal1: faulty
[6 empty] | 95 | Thermal runaway suppression device agent eruption | 0: normal1: faulty
[6 empty] | 96 | The battery pack power connection is abnormal. | 0: normal1: faulty
[6 empty] | 97 | Battery pack end of life | 0: normal1: faulty
[6 empty] | 98 | Battery pack overvoltage | 0: normal1: faulty
[6 empty] | 99 | Battery pack undervoltage | 0: normal1: faulty
[6 empty] | 100 | Battery overcurrent protection | 0: normal1: faulty
[6 empty] | 101 | Battery pack overtemperature | 0: normal1: faulty
[6 empty] | 102 | Battery pack low temperature | 0: normal1: faulty
[6 empty] | 103 | The battery pack is locked. | 0: normal1: faulty
[6 empty] | 104 | The battery is faulty. | 0: normal1: faulty
[6 empty] | 105 | The SOH of the battery pack is too low. | 0: normal1: faulty
[6 empty] | 106 | Battery pack sampling exception | 0: normal1: faulty
[6 empty] | 107 | Battery pack configuration data is abnormal. | 0: normal1: faulty
[6 empty] | 108 | The battery pack specifications do not match the entire system. | 0: normal1: faulty
[6 empty] | 109 | The electrochemical cell temperature rise is abnormal. | 0: normal1: faulty
[6 empty] | 110 | Pack thermal runaway alarm | 0: normal1: faulty
[6 empty] | 111 | Battery pack recharge failure | 0: normal1: faulty
[6 empty] | 112 | Equalization module overcurrent protection | 0: normal1: faulty
[6 empty] | 113 | The internal communication of the equalization module is abnormal. | 0: normal1: faulty
[6 empty] | 114 | The bus voltage of the equalization module is abnormal. | 0: normal1: faulty
[6 empty] | 115 | The battery voltage of the equalization module is abnormal. | 0: normal1: faulty
[6 empty] | 116 | Equalization module board internal overtemperature protection | 0: normal1: faulty
[6 empty] | 117 | Overtemperature protection for the MCU on the battery side of the equalization module | 0: normal1: faulty
[6 empty] | 118 | Overtemperature protection for the connection terminal of the equalization module | 0: normal1: faulty
[6 empty] | 119 | Cable connections to the bus-side port of the equalization module are faulty. | 0: normal1: faulty
[6 empty] | 120 | The bus of the equalization module fails to be soft-started. | 0: normal1: faulty
[6 empty] | 121 | The balancing module version does not match. | 0: normal1: faulty
[6 empty] | 122 | Equalization module address pairing timed out. | 0: normal1: faulty
[6 empty] | 123 | Equalization module soft-start MOS short-circuit fault | 0: normal1: faulty
[6 empty] | 124 | The balancing module is abnormal. | 0: normal1: faulty
[6 empty] | 125 | Equalization module overcurrent fault | 0: normal1: faulty
[6 empty] | 126 | The BMU board is short-circuited. | 0: normal1: faulty
[6 empty] | 127 | BMU sampling disconnection fault | 0: normal1: faulty
[6 empty] | 128 | A BMU internal fault occurs. | 0: normal1: faulty
[6 empty] | 129 | Disconnection Between BMU Nodes | 0: normal1: faulty
[6 empty] | 130 | The BMU communication is abnormal. | 0: normal1: faulty
[6 empty] | 131 | The RPCB voltage is abnormal. | 0: normal1: faulty
[6 empty] | 132 | The RPCB port is short-circuited. | 0: normal1: faulty
[6 empty] | 133 | The internal temperature of the RPCB is abnormal. | 0: normal1: faulty
[6 empty] | 134 | RPCB overcurrent fault | 0: normal1: faulty
[6 empty] | 135 | The ISO insulation test on the battery side is abnormal. | 0: normal1: faulty
[6 empty] | 136 | The RPCB power loop is abnormal. | 0: normal1: faulty
[6 empty] | 137 | RPCB version mismatch | 0: normal1: faulty
[6 empty] | 138 | The RPCB device is abnormal. | 0: normal1: faulty
[6 empty] | 139 | Battery-side RCD protection | 0: normal1: faulty
[6 empty] | 140 | RPCB overcurrent protection | 0: normal1: faulty
[6 empty] | 141 | RPCB Fan Alarm | 0: normal1: faulty
[6 empty] | 142 | Battery ISO Insulation Detection Alarm | 0: normal1: faulty
[6 empty] | 143 | RPCB overcurrent alarm | 0: normal1: faulty
[6 empty] | 144 | The total voltage of the battery cluster is abnormal. | 0: normal1: faulty
[6 empty] | 145 | There is a large difference between the total voltage of the battery cluster and the accumulated sum of the electrochemical cells. | 0: normal1: faulty
[6 empty] | 146 | Battery packs fail to be used together. | 0: normal1: faulty
[6 empty] | 147 | BCU chip overtemperature | 0: normal1: faulty
[6 empty] | 148 | The BCU is abnormal. | 0: normal1: faulty
[6 empty] | 149 | The software version of the equalization module is inconsistent. | 0: normal1: faulty
[6 empty] | 150 | The BCU auxiliary power source is abnormal. | 0: normal1: faulty
[6 empty] | 151 | The BCU memory is abnormal. | 0: normal1: faulty
[6 empty] | 152 | The cluster power control board communication is abnormal. | 0: normal1: faulty
[6 empty] | 153 | The DCDC communication is abnormal. | 0: normal1: faulty
[6 empty] | 154 | The PCS communication is abnormal. | 0: normal1: faulty
[6 empty] | 155 | The communication of the equalization module is abnormal. | 0: normal1: faulty
[6 empty] | 156 | ESS SOH Calibration | 0: normal1: faulty
[6 empty] | 157 | The battery cluster voltage exceeds the threshold. | 0: normal1: faulty
[6 empty] | 158 | The access of the cluster device does not match the configuration of the entire system. | 0: normal1: faulty
[6 empty] | 159 | Battery sampling exception | 0: normal1: faulty
[6 empty] | 160 | Large deviation of battery voltage consistency | 0: normal1: faulty
[6 empty] | 161 | Large deviation of battery temperature consistency | 0: normal1: faulty
[6 empty] | 162 | DC-DC module protection | 0: normal1: faulty
[6 empty] | 163 | The DCDC module is faulty. | 0: normal1: faulty
[6 empty] | 164 | DC-DC module bus-side port overvoltage protection | 0: normal1: faulty
[6 empty] | 165 | DCDC module over-humidity protection | 0: normal1: faulty
[6 empty] | 166 | DC-DC module overtemperature protection | 0: normal1: faulty
[6 empty] | 167 | Low temperature protection for the DC-DC module | 0: normal1: faulty
[6 empty] | 168 | DCDC module bus-side terminal overtemperature protection | 0: normal1: faulty
[6 empty] | 169 | Overtemperature protection for battery terminals on the DCDC module | 0: normal1: faulty
[6 empty] | 170 | The liquid cooling temperature of the DCDC module is abnormal. | 0: normal1: faulty
[6 empty] | 171 | DC-DC module version mismatch protection | 0: normal1: faulty
[6 empty] | 172 | The NTC of the DC-DC module is faulty. | 0: normal1: faulty
[6 empty] | 173 | The DSP_EPO of the DC-DC module is faulty. | 0: normal1: faulty
[6 empty] | 174 | Short-circuit protection of the DC-DC module | 0: normal1: faulty
[6 empty] | 175 | DC-DC module bus overvoltage fault | 0: normal1: faulty
[6 empty] | 176 | PCS DC overvoltage | 0: normal1: faulty
[6 empty] | 177 | PCS DC reverse connection | 0: normal1: faulty
[6 empty] | 178 | The phase cable of the PCS power grid is short-circuited to the PE. | 0: normal1: faulty
[6 empty] | 179 | PCS power grid failure | 0: normal1: faulty
[6 empty] | 180 | PCS grid undervoltage | 0: normal1: faulty
[6 empty] | 181 | PCS grid overvoltage | 0: normal1: faulty
[6 empty] | 182 | PCS Power Grid Voltage Imbalance | 0: normal1: faulty
[6 empty] | 183 | PCS grid overfrequency | 0: normal1: faulty
[6 empty] | 184 | PCS grid underfrequency | 0: normal1: faulty
[6 empty] | 185 | The PCS power grid frequency is unstable. | 0: normal1: faulty
[6 empty] | 186 | PCS AC overcurrent | 0: normal1: faulty
[6 empty] | 187 | The DC component of the PCS is too large. | 0: normal1: faulty
[6 empty] | 188 | Reverse phase sequence on the AC side of the PCS | 0: normal1: faulty
[6 empty] | 189 | PCS residual current abnormality | 0: normal1: faulty
[6 empty] | 190 | Abnormal grounding of PCS system | 0: normal1: faulty
[6 empty] | 191 | Low PCS insulation impedance | 0: normal1: faulty
[6 empty] | 192 | PCS temperature too high | 0: normal1: faulty
[6 empty] | 193 | The PCS device is abnormal. | 0: normal1: faulty
[6 empty] | 194 | The PCS upgrade fails or the version does not match. | 0: normal1: faulty
[6 empty] | 195 | The fan inside the PCS is abnormal. | 0: normal1: faulty
[6 empty] | 196 | The temperature of the PCS AC terminal is abnormal. | 0: normal1: faulty
[6 empty] | 197 | The temperature of the PCS DC terminal is abnormal. | 0: normal1: faulty
[6 empty] | 198 | PCS Black Startup Failure | 0: normal1: faulty
[6 empty] | 199 | The time sequence of the PCS black boot command is abnormal. | 0: normal1: faulty
[6 empty] | 200 | The PCS fuse is broken. | 0: normal1: faulty
[6 empty] | 201 | PCS fuse self-check error | 0: normal1: faulty
[6 empty] | 202 | PCS FASTIO self-check exception | 0: normal1: faulty
[6 empty] | 203 | PCS DC bus short circuit | 0: normal1: faulty
[6 empty] | 204 | PCS relay overtemperature | 0: normal1: faulty

## PCS (new-generation energy stor
Telemetry |  |  |  | Teleindication | 信号名称CN | 状态 | Telecontrol | 信号名称CN | 命令 | Teleadjust
No. | Signal Name | Unit | Range | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | A-B line voltage of the power grid | V | [0,6553] | 1 | Communication fault | 0: normal 1: faulty | 1 | Power-on control | 0: On1: Invalid
2 | B-C line voltage of the power grid | V | [0,6553] | 2 | latching state | 0: barred1: unbarred | 2 | Shutdown control | 0: Power off1: Invalid
3 | Power grid C-A line voltage | V | [0,6553] | 3 | Reserved | / | 3 | Power-on/off control | 0: power off1: power on
4 | Phase A voltage of the power grid | V | [0,6553] | 4 | Standby | PCS running status 0: not in this state 1: PCS Current State
5 | Phase B voltage of the power grid | V | [0,6553] | 5 | Runs
6 | Phase C voltage of the power grid | V | [0,6553] | 6 | Shutdown
7 | Phase A current of the power grid | A | [-327,327] | 7 | Spot check
8 | Phase B current of the power grid | A | [-327,327] | 8 | Reserved
9 | Phase C current of the power grid | A | [-327,327] | 9 | Normal operation
10 | Power grid frequency | Hz | [0, 655] | 10 | Power-limited derating operation
11 | Active power | kW | [-3.4E+38, 3.4E+38] | 11 | Self-derating operation
12 | Reactive power | kVar | [-3.4E+38, 3.4E+38] | 12 | Hot Standby Operation
13 | Power Factor | N/A | (-1, 1] | 13 | Reserved
14 | DC voltage | V | [0,6553] | 14 | Normal Shutdown
15 | direct current | A | [-327,327] | 15 | Fault shutdown
16 | Total power on the DC side | kW | [-3.4E+38, 3.4E+38] | 16 | Shutdown due to power restriction
17 | Internal temperature | ℃ | [-3276,3276] | 17 | Reserved
18 | Electricity generated on the current day | kWh | [0, 3.4E+38] | 18 | The phase line of the power grid is short-circuited to PE. | 0: normal 1: faulty
19 | Electricity Generated in the Current Month | kWh | [0, 3.4E+38] | 19 | Power grid failure | 0: normal 1: faulty
20 | Electricity generated in the current year | kWh | [0, 3.4E+38] | 20 | Power grid undervoltage | 0: normal 1: faulty
21 | Accumulated generated electricity | kWh | [0, 3.4E+38] | 21 | Power grid overvoltage | 0: normal 1: faulty
22 | Current-day absorbed power | kWh | [0, 3.4E+38] | 22 | Power grid voltage imbalance | 0: normal 1: faulty
23 | Electricity absorbed in the current month | kWh | [0, 3.4E+38] | 23 | Power grid overfrequency | 0: normal 1: faulty
24 | Electricity absorbed in the current year | kWh | [0, 3.4E+38] | 24 | Power grid underfrequency | 0: normal 1: faulty
25 | Accumulated absorbed electricity | kWh | [0, 3.4E+38] | 25 | Unstable power grid frequency | 0: normal 1: faulty
26 | Work mode | / | 0：PQ 1：VSG | 26 | Output overcurrent | 0: normal 1: faulty
27 | Running Status | / | 0x0000: standby: initialization 0x0001: standby: insulation resistance detection 0x0003: standby: power grid detection 0x0005: standby: cable connection check 0x0006: Standby: soft-starting 0x0100: start 0x0204: Run: Hot Standby 0x0205: Run: Reactive power compensation for hot backup 0x0206:Run: PQ run 0x0207:Run: VSG running 0x0208:Running: Limit Power 0x0209: Run: Self-derating 0x0300: shutdown: abnormal shutdown 0x0301: shutdown: shutdown by command 0x0302: Shutdown: OVGR 0x0303: Power off: Communication is disconnected. 0x0304: Shutdown: Power limited 0x0305: Power off: Power on manually 0x0306: Shutdown: The DC switch is off. 0x0307: Shutdown: Fast Shutdown 0x0308: shutdown: input underpower 0x030A: Shutdown: command for quick shutdown 0x0401: Power grid scheduling: cos phi-P curve 0x0402: Power grid scheduling: Q-U curve 0x0403: Power grid scheduling: PF-U curve 0x0404: power grid scheduling: dry contact 0x0405: Power grid scheduling: Q-P curve 0x0500: ready for spot check 0x0501: Spot check in progress 0x0600: The inspection is in progress. 0X0900: DC input detection 0xA001: standby: no DC input 0xB000: Communication is interrupted. 0xC000: Loading | 27 | The DC component of the output current is too large. | 0: normal 1: faulty | <-Descriptions： | Running status
28 | Startup time | / | [0, 3.4E+38] | 28 | Abnormal residual current | 0: normal 1: faulty |  | 0-3、256、769-778、1792、2304、2560、40960、40961 | Standby
29 | Power-off time | / | [0, 3.4E+38] | 29 | Abnormal system grounding | 0: normal 1: faulty |  | 512-515、1025-1029、1280、1281、1536、2048 | Runs
|  |  |  | 30 | Low insulation resistance | 0: normal 1: faulty |  | 2816 | broken chain
|  |  |  | 31 | Temperature too high | 0: normal 1: faulty |  | 768 | Abnormal shutdown
|  |  |  | 32 | Device abnormality | 0: normal 1: faulty |  | 49152 | Loading...
|  |  |  | 33 | Upgrade failed. | 0: normal 1: faulty
|  |  |  | 34 | The monitoring unit is faulty. | 0: normal 1: faulty
|  |  |  | 35 | The external fan is abnormal. | 0: normal 1: faulty
|  |  |  | 36 | The internal fan is abnormal. | 0: normal 1: faulty
|  |  |  | 37 | DC input overvoltage | 0: normal 1: faulty
|  |  |  | 38 | DC input reverse connection | 0: normal 1: faulty
|  |  |  | 39 | Input short-circuit or reverse connection | 0: normal 1: faulty
|  |  |  | 40 | input concatenation | 0: normal 1: faulty
|  |  |  | 41 | DC is not reliably connected | 0: normal 1: faulty
|  |  |  | 42 | Parallel communication abnormal | 0: normal 1: faulty
|  |  |  | 43 | Reversed phase sequence on the AC side | 0: normal 1: faulty
|  |  |  | 44 | String-to-ground short circuit | 0: normal 1: faulty
|  |  |  | 45 | Communication disconnection failure protection | 0: normal 1: faulty
|  |  |  | 46 | AC terminal temperature abnormal | 0: normal 1: faulty
|  |  |  | 47 | DC terminal temperature abnormal | 0: normal 1: faulty
|  |  |  | 48 | Black start failure | 0: normal 1: faulty
|  |  |  | 49 | Black start command sequence abnormal | 0: normal 1: faulty
|  |  |  | 50 | Abnormal DC input | 0: normal 1: faulty

## CMU (new-generation energy stor
Telemetry |  |  |  |  | Teleindication | 信号名称CN | 状态 | Telecontrol | 信号名称CN | 命令 | Teleadjust
NO. | Signal Name | Accuracy | Range | Unit | NO. | Signal Name | Status | NO. | Signal Name | Commands | NO. | Signal Name | Unit | Precision
1 | Rated power | 0.001 | [0, 3.4E+38] | kWh | 1 | Communication failure | 0: normal1: faulty
2 | rated power | 0.001 | [0, 3.4E+38] | kW | 2 | Energy storage compartment door | 0: off1: on
3 | SOC | 1 | [0, 100] | % | 3 | Integrated control cabin left door | 0: off1: on
4 | Charge/discharge power | 0.001 | [-3.4E+38, 3.4E+38] | kW | 4 | Integrated control cabin right door | 0: off1: on
5 | Rechargeable battery | 0.001 | [0, 3.4E+38] | kWh | 5 | Water in the battery compartment | 0: normal1: alarm
6 | Dischargeable capacity | 0.001 | [0, 3.4E+38] | kWh | 6 | Comprehensive control compartment water alarm | 0: normal1: alarm
7 | Current-day charging capacity | 0.01 | [0, 3.4E+38] | kWh | 7 | Abnormal power supply voltage | 0: normal1: alarm
8 | Current-day discharge capacity | 0.01 | [0, 3.4E+38] | kWh | 8 | The outdoor temperature sensor is faulty. | 0: normal1: alarm
9 | Electricity charged in the current month | 0.01 | [0, 3.4E+38] | kWh | 9 | Outdoor low temperature alarm | 0: normal1: alarm
10 | Discharged electricity in the current month | 0.01 | [0, 3.4E+38] | kWh | 10 | Liquid cooling unit communication error | 0: normal1: fire alarm
11 | Electricity charged in the current year | 0.01 | [0, 3.4E+38] | kWh | 11 | Power open phase alarm | 0: normal1: fire alarm
12 | Discharge power of the year | 0.01 | [0, 3.4E+38] | kWh | 12 | The power supply to the compressor drive is abnormal. | 0: normal1: alarm
13 | Accumulated charge capacity | 0.01 | [0, 3.4E+38] | kWh | 13 | Rehydration pump power supply abnormal | 0: normal1: alarm
14 | Accumulated discharge capacity | 0.01 | [0, 3.4E+38] | kWh | 14 | Rehydration pump failure | 0: normal1: alarm
15 | ESU compartment temperature 1 | 0.1 | [-3276,3276] | ℃ | 15 | Water pump drive communication error | 0: normal1: alarm
16 | Battery compartment humidity 1 | 0.1 | [0, 100] | % | 16 | Water pump drive alarm | 0: normal1: alarm
17 | ESU compartment temperature 2 | 0.1 | [-3276,3276] | ℃ | 17 | Water pump drive power supply abnormal | 0: normal1: alarm
18 | Battery compartment humidity 2 | 0.1 | [0, 100] | % | 18 | Water pump drive output abnormal | 0: normal1: alarm
19 | CO gas concentration 1 | 1 | [0, 65535] | ppm | 19 | Water pump drive overcurrent alarm | 0: normal1: alarm
20 | CO gas concentration 2 | 1 | [0, 65535] | ppm | 20 | Electric control box spoiler fault | 0: normal1: alarm
21 | H2 gas concentration 1 | 1 | [0, 65535] | ℃ | 21 | Compressor discharge high pressure alarm | 0: normal1: alarm
22 | H2 gas concentration 2 | 1 | [0, 65535] | % | 22 | Compressor suction low pressure alarm | 0: normal1: alarm
23 | Temperature of integrated control cabin | 0.1 | [-3276,3276] | ℃ | 23 | Compressor low superheat alarm | 0: normal1: alarm
24 | Integrated control cabin humidity | 0.1 | [0, 100] | % | 24 | Compressor discharge pressure sensor fault | 0: normal1: alarm
25 | Active power of auxiliary source | 0.001 | [-3.4E+38, 3.4E+38] | kW | 25 | Condenser outlet pressure sensor fault | 0: normal1: alarm
26 | Auxiliary source reactive power | 0.001 | [-3.4E+38, 3.4E+38] | kVar | 26 | Condenser outlet temperature sensor fault | 0: normal1: alarm
27 | Auxiliary power factor | 0.001 | [-1, 1] | N/A | 27 | Compressor suction pressure sensor fault | 0: normal1: alarm
28 | Daily auxiliary power consumption | 0.01 | [0, 3.4E+38] | kWh | 28 | Compressor suction temperature sensor fault | 0: normal1: alarm
29 | Total auxiliary power consumption | 0.01 | [0, 3.4E+38] | kWh | 29 | The return water pressure sensor on the battery side is faulty. | 0: normal1: alarm
30 | Running status of the liquid cooling unit | / | / | "0: Power off; 1: self-loop; 2: Refrigeration; 3: heating; 4: offline | 30 | The water supply pressure sensor on the battery side is faulty. | 0: normal1: alarm
31 | Outdoor temperature | ℃ | 0.1 | [-50, 150] | 31 | Water pump outlet pressure sensor fault | 0: normal1: alarm
32 | Supply water temperature at the battery side | ℃ | 0.1 | [-50, 150] | 32 | Coolant High Pressure Alarm | 0: normal1: alarm
33 | Water return temperature at the battery side | ℃ | 0.1 | [-50, 150] | 33 | Coolant Low Pressure Alarm | 0: normal1: alarm
[5 empty] | 34 | Outdoor fan communication failure | 0: normal1: alarm
[5 empty] | 35 | The power supply to the outdoor fan is abnormal. | 0: normal1: alarm
[5 empty] | 36 | Outdoor fan overcurrent alarm | 0: normal1: alarm
[5 empty] | 37 | Compressor Pre-heating Alarm | 0: normal1: alarm
[5 empty] | 38 | The communication of the liquid injection and drainage fixture is abnormal. | 0: normal1: alarm
[5 empty] | 39 | Vacuumizing abnormality | 0: normal1: alarm
[5 empty] | 40 | Compressor drive alarm | 0: normal1: alarm
[5 empty] | 41 | The compressor drive output is abnormal. | 0: normal1: alarm
[5 empty] | 42 | Compressor overcurrent alarm | 0: normal1: alarm
[5 empty] | 43 | Compressor drive communication error. | 0: normal1: alarm
[5 empty] | 44 | Exhaust high temperature alarm | 0: normal1: alarm
[5 empty] | 45 | Compressor exhaust temperature sensor fault | 0: normal1: alarm
[5 empty] | 46 | Refrigerant Insufficient Alarm | 0: normal1: alarm
[5 empty] | 47 | Rehydration pump function abnormal | 0: normal1: alarm
[5 empty] | 48 | Drive heat dissipation fan fault | 0: normal1: alarm
[5 empty] | 49 | Outdoor fan fault | 0: normal1: alarm
[5 empty] | 50 | The electric heater is faulty. | 0: normal1: alarm
[5 empty] | 51 | The water supply temperature sensor on the battery side is faulty. | 0: normal1: alarm
[5 empty] | 52 | The return water temperature sensor on the battery side is faulty. | 0: normal1: alarm
[5 empty] | 53 | The supply and return water temperature sensor on the battery side is abnormal. | 0: normal1: alarm
[5 empty] | 54 | Battery side water supply high temperature alarm | 0: normal1: alarm
[5 empty] | 55 | Battery side water supply low temperature alarm | 0: normal1: alarm
[5 empty] | 56 | Coolant Expiration Alarm | 0: normal1: alarm
[5 empty] | 57 | Coolant Expired Shutdown Alarm | 0: normal1: alarm
[5 empty] | 58 | Coolant Change Not Completed | 0: normal1: alarm
[5 empty] | 59 | The water pump is not functioning properly. | 0: normal1: alarm
[5 empty] | 60 | Multi-way valve communication error | 0: normal1: alarm
[5 empty] | 61 | Multi-way valve failure | 0: normal1: alarm
[5 empty] | 62 | Water tank low level alarm | 0: normal1: alarm
[5 empty] | 63 | The return air temperature of the air conditioner in the integrated control compartment is too high. | 0: normal1: alarm
[5 empty] | 64 | The indoor fan of the air conditioner in the integrated control compartment is faulty. | 0: normal1: alarm
[5 empty] | 65 | The outdoor fan of the air conditioner in the integrated control compartment is faulty. | 0: normal1: alarm
[5 empty] | 66 | A/C compressor fault in integrated control compartment | 0: normal1: alarm
[5 empty] | 67 | The return air temperature sensor in the integrated control compartment is faulty. | 0: normal1: alarm
[5 empty] | 68 | High pressure of air conditioning system in integrated control cabin | 0: normal1: alarm
[5 empty] | 69 | The temperature sensor of the air conditioner evaporator in the integrated control compartment is faulty. | 0: normal1: alarm
[5 empty] | 70 | The temperature sensor of the air conditioner condenser in the integrated control compartment is faulty. | 0: normal1: alarm
[5 empty] | 71 | Comprehensive control cabin air conditioning evaporator freezing | 0: normal1: alarm
[5 empty] | 72 | Frequent high pressure of air conditioning system in integrated control cabin | 0: normal1: alarm
[5 empty] | 73 | The AC SPD is faulty. | 0: normal1: alarm
[5 empty] | 74 | The battery compartment door is open. | 0: normal1: alarm
[5 empty] | 75 | Water Alarm | 0: normal1: alarm
[5 empty] | 76 | smoke detector alarm | 0: normal1: alarm
[5 empty] | 77 | High concentration of combustible gases | 0: normal1: alarm
[5 empty] | 78 | Combustible gas detector communication failure | 0: normal1: alarm
[5 empty] | 79 | Combustible gas detector failure | 0: normal1: alarm
[5 empty] | 80 | Temperature and humidity sensor communication failure | 0: normal1: alarm
[5 empty] | 81 | The temperature and humidity sensor is faulty. | 0: normal1: alarm
[5 empty] | 82 | Heat detector alarm | 0: normal1: alarm
[5 empty] | 83 | The ambient temperature inside the cabin is too high. | 0: normal1: alarm
[5 empty] | 84 | EPO emergency stop alarm | 0: normal1: alarm
[5 empty] | 85 | Fire alarm | 0: normal1: alarm
[5 empty] | 86 | The exhaust fan is faulty. | 0: normal1: alarm
[5 empty] | 87 | The device access does not match the device configuration. | 0: normal1: alarm
[5 empty] | 88 | The SmartModule communication is abnormal. | 0: normal1: alarm
[5 empty] | 89 | I/O expansion board communication is abnormal. | 0: normal1: alarm
[5 empty] | 90 | Fire suppression system abnormality | 0: normal1: alarm
[5 empty] | 91 | Fire Suppression System Zone Control Valve Start | 0: normal1: alarm
[5 empty] | 92 | The offering software package is not backed up. | 0: normal1: alarm
[5 empty] | 93 | The electronic label board data is abnormal. | 0: normal1: alarm
[5 empty] | 94 | The communication between the upper-layer controller is abnormal. | 0: normal1: alarm
[5 empty] | 95 | The communication of the fire suppression system is abnormal. | 0: normal1: alarm
[5 empty] | 96 | Auxiliary power meter communication exception | 0: normal1: alarm
[5 empty] | 97 | Power-on authorization is not enabled. | 0: normal1: alarm
[5 empty] | 98 | Fire Suppression System Agent Explosion | 0: normal1: alarm
[5 empty] | 99 | CMU chip overtemperature | 0: normal1: alarm
[5 empty] | 100 | The CMU auxiliary source is abnormal. | 0: normal1: alarm
[5 empty] | 101 | The CMU memory is abnormal. | 0: normal1: alarm
[5 empty] | 102 | CMU internal exception | 0: normal1: alarm
[5 empty] | 103 | Inconsistent component software versions | 0: normal1: alarm
[5 empty] | 104 | Fire suppression device cabin solenoid valve start | 0: normal1: alarm
[5 empty] | 105 | Fire suppression device manual alarm activation | 0: normal1: alarm
[5 empty] | 106 | Fire suppression device emergency stop button pressed | 0: normal1: alarm
[5 empty] | 107 | The gas release indicator of the fire suppression device is on. | 0: normal1: alarm
[5 empty] | 108 | Air conditioner communication in the integrated control compartment is abnormal. | 0: normal1: alarm
[5 empty] | 109 | The BCU communication is abnormal. | 0: normal1: alarm
[5 empty] | 110 | The PSU module is faulty. | 0: normal1: alarm
[5 empty] | 111 | Failed to locate the physical location of the cluster. | 0: normal1: alarm
[5 empty] | 112 | The voltage of the three-phase auxiliary power supply is abnormal. | 0: normal1: alarm
[5 empty] | 113 | Three-phase auxiliary source overcurrent | 0: normal1: alarm
[5 empty] | 114 | Integrated control cabin door open | 0: normal1: alarm
[5 empty] | 115 | Overtemperature of the wiring copper bar in the integrated control compartment | 0: normal1: alarm
[5 empty] | 116 | Fire suppression system alarm | 0: normal1: alarm
[5 empty] | 117 | DC busbar T/H sensor communication failure | 0: normal1: alarm
[5 empty] | 118 | Energy storage compartment door travel switch triggering | 0: normal1: alarm
[5 empty] | 119 | Integrated control cabin left door travel switch triggered | 0: normal1: alarm
[5 empty] | 120 | The ambient temperature inside the cabin is overheated. | 0: normal1: alarm
[5 empty] | 121 | The temperature and humidity sensor of the integrated control compartment is abnormal. | 0: normal1: alarm

## BCU (new-generation energy stor
Telemetry |  |  |  |  | Teleindication | 信号名称CN | 状态 | Telecontrol | 信号名称CN | 命令 | Teleadjust
No. | Signal Name | Precision | Range | Unit | No. | Signal Name | Status | No. | Signal Name | Command | No. | Signal Name | Unit | Precision
1 | Working status | / | 0x0000 Standby 0x0100 Startup 0x0200 Running 0x0205 Running: Battery Current Limiting 0x0207 Running: The ESS is derated. 0x0300: abnormal shutdown 0x0301 Shutdown: Shutdown by command 0x0302 Power-off: The power-on is not authorized. 0x0304 Shutdown: EPO Shutdown 0xB000: offline 0xC000 Loading | / | 1 | Communication fault | 0: normal 1: faulty
2 | Electric voltage | 0.1 | [-3276,3276] | V | 2 | Battery pack power connection error. | 0: normal; 1: alarm
3 | Electric current | 0.1 | [-3276,3276] | A | 3 | Battery pack end of life | 0: normal; 1: alarm
4 | ISO Insulation Resistance | 0.001 | [0, 65.535] | MΩ | 4 | Battery pack overvoltage | 0: normal; 1: alarm
5 | SOC | 1 | [0, 100] | % | 5 | Battery pack undervoltage | 0: normal; 1: alarm
6 | SOH | 1 | [0, 100] | % | 6 | Battery overcurrent protection | 0: normal; 1: alarm
7 | SOE | 1 | [0, 100] | % | 7 | Battery pack overtemperature | 0: normal; 1: alarm
8 | DOD | 1 | [0, 100] | % | 8 | Battery pack low temperature | 0: normal; 1: alarm
9 | Charge/discharge power | 0.001 | [-3.4E+38, 3.4E+38] | kW | 9 | Battery pack lockout | 0: normal; 1: alarm
10 | Rechargeable battery | 0.001 | [0, 3.4E+38] | kWh | 10 | Battery failure | 0: normal; 1: alarm
11 | Dischargeable capacity | 0.001 | [0, 3.4E+38] | kWh | 11 | Battery pack SOH too low | 0: normal; 1: alarm
12 | Current-day charging capacity | 0.01 | [0, 3.4E+38] | kWh | 12 | Battery Pack SOH Calibration | 0: normal; 1: alarm
13 | Current-day discharge capacity | 0.01 | [0, 3.4E+38] | kWh | 13 | Battery pack passive equalization resistance overtemperature | 0: normal; 1: alarm
14 | Electricity charged in the current month | 0.01 | [0, 3.4E+38] | kWh | 14 | Battery Pack Sampling Abnormal | 0: normal; 1: alarm
15 | Discharged electricity in the current month | 0.01 | [0, 3.4E+38] | kWh | 15 | The battery pack configuration data is abnormal. | 0: normal; 1: alarm
16 | Electricity charged in the current year | 0.01 | [0, 3.4E+38] | kWh | 16 | The battery pack specifications do not match the device. | 0: normal; 1: alarm
17 | Discharge power of the year | 0.01 | [0, 3.4E+38] | kWh | 17 | Abnormal cell temperature rise | 0: normal; 1: alarm
18 | Accumulated charge capacity | 0.01 | [0, 3.4E+38] | kWh | 18 | PACK thermal runaway alarm | 0: normal; 1: alarm
19 | Accumulated discharge capacity | 0.01 | [0, 3.4E+38] | kWh | 19 | Battery Pack Recharge Failure | 0: normal; 1: alarm
20 | Maximum battery pack temperature | 0.01 | [-327,327] | ℃ | 20 | Overcurrent protection for the equalization module | 0: normal; 1: alarm
21 | Location of the highest battery pack temperature | 1 | [0, 65535] | N/A | 21 | The internal communication of the equalization module is abnormal. | 0: normal; 1: alarm
22 | Minimum battery pack temperature | 0.01 | [-327,327] | ℃ | 22 | Equalization module bus voltage abnormal | 0: normal; 1: alarm
23 | Position of the lowest battery pack temperature | 1 | [0, 65535] | N/A | 23 | Equalization module battery voltage abnormal | 0: normal; 1: alarm
24 | Minimum battery pack voltage | 0.1 | [0, 6553] | V | 24 | Overtemperature protection inside the equalization module | 0: normal; 1: alarm
25 | Position of the lowest battery pack voltage | 1 | [0, 65535] | N/A | 25 | MCU overtemperature protection for the equalization module on the battery side | 0: normal; 1: alarm
26 | Maximum battery pack voltage | 0.1 | [0, 6553] | V | 26 | Overtemperature protection for the connecting terminal of the equalization module | 0: normal; 1: alarm
27 | Position of the highest battery pack voltage | 1 | [0, 65535] | N/A | 27 | Wiring fault on the bus port of the equalization module | 0: normal; 1: alarm
[5 empty] | 28 | Equalization module bus soft-start failed | 0: normal; 1: alarm
[5 empty] | 29 | Equalization Module Version Mismatch | 0: normal; 1: alarm
[5 empty] | 30 | Equalization module address pairing timeout | 0: normal 1: faulty
[5 empty] | 31 | Equalization module soft-start MOS short-circuit fault | 0: normal 1: faulty
[5 empty] | 32 | Equalization module abnormal | 0: normal 1: faulty
[5 empty] | 33 | Equalization module overcurrent fault | 0: normal 1: faulty
[5 empty] | 34 | Spares | 0: normal 1: faulty
[5 empty] | 35 | Internal Short Circuit of the BMU Board | 0: normal 1: faulty
[5 empty] | 36 | BMU sampling disconnection fault | 0: normal; 1: alarm
[5 empty] | 37 | BMU internal fault | 0: normal; 1: alarm
[5 empty] | 38 | BMU Node Disconnection | 0: normal; 1: alarm
[5 empty] | 39 | BMU communication error. | 0: normal; 1: alarm
[5 empty] | 40 | RPCB overcurrent alarm | 0: normal; 1: alarm
[5 empty] | 41 | The RPCB voltage is abnormal. | 0: normal; 1: alarm
[5 empty] | 42 | RPCB port short-circuit fault | 0: normal; 1: alarm
[5 empty] | 43 | RPCB internal temperature abnormal | 0: normal; 1: alarm
[5 empty] | 44 | RPCB overcurrent fault | 0: normal; 1: alarm
[5 empty] | 45 | Battery-side ISO detection abnormal | 0: normal; 1: alarm
[5 empty] | 46 | The RPCB power loop is abnormal. | 0: normal; 1: alarm
[5 empty] | 47 | RPCB version mismatch | 0: normal; 1: alarm
[5 empty] | 48 | The RPCB device is abnormal. | 0: normal; 1: alarm
[5 empty] | 49 | Battery side RCD protection | 0: normal; 1: alarm
[5 empty] | 50 | RPCB overcurrent protection | 0: normal; 1: alarm
[5 empty] | 51 | RPCB fan alarm | 0: normal; 1: alarm
[5 empty] | 52 | Surge protector fault | 0: normal; 1: alarm
[5 empty] | 53 | Battery ISO Insulation Detection Alarm | 0: normal; 1: alarm
[5 empty] | 54 | 19 V auxiliary power abnormal | 0: normal; 1: alarm
[5 empty] | 55 | Inconsistent component software versions | 0: normal; 1: alarm
[5 empty] | 56 | Abnormal total voltage of battery cluster | 0: normal; 1: alarm
[5 empty] | 57 | The difference between the total voltage of the battery cluster and the sum of the cell voltage is large. | 0: normal 1: faulty
[5 empty] | 58 | Failed to mix battery packs. | 0: normal 1: faulty
[5 empty] | 59 | BCU chip overtemperature | 0: normal 1: faulty
[5 empty] | 60 | BCU internal exception. | 0: normal 1: faulty
[5 empty] | 61 | Equalization module software version inconsistency | 0: normal 1: faulty
[5 empty] | 62 | BCU auxiliary power supply abnormal | 0: normal 1: faulty
[5 empty] | 63 | BCU storage exception | 0: normal; 1: alarm
[5 empty] | 64 | Cluster power control board communication abnormal | 0: normal; 1: alarm
[5 empty] | 65 | The DCDC communication is abnormal. | 0: normal; 1: alarm
[5 empty] | 66 | PCS communication is abnormal. | 0: normal; 1: alarm
[5 empty] | 67 | Equalization module communication error | 0: normal; 1: alarm
[5 empty] | 68 | Abnormal wiring detection | 0: normal; 1: alarm
[5 empty] | 69 | Cluster PCS failure | 0: normal; 1: alarm
[5 empty] | 70 | Cluster PCS communication abnormal | 0: normal; 1: alarm
[5 empty] | 71 | The SOH of the energy storage system needs to be calibrated. | 0: normal; 1: alarm
[5 empty] | 72 | BCU Node Disconnection | 0: normal; 1: alarm
[5 empty] | 73 | Battery cluster voltage out of range | 0: normal; 1: alarm
[5 empty] | 74 | The cluster device access does not match the configuration. | 0: normal; 1: alarm
[5 empty] | 75 | Abnormal battery sampling | 0: normal; 1: alarm
[5 empty] | 76 | The battery voltage consistency deviation is large. | 0: normal; 1: alarm
[5 empty] | 77 | Large deviation of battery temperature consistency | 0: normal; 1: alarm